06/29/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-517 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Dispersal System Operation" ,"Effluent Screens" ,"Control Operation"] |  | NO | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | The peat in the Puraflo modules has deteriorated and will need to be replaced or have a different alternative treatment unit installed. The control panel settings have been altered to operate the pump on a demand basis, instead of the time-dosed basis as originally designed. The septic tank & pump tank are both leaking at the base of the riser. Scum & sludge in the tanks was at a level where we would recommend pumping the tanks. We were unable to excavate and inspect the distribution box, nor able to probe the drainfield lines because this area has been compacted by heavy equipment. It is possible the distribution box and header lines have been damaged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
04/25/2023 |  | RoutineScheduled | 2002-143-0266 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Effluent Screens","Control Operation","Distribution Pump Operation","Recirculation Pump"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 12:00 AM
06/06/2023 | Alternative |  | 03-197-A9 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/06/2023 |  | 2.110000 |  |  | 1.000000 |  |  | Will be sent separately |  | BOD: 2.11 TSS: 1.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 12:00 AM
12/02/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. 10" of solids in recirculation portion of treatment unit. 4" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 07:03 PM
05/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | st/atu needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
08/09/2023 | Alternative | RoutineScheduled | SD-12-328 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | Puraflo | Pump | Gravity | Trenches | Not Applicable | 65.700000 | ["SludgeScum Accumulation","Effluent Screens"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | Septic | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 07:45 AM
05/22/2023 |  | RoutineScheduled | 175-16-0234 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Deck has blocked control panel. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
03/22/2023 |  | Initial Visit | 107-02-0197 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  |  | Trenches |  |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | 12:00 AM
01/18/2023 |  | Routine/Scheduled | 550-STS-6449 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 2:20PM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Multiflo FTB | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
06/29/2023 | Alternative | RoutineScheduled | 107-05-0332 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | [] | [18 empty] | Cleaned Filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 05:15 PM
12/28/2023 | Alternative | RoutineScheduled | 165-STS-336495 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Multiflo |  |  | Gravity | Discharge | Chlorination |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/09/2024 | 12:00 AM
07/07/2023 | Alternative |  | 033-06-0263-ST | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
06/03/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 6" of accumulated solids in first portion of septic tank. 12" of accumulated solids in second portion of septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Removed roots from the treatment unit that had gotten in under the lid. 0" of solids in recirculation portion of treatment unit. 1" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 07:03 PM
07/06/2023 | Alternative | Reportable Incident Component Maintenance | 099-15-0093 SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Level Sensor Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to hung toliet and pump has slowed down and was not timed properly. Retimed pump and did routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/30/2023 | Alternative | Routine/Scheduled | 093-04-0012 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | Dec 30 1899 11:20AM
09/18/2023 | Alternative | Reportable Incident Component Maintenance | SD-08-418 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm in recirc tank started 4 days ago. RSV was clogged and had popped out of its holder. Removed the bottom of the RSV and cleaned everything inside. The only effluent transferring over to the pump tank was flowing directly through the RSV hub. Showed owner that tank had a lot of trash in it that should not have been flushed. Pumped level down enough to ensure that inlet tee was not clogged. Advised owner system could need up to 24 hours to get back to proper level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
05/12/2023 | Alternative | RoutineScheduled | S-09-111-0144 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Gravity | Gravity | Discharge | Chlorination |  | ["Control Operation","BlowerCompressorAerator Operation"] | ["Control Operation","BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Septic tank 1 in scum and 10" sludge, treatment tank under 1 in scum and 6" light trace of sludge, discharge tank trace sludge and filter was clear. Pulled inner filter OK, Checked cl2 and decl2 tabs lets Present. owner will replenish as needed. Good aeration on treatment and dechlor, cleaner blower airfilter. Owner replenished the Chlorine and dechlor tablets as needed. System is fully operation. No effluent was present at the time of visit to sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
11/17/2023 | Alternative | Routine/Scheduled | 036-STS-35347 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/17/2023 | Dec 30 1899 11:27AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | Dec 30 1899 1:58PM
03/07/2023 |  | Routine/Scheduled | 11-120-0298A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/07/2023 | Jan 1 1900 10:08AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/23/2023 |  | RoutineScheduled | 033-17-0224-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend replacing the air release valve housing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
04/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic/atu tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
12/10/2023 | Alternative | Routine/Scheduled | 14-118-0020 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Water level high upon arrival due to clogged pump and vortex filter. Pumped out during service. Inlet tee appears to be intact Discharge/Pump Tank Condition of above Component Notes for above Component Water level high upon arrival due to clogged pump and vortex filter. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Flushed and cleaned vortex filter. Checked and confirmed drawdown within discharge tank Aeration Condition of above Component Notes for above Component Water level high upon arrival due to clogged discharge pump and vortex filter. Flushed and cleaned weir. Upgraded diffuser while on site. Checked and confirmed high level alarm float is functioning properly Air Pump/Blower Condition of above Component Notes for above Component Upon arrival, I go the aerator had failed. Upgraded aerator while on site. Checked and confirmed aerator is functioning properly. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly Drip Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 12:38PM
04/21/2023 | Alternative | Routine/Scheduled | S07-180-0104 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/21/2023 | Jan 1 1900 12:15PM
10/20/2023 | Alternative | Routine/Scheduled | 19-120-0209AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 2 in of sludge less than 1 in of solids Pulled and cleaned filter Filter housing intact and filter properly working No signs of infiltration -Discharge/Pump Tank: Normal level Tested floats and pump all working as should All plumbing intact and pump moving water properly -Peat Moss: Tipping bucket and dispersal trays are intact and properly working Racked out peat moss Peat moss in good shape and properly taking water No standing water or puddling -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Pump pulled 10.2 amps All components working properly -Distribution Box: Customer did not want us to dig it up at this time -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 1:34PM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired pipe between primary tank and pump tank Replaced cracked valve box lid All corrections were made and this inspection in required annually for VDH Call 540-860-8086 with any questions | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
12/21/2023 | Alternative | Initial Visit | VAG401450 | Bath | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Sand Filter | Pump | Gravity | Discharge | Chlorination |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [17 empty] | The system did not need to be pumped. The controls were operating as designed, however the float switches were just hanging in the tank without a pivot point. Float weights were added so the floats would have a pivot point and would only pump out a small amount of effluent at a time. The tablet feeders had tablets in them at the time of inspection. There were no samples drawn because there was no discharge at the time of inspection. The lids were secured. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/17/2024 | 05:30 PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/26/2023 | Alternative | Reportable Incident Component Maintenance | 099-18-0122 C-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in a high level alarm due to RSV floating and not allowing waste water to transfer to the discharge tank. Cleaned RSV and adjusted water levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
06/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Other conventional maintenance performed | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | [] | [] | [18 empty] | System is working properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | Dec 30 1899 12:45PM
05/05/2023 | Alternative | Routine/Scheduled | 166-07-049 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 08:30 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/08/2023 | Alternative |  | 169-STS-26545 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/08/2023 |  | 3.770000 | [5 empty] | Will be sent separately |  | BOD: 3.77 TSS: BDL E.Coli: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 12:00 AM
11/27/2023 | Alternative | RoutineScheduled | VAG401862 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] | [18 empty] | This report got missed when November reports were submitted. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/15/2024 | 10:45 AM
03/21/2023 | Alternative | Routine/Scheduled | 150-04-258 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/21/2023 | 10:38 AM
07/17/2023 | Alternative | Routine/Scheduled | 03-174-0047 | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss in fair condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 8:00AM
09/30/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | None |  | Pump | Gravity | Mound |  |  | ["None"] | ["None"] | NO | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank, no surface crust. 2" of solids in discharge pump tank. Some condensation within the pump control panel, removed as mush as possible. Inspected sand mound for any sign of ponding water, none found. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/24/2023 | 07:03 PM
04/13/2023 | Alternative | Routine/Scheduled | 800-STS-14574 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The aerator should be raised due to dirt and ants. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | Dec 30 1899 10:15AM
02/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-8"sludge 4"scum/ Microfast ATU-4"sludge/ Pump Tank-1"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls are inside the house/ Controls, pumps, floats and alarm are functioning properly/ Counts: Pump1-371 ETM-13h 4m/ Pump2-368 ETM-12h 56m/ Peak-8/ High-7 On-2m 8s Standard Off-6h Peak Off-4h 48m / No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | SD-07-757 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Ecopod blower needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
08/09/2023 | Alternative | Reportable Incident | 15-140-0019 | Emporia | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm and the aerator not working. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The pressure switch on the aerator is not hooked up - needs to be addressed and/or fixed. The timer is set to 7 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/09/2023 | Dec 30 1899 9:30AM
10/05/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped and cleaned out the pump tank and Clearstream tank. Once there is enough water in the tanks need to hook up the pressure switch on the aerator. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/05/2023 | Dec 30 1899 10:00AM
11/09/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | Dec 30 1899 11:30AM
12/08/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 9:20AM
10/09/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.410000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 04:00 PM
07/19/2023 | Alternative | Routine/Scheduled | C-175-17-0088 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 12:58PM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] |  | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | Needs new control panel & hydraulic unit. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/17/2023 | Dec 30 1899 12:46PM
03/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 5"scum/ Microfast-18"sludge / Pump Tank-2"sludge/ Septic Microfast Tank requires pump out/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Pump-3556 ETM-9662h 22m/ Peak-16/ High-0/ Watermeter-0,224,737.2 / On-17m 18s Off-3h Peak off-2h 24m/ No breakout or spongy areas on the drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/14/2023 | Alternative | Initial Visit | 18-160-0105 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 4.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | [] | NA | Septic | Dark Brown | [14 empty] | Inspected | - has three tanks but there is a small distribution box between pretreatment and pump chamber, reason unknown - recommend all tanks be pumped/cleaned - replaced blower onsite | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | 12:00 AM
11/07/2023 | Alternative | Routine/Scheduled | 041-STS-260809 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [16 empty] | Recommend Pump out, flagged tanks that need to be pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | Dec 30 1899 9:00AM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
01/13/2023 |  | Routine/Scheduled | R03-111-0114 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/13/2023 | Jan 1 1900 12:45PM
02/01/2023 |  | RoutineScheduled | 179-STS-88650 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Settling has occurred around the tanks and this area is now holding water. We recommend contacting your builder to see if they will assist you with regrading & improving drainage away from the tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance | SWT-05-533 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The blue valve in the drip dispersal system is sticking. We recommend replacing it and the cover on the air release valve. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | 182-01-0124 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Please remove trees in path to panel and also trim bushes around system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
09/29/2023 | Alternative | RoutineScheduled | 03-125-034 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/29/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled | 06-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Control Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/27/2023 | 12:00 AM
07/18/2023 | Alternative | Initial Visit | 151-08-0087 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Last documented service by Millers - 06/11/2019 Primary septic tank - recommend pumpout - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 4 Modules - peatmoss in fair condition - raked turned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 11:00 AM
02/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
07/28/2023 | Alternative | Reportable Incident | 234-16-334 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/28/2023 | Dec 30 1899 11:00AM
01/03/2023 |  |  | 179-13-0092-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance | SD-06-20l | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
04/27/2023 | Alternative | RoutineScheduled | 105-18-0187 | Appomattox | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Septic | Eco Flo | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | ["Effluent Screens"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 12:00 AM
05/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
11/01/2023 | Alternative | Routine/Scheduled | 093-14-0064 | Isle Of Wight | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/01/2023 | Dec 30 1899 11:21AM
09/06/2023 | Alternative | Routine/Scheduled | 151-09-0134 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 55.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 05:23 PM
07/06/2023 | Alternative | RoutineScheduled | 108-16-0016 (ALT. SYSTEM) | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [7 empty] | 07/06/2023 | Pump Chamber | 1.000000 |  |  | 1.200000 |  |  | Attached to this report |  | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The recirculating pump was pulled and sprayed off. The Bod and TSS were within permitted limits. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 11:00 AM
12/14/2023 | Alternative | RoutineScheduled | 121-STS-12055 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 1.000000 | 1500 | ECOFLO |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | [18 empty] | - repaired the piping in the Ecoflo | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled | 175-14-0275 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. A piece of the flange on the 20" riser over the media is broken off. It is a little above grade so not likely a path for infiltration, but should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
04/07/2023 |  | RoutineScheduled | 179-07-0378-ST | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Bad timer enabler float, replaced. fluffed media and removed a few small roots. Recommend removing bushes and tree growing up against puraflow pod. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
10/21/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Replaced recirculation middle float and reconnected discharge middle float electrical connection in electrical junction box since last annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 14" of solids in recirculation portion of treatment unit. 16" of solids in discharge portion of treatment unit. Tested floats, pumps, and alarm. Excellent treatment quality. Treatment unit may need to be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/24/2023 | 07:03 PM
03/01/2023 |  | Pump-Out Only | {FIPSCode}-STS-26549 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Pad | Not Applicable | 450.000000 | None | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Pumped processing tank empty and serviced. Serviced RSV, recirc pump, pump vault and effluent screen. Replaced treatment system lid and pressure washed media drapes. Refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/02/2023 | Jan 1 1900 8:00AM
09/11/2023 | Alternative | Routine/Scheduled | 2007-143-0054 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | - Septic Tank: Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. - Discharge Tank: Water level normal. Structural integrity of tank appears to be intact. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. - Peat Moss: First tank has fractures in top corners near lid. Peat moss is bad/ failing. Structural integrity of tipping bucket appears to be intact. Checked and confirmed tipping bucket is functioning properly. Structural integrity of second tank appears to be intact. Structural integrity of tipping bucket appears to be intact. Checked and confirmed tipping bucket is functioning properly. Raked and tilled peat moss. Peat moss is in good condition - Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. - Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. - Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 10:41 AM
02/20/2023 |  | RoutineScheduled | SWT-05-258 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"Effluent Screens"] | ["Septic Tank Baffles" ,"Effluent Screens" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
10/18/2023 | Alternative | RoutineScheduled | 07-197-A11 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [11 empty] | Both tablets stocked, aerator working, no odor, clear. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
02/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0321 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
01/04/2023 |  | Routine/Scheduled | 228-07-1005 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | Jan 1 1900 9:30AM
04/24/2023 |  | RoutineScheduled | 177-09-0098-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-530 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
11/16/2023 | Alternative | RoutineScheduled | 185-STS-17514 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/16/2023 | 12:00 AM
11/29/2023 | Alternative | Initial Visit | 041-STS-261796 | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the alarm going off Wednesday night and the red light now being on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the aerator. Changed the mesh screen in the spinfilter. The pipe from the Clearstream tank to the pump tank has settled - needs to be fixed. The Clearstream tank, septic tank, and pump tank all need to be pumped out and cleaned due to paint being in the tanks. There are tire tracks across the drainfield. The timer was set at 3 minutes 30 seconds every 2 hours changed it to 8 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/29/2023 | Dec 30 1899 12:30PM
12/11/2023 | Alternative | Routine/Scheduled | S 800-14-0192 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EcoPod |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | Dec 30 1899 11:53AM
01/03/2023 | Alternative |  | 101-07-0116 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Jeffery & Roselyn | Kay | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/03/2023 | Alternative | Pump-Out Only | 087-STS-6152 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Supervised pump out of trash tank/ aeration tank of 1000 gallons performed by CWS. Supervised refill of trash tank/ aeration tank performed by Bruce's and son Waterwork | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 08:53 AM
12/07/2023 | Alternative | RoutineScheduled | 169-STS-25805 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.500000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/21/2023 |  | RoutineScheduled | {FIPSCode}-STS-15027 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | Musty | Clear | 7.200000 | 9.300000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 03/01/2023 | 02:21 PM
04/27/2023 | Alternative | RoutineScheduled | S-10-111-0087 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | EcoPod |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 6" of accumulated solids in septic tank. Cleaned septic tank filter. 10" of solids in discharge pump tank. Cleaned drip manifold spin filter. Cleaned blower air filter. Tested floats, pump and alarms. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | Jan 1 1900 7:03PM
10/05/2023 | Alternative | Routine/Scheduled | 2008-143-0095 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Peat checked. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 10:41 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-15-0106-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The drainfield is overgrown with grass & pine saplings on the header lines. This should be mowed & maintained in a mowed condition to prevent roots from growing into the distribution box. We also recommend adding a 6" riser to the Pump Tank to make it easier to remove the lid for inspection and service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
05/04/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | pumped pump tank down replaced pump. Pump is working as it should | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
01/05/2023 |  | RoutineScheduled | 2010-143-0140 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 09:30 AM
05/19/2023 |  | Routine/Scheduled | 228-09-0030A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | Jan 1 1900 12:54PM
09/07/2023 | Alternative | RoutineScheduled | 2016-143-0023 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/27/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired force main & installed 3 control floats. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/07/2023 | Dec 30 1899 6:39AM
09/28/2023 | Alternative | Follow-Up Component Maintenance | SWP-01-271 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank pumped out by others. Peat replacement completed. Degraded peat was removed by hand and new peat was installed. Peat was purchased from Driller Services. Degraded peat was disposed at Spotsylvania Refuse. Replaced 3 support bars. Resealed outlet risers on both tanks. Installed proper A300 filter. Distribution box is completely destroyed, will send proposal for replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/02/2023 | 05:18 AM
10/18/2023 | Alternative | Follow-Up Component Maintenance | SD-13-404 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Installed new Clearstream discharge pump and did a drawdown. New pump flow rate approximately 26 gpm. Replaced the high level alarm float and the override float. Timer float was still working but was a mercury float and moved into the override float position. So new floats are in the timer enabler and high level alarm positions. Replaced junction box.Rust stains on baffle wall suggest infiltration, nothing seen today. Override float (pump on) is above the high level float now, so heavy infiltration would cause alarm first. Recommend adding wires to make the pressure switch active for the compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
06/22/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0325-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 3.03 amps. Treatment is crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
08/23/2023 | Alternative | Reportable Incident | 136-04-217 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the aerator not working. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The alarm in the Clearstream is not working - recommend installing new alarm assembly. Replaced mute button and cover. The septic tank needs to be pumped. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/23/2023 | 04:15 PM
03/10/2023 |  | RoutineScheduled | 033-13-0006-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
05/20/2023 | Alternative | RoutineScheduled | 09-10-0309 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump | Gravity | Mound |  | 600.000000 | [] | [] | [17 empty] | Pumped Out | REPLACED FIBER, PUMPED SEPTIC TANK, RUHUNG ALL FLOATS IN PUMP STATION, CLEANED SPRAYERS, REPLACED A SPRAYER NOZZLE, CLEANED FILTER | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 10:30 AM
02/22/2023 |  | RoutineScheduled | 145-97-0072 (LEGACY ALT. SYSTEM) | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2000 | Septic Tank Only | Sand Filter | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The sand filters was inspected and are in good operating conditions. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 09:00 AM
03/15/2023 |  | RoutineScheduled | 07-125-176 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled | 95-192-211 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/02/2023 | 12:00 AM
08/29/2023 | Alternative | Routine/Scheduled | 234-13-463 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 12:30PM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/21/2023 | Alternative | Routine/Scheduled | 14-160-0148 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:30 PM
04/11/2023 |  |  | 159-19-0052 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Aquasafe |  | Gravity | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:00 AM
01/30/2023 |  | RoutineScheduled | 179-07-0238-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment looks good due to customer not adding salts in the past months but we still recommend disconnecting water softener treatment drain line from sewer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance | 047-17-112 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
12/05/2023 | Alternative | RoutineScheduled Component Maintenance | 175-11-0491 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/08/2023 | 08:29 AM
06/28/2023 | Alternative | Routine/Scheduled | 136-07-0158 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Real Estate Inspection Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss in fair condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | 07:45 AM
10/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Loudoun Environmental Treatment | 1942001460 | Raymond | Kirkpatrick | 1.000000 | 1500 | .75Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2024 | 12:00 AM
01/27/2023 | Alternative | Routine/Scheduled | 166-06-163 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Chlorination | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Found compressor failed & control panel failed due to power surge / lightning strike. Primary septic tank normal level. Aeration tank - replaced compressor and controls - mixing present. Discharge tank - serviced drip headworks - pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 09:45 AM
02/14/2023 |  | Routine/Scheduled | 036-STS-31959 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/14/2023 | Jan 1 1900 11:33AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-11-0268 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
03/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/02/2023 |  | RoutineScheduled | 175-01-0989 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
04/25/2023 | Alternative |  | SD-12-314 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["Level Sensor Operation","Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 01:30 PM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping ATU | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/10/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Wetland | [6 empty] | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Whitewater ATU | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Septic/atu needs pumped. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
04/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/28/2023 | Alternative | Routine/Scheduled | S-175-14-0019 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Dec 30 1899 9:18AM
11/30/2023 | Alternative | RoutineScheduled | 09-137-0128 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | MicroFast |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
09/11/2023 | Alternative | Reportable Incident | 147-13-0041 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The timer is set to 6 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/11/2023 | Dec 30 1899 10:15AM
03/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Dec 30 1899 12:48PM
01/03/2023 |  | Routine/Scheduled | 550-STS-5886 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | Jan 1 1900 9:45AM
04/13/2023 |  | Routine/Scheduled | 133 07 0103 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 03:45 PM
04/26/2023 | Alternative | Follow-Up | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 2.000000 | 8000 | none | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 4-26-23 Re tested all zones Z 1 16.0, Z2 24.0 Z3, 22, Z4 18.3, Z5 18 gpm, Z6 17.2 Turned all zones to Auto adjusted run times in TCOM 04/28/2023 Tanks full manhole 1 leaking at surface, needs to be repaired. Pumped 4,000 Advantage, 4,000 Butler | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/02/2023 | 11:05 AM
04/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/23/2023 | Alternative | Pump-Out Only |  | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pump out of treatment system as recommended during last service visit. Processing tank refilled with fresh water for re-start. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | Dec 30 1899 9:00AM
10/06/2023 | Alternative | Pump-Out Only | 06-160-0438 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Microfast | [6 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 12:00 AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
11/22/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | 4' Liquid depth,0 scum & sludge just had it pumped, Alarms, pumps, floats all working, Field dry. Cleaned blower filter, it did hep the aeration | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 11:45 AM
06/09/2023 | Alternative | RoutineScheduled | 2008-143-0018 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
04/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
07/29/2023 | Alternative |  | SD-15-147 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | The TSS sample duplicate relative percent difference (RPD) recovered outside of QC acceptance criteria possibly due to a non-homogeneous sample matrix. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
07/03/2023 | Alternative | Routine/Scheduled | 228-17-0280 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear |  | 4.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/03/2023 | Dec 30 1899 12:10PM
12/06/2023 | Alternative | Routine/Scheduled | 09-135-3130 | Giles | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 2.000000 |  | Biomicrobics MicroFAST |  | Gravity | Gravity | Discharge | UV | 150.000000 | None | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | None | Clear | 6.900000 | 7.500000 | 0.000000 |  |  | 12/07/2023 | Sample Tap | 2.000000 |  | 1.000000 | 1.000000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 04:00 PM
06/13/2023 | Alternative | Reportable Incident Component Maintenance | 179-STS-87221 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed blower. Replaced blower. Preformed rountine inspection. Two part septic tank needs to be pumped out due to sludge levels. Advised home owner to stop using sent beads and gave him a copy of the Do's and Dont's. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
06/09/2023 | Alternative | Pump-Out Only | 05-160-0353 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | - pumped Microfast - replumbed pump to replace check valve - system is functioning, recommend inlet line be repaired/replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
07/17/2023 | Alternative | Routine/Scheduled | 08-120-0499A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | Dec 30 1899 3:32PM
02/06/2023 |  | RoutineScheduled | C102-06-0065 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Delta Whitewater | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | The system did not need to pumped. The effluent filter and spin filter were both cleaned. The blower filter was cleaned. The pressure bell was pulled and reset. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | Jan 1 1900 12:55PM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-90219 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Water in j-box, vacuumed it out. Grease building up in septic tank, left copy of Do's and Don'ts. Grass very tall around septic components, recommend maintaining. RECIRC: HL-4, LL-29, OVERRIDE-264. DISCHARGE: HL-31, OVERRIDE-49. "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
09/29/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | See attachments | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90315 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Wipes and grease keeps accumulating in septic tank, gave customer copy of Do's and Don'ts last year. 1 valve cover missing for 1 air release valve. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
07/21/2023 | Alternative | Reportable Incident | 800-STS-13769 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Owner called due to an alarm. Installed a new UV bulb and installed a new UV ballast. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/21/2023 | Dec 30 1899 12:00PM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
01/14/2023 |  | RoutineScheduled | 133 05 0549 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 300 | BioMicrobics MicroFast |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | [17 empty] | Annual inspection. Replaced blower three weeks prior. 10" of accumulated solids in septic tank. 18" of accumulated solids in treatment unit. 12" of solids in discharge pump tank. Cleaned drip manifold spin filter. Flushed drip field through removing air releases. Adequate aeration. Tested floats, pump and alarm. Septic tank, treatment unit and discharge pump tank should need to be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/20/2023 | 07:03 PM
04/11/2023 |  |  | 085-STS-35440 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
04/25/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic Tank 6" scum, 8" trace sludge, Treatment tank has a trace while running, Pump Tank 6-10" sludge, Both Alarms tested good, Pumps opperational, Flushed drip filter and flushed drip lines. The drainfield looks dry and unremarkable, The zoner valve box appears operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
07/03/2023 | Alternative | RoutineScheduled | 175-03-0703 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Mckim Septic and Pumping | 1942001330 | Michelle | McKim | 1.000000 | 2000 |  |  | Pump | Gravity | Mound | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/20/2023 | 07:30 AM
01/21/2023 |  | Routine/Scheduled | 149-STS-10577 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 100 |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [16 empty] | Needs a pump out, I flagged lids that need it. No Grease. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/21/2023 | Jan 1 1900 11:30AM
12/07/2023 | Alternative | RoutineScheduled | 033-STS-88967 | Caroline | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | check sludge, clean filters, fixed uv bulb and ballast, system check - okay | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/02/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 12:56 PM
01/03/2023 |  |  | 04-197-A19 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/03/2023 |  | 6.450000 |  |  | 3.600000 |  |  | Will be sent separately |  | BOD: 6.45 TSS: 3.60 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | 12:00 AM
07/20/2023 | Alternative |  | {FIPSCode}-STS-17112 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/20/2023 |  | 13.200000 |  |  | 15.400000 |  |  | Will be sent separately |  | BOD: 13.2 TSS: 15.4 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 12:00 AM
07/11/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced peta in (5) Puraflo modules. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | Dec 30 1899 12:46PM
03/15/2023 |  | RoutineScheduled | 177-19-0099-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
10/12/2023 | Alternative | RoutineScheduled | 2006-143-0087 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1000 | 750 | 250 | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Disinfection","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 11:00 AM
12/13/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  | 375.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 10:12 AM
02/23/2023 |  | Routine/Scheduled | 550-STS-6756 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | UV | 750.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [5 empty] | 02/23/2023 | Sample Chamber | [8 empty] | 180 day post install inspection / service. Primary septic tank - effluent screen heavily clogged - serviced. Processing Tank - recirc pump, spray grid & media drapes serviced. U.V. - bulb and housing serviced. Pump Tank - float sensors, pump and controls operating. Lab Samples obtained for BOD5, TSS, & E-Coliform and transported to Universal Laboratories, Hampton. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | Jan 1 1900 7:00AM
08/29/2023 | Alternative | Routine/Scheduled | 234-09 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 10:55AM
12/20/2023 | Alternative | Reportable Incident |  | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the control panel NOT in alarm condition and system in normal level. I put control panel in TEST mode and confirmed pumps and floats were functioning properly. I noted inflow from the recirculation Inlet which could indicate a leaking fixture within the residence or groundwater infiltration from the septic tank of the main residence. I noted alarm issues that began on 12/11 and corrected itself and then another on 12/18. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | Dec 30 1899 8:39AM
12/11/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/11/2023 | Dec 30 1899 10:10AM
08/11/2023 | Alternative | Initial Visit | 163-STS-335141 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  |  |  | Gravity | Pressure | Drip | Not Applicable |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 04:15 PM
08/22/2023 | Alternative | Routine/Scheduled | 2017-143-0021 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Septic tank pumped out, filter cleaned, manifold flushed, uv bulb changed, removed scum from recirc chamber. Recirc pump replaced. System should return to normal operation. Panel reset. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/22/2023 | 01:35 PM
09/25/2023 | Alternative | Routine/Scheduled | CBAD-B3HGWP | Amelia | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Piedmont | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/25/2023 | Dec 30 1899 2:07PM
06/11/2023 | Alternative | RoutineScheduled | SD-02-191 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Multiflo | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | [15 empty] | informal No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/20/2023 | 07:40 AM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Was unable to inspect drain field covered with brush and high weeds. Needs bushhogged and mowed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air line from blower to the Whitewater unit appears to be obstructed. No aeration is occurring. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance | 107-07-0448 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Control panel Replaced breaker and contactor in another panel | This AOSS should now return to normal function after having provided the above state routine maintenance | 07/06/2023 | 08:40 AM
01/26/2023 | Alternative | Routine/Scheduled | 151-03-379 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | 04:12 PM
01/16/2023 |  | Routine/Scheduled | 01-120-0445A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing TAnk - RSV, recirc pump & effluents screen serviced. Treatment Module - media drapes & spray grid serviced. DBox is deep bury - not accessed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | Jan 1 1900 7:30AM
10/26/2023 | Alternative | Routine/Scheduled | 154-03-0532 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Manifold flushed. Filter was clogged. Septic tank needs a pump out. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | 01:22 PM
01/30/2023 |  | RoutineScheduled | SP-95-228 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
03/28/2023 |  | RoutineScheduled | 107-05-0303 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Recirculation Pump"] | ["Effluent Screens","Recirculation Pump"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
05/11/2023 |  | RoutineScheduled | 177-07-0198-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
09/26/2023 | Alternative | Reportable Incident Component Maintenance | 099-07-0081-SP | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to look at broken manifold for drip tubing caused by trees that were up rooted. Proposal to be sent to repair the system. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/02/2023 | 05:18 AM
08/14/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1000 | anua (puraflo) |  | Pump | Gravity | Trenches | Not Applicable | 100.000000 | ["Effluent Screens"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Dark Brown | [15 empty] | The septic tank was recently pumped out within the last year. the homeowner is going to add yeast to help build the micro's bacteria up in the tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 10:30 AM
10/23/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 12:10PM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
06/06/2023 |  |  |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip | Not Applicable | 228.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/12/2023 | 08:00 PM
06/17/2023 | Alternative | RoutineScheduled | 2050-03-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 6.800000 |  |  | 2.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/02/2023 | 12:00 AM
11/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Fuji clog cleared | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
08/10/2023 | Alternative |  | SD-09-006 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan |  |  | Roger | Gibson | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | 182-08-0199 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 11/27/2023 |  | 120.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample not normal due to bad blower which was replaced | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
08/28/2023 | Alternative | RoutineScheduled | 12-100-0348 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1500 | AQUASAFE |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | NA | [17 empty] | SLUDGE JUDGE 5" FROM BOTTOM, 2" FROM TOP EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 02:20 PM
11/04/2023 | Alternative | RoutineScheduled | 109-05-0911 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 500 | MultiFlo ATU |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank - 1" solids crust, 8" of solids in bottom. Excellent aeration and treatment quality. Discharge pump tank low. Removed pressure bell and tested. Cleaned drip manifold spin filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 07:03 PM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0248 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Gravity | Gravity | Pad | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] |  | NA | Musty | Clear | 121.000000 | 5.100000 |  | 0.000000 |  | 07/19/2023 |  | 13.000000 |  | 1600.000000 | 66.000000 |  |  | Will be sent separately | Inspected | Needs Ecopod blower & UV bulb & chord. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 08/15/2023 | 01:44 PM
04/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/07/2023 |  |  | 2004-143-0224 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/08/2023 | 12:00 AM
03/27/2023 | Alternative | Routine/Scheduled | 093-07-0193 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | Dec 30 1899 2:16PM
09/01/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-64150 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
10/25/2023 | Alternative |  | 18-100-0018 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
05/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
03/31/2023 |  | RoutineScheduled | 154-08-0113 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled | 061-16-277 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [5 empty] | 03/14/2023 | Pump Chamber | 8.000000 | [5 empty] | Will be sent separately | Inspected | Completed annual inspection and collected effluent sample for 5-year BOD test. Drip system is a continuous flush so measurement of drip rate is only a gross approximation, and the flush rate cannot even be estimated. Only 1 nozzle in the EZ Treat pod needed cleaning. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
12/06/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.290000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:45 PM
10/16/2023 | Alternative | RoutineScheduled | 107-03-0163 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | [5 empty] | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | homeowner to schedule pumping of FAST | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
09/12/2023 | Alternative | Reportable Incident | 136-14-0092 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | 9/12 Alarm Call: - Came out for an alarm call on a ecopod. Found the co tool breaker tripped in the panel for discharge tank. Reset it and the air pump alarm came out and tripped again. The air pump is stealing power from the control breaker for discharge tank. Air blower is bad, air filter is falling apart and air housing is deteriorated. Control panel is aged but still working 9/19 Annual maintenance and install: -Installation of new Ecopod Blower -Installation of an Ecopod 1" Intake Filter-Installation of a 1" piping intake Filter Assembly -Installation of new Orenco MVP control panel. Connection to existing electrical. -Septic Tank: Found the septic tank at normal level. Has 6 inches of sludge and less than 1 inch of solids. -Discharge/Pump Tank: Found at normal level. Had less than 1inch of sludge and solids. Float and pump are aged but working. -Aeration: Found at normal level. Has 3 of suspended solids. -Air Pump/Blower: Air pump has 120 volts. Both audio and visual alarms are working as they should. The pump pulled 3.4 amps. -Control Panel: Control panel has 120 volts. Both audio and visual alarms are working as they should. The pump pulled 5.3 amps. -Distribution Box: Unable to locate distribution box need permit. -Drain Field: No signs of surfacing in drain field area. 9/22 Install -Installation of a Liberty Pump includes: - Removal & disposal of spent Pump - Manufacturer Warranty -Installation of a Plumbing Kit -Installation of 3 new Floats Installation of a Float Tree Assembly to secure Floats -Conduit & Wiring up to 10' | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | 01:33 PM
02/27/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Microfast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 6' of sludge and zero scum in septic tank,3" loose sludge in microfast side. zero sludge in pump tank. 216 hrs of pump time. Blower is operational, pump is operational, Blower alarm working, Tank alarm is working. Walked Filed had two leaks, Fixed the next day. Everything is working as intended. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | 10:30 AM
12/11/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.120000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | 01:45 PM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Equalization tank, aerobic treatment unit & pump tank pumped by Septi Clean. The Septic tank was partially pumped. Pumping of the remainder of the Septic Tank is scheduled for 6/19/2023 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
05/25/2023 | Alternative | RoutineScheduled | 181-04-0278 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 4.000000 | 4000 | Septic Tank |  | Pump | Pressure | Trenches | Not Applicable | 800.000000 | [] | [] | NO | [17 empty] | Semi-annual inspection of LPD #4; HD ID 181-04-0278. No visible sign of malfunction in area of LPD trenches; cycled both the transfer pump (8.02 amps) and LPD pump (15.76 amps) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0219-SWP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Distribution Pump Operation" ,"Dispersal System Operation" ,"Auxiliary Filter"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, there is effluent surfacing in the dispersal area. Additionally, the tanks show signs of groundwater infiltration. We recommend contacting an Alternative Onsite Soil Evaluator (AOSE) for repair or replacement options. 2/21/24: Per email from Ed Scott to MWebb: "These customers were referred to an AOSE for repair or replacement options. I have a letter in the file from 2009 that recommended to the owner at that time that they contact the system designer because the tanks were leaking, and we were concerned about the drip dispersal area's ability to absorb water." | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | 08:44 AM
09/04/2023 | Alternative | Routine/Scheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Best 1 |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/04/2023 | 10:30 AM
11/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [17 empty] | Septic Tank-3"sludge 2"scum/ Microfast ATU Tank-2"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and the blower is working correctly/ Found the redundant off float and timer enable float were faulty and were replaced during inspection/ Controls, pump, floats and alarms are now working correctly/ UV-Light sleeve was cleaned and light is functioning properly/ Counts: Pump-3047 ETM-386h 44m/ On-7m 54s Off-3h/ High counts-11/ Watermeter-0060010.59/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Other"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | Air leak fixed at blower. Drip field being cleared off | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 12:00 AM
10/13/2023 | Alternative |  | 137-34-067 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | [9 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | Repair | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/19/2023 | 09:05 AM
10/31/2023 | Alternative | Routine/Scheduled | 085-STS-33647 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the lid on the Clearstream tank. The septic tank has a lot of grease in it again. The timer is set to 2.5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | Dec 30 1899 11:30AM
04/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/20/2023 | Alternative | Routine/Scheduled | 03-120-0400A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge pump plumbing has exceeded life expectancy. Discharge floats have exceeded life expectancy -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. Media sheets have exceeded life expectancy. Media lid safety support struts have failed -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | Dec 30 1899 3:23PM
03/06/2023 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed N140/115v effluent pump, 2" brass check valve & 3 control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
11/22/2023 | Alternative | Reportable Incident | 101-STS-92805 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed pump. Rebuild failed aerator. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/09/2023 | Alternative | Routine/Scheduled | 18-174-0044 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/09/2023 | Dec 30 1899 12:45PM
12/28/2023 | Alternative | RoutineScheduled | 181-05-0369 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Filter checked and cleaned. Control panel functioning properly. System did not need to be pumped. No apparent leaks in system or drain field area. Lids properly secured | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2024 | 08:45 PM
11/30/2023 | Alternative | Follow-Up | 800-STS-13899 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped out the septic tank and sludge from the Clearstream tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | Dec 30 1899 9:00AM
10/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank to Puraflo Pump Tank #1 | Pump Tank #2 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation"] | [] | YES | [17 empty] | Septic Tank-14"sludge 1"scum/ Pump Tank #1-2"sludge 0"scum/ Pump Tank #2-2"sludge 0"scum/ May need pump out of the septic tank next year/ Counts for Puraflo Pumps: Pump1-011987 ETM-0023318/ Pump2-011941 ETM-0022520 On-1m 8s Off-2h/ Counts to Pump Tank #2: Pump1-018585 ETM-0077426/ Pump2-018193 ETM-0077261/ Controls, pumps, floats and alarms are functioning properly/ Puraflo Peat turned in all 6 modules and is in good condition/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/10/2023 | Alternative | Routine/Scheduled | 810-STS-3773 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 11:15AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/14/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Control Operation"] | ["Control Operation"] | NA | [17 empty] | Service call only: Replaced 2 faulty pump contactors in the duplex drip panel. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/27/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed Microfast blower. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/13/2023 | Dec 30 1899 11:23AM
01/10/2023 |  | RoutineScheduled | 195-Discharge-29122 Jeb Syuart Hwy | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/10/2023 | 12:00 AM
09/18/2023 | Alternative | RoutineScheduled | -STS-43351 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [7 empty] | 09/18/2023 | Pump Chamber | 1.000000 |  |  | 0.780000 |  |  | Attached to this report |  | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The recirculating pump was pulled and cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The BOD and TSS were within the permitted limits. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 5:00PM
07/26/2023 | Alternative | RoutineScheduled | 04-142-0511 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/05/2023 | Alternative | Routine/Scheduled | 151-15-2015 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 07:26 PM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator is not functioning. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
10/09/2023 | Alternative | RoutineScheduled | 177-STS-89445 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/01/2023 | Alternative | RoutineScheduled | C-122-14-0045 | Craig | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1500 | BioMicrobics Microfast 0.5 |  | Gravity | Gravity | Trenches | Not Applicable | 250.000000 | ["None"] | ["None"] | NA | [17 empty] | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/03/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0051 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
01/18/2023 |  | RoutineScheduled | 12-100-0008 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1500 | ELJEN |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | EVERYTHING WORKING. PUMPED SLUDGE. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/21/2023 | 08:45 AM
08/11/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 | 1000 | 1000 | Pump |  | Drip | Not Applicable |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 12:00 AM
06/29/2023 | Alternative | Reportable Incident |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | Distribution Pump Operation | Distribution Pump Operation | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/27/2023 | 11:45 AM
02/24/2023 |  | Routine/Scheduled | 095-STS-5018 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/24/2023 | Jan 1 1900 10:07AM
07/03/2023 | Alternative | RoutineScheduled | 175-05-0011 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Mckim Septic and Pumping | 1942001330 | Michelle | McKim | 1.000000 | 2000 |  |  | Pump | Gravity | Mound | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/20/2023 | 07:35 AM
05/17/2023 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Jan 1 1900 2:40PM
05/11/2023 | Alternative |  | 099-08-0206-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
08/17/2023 | Alternative | RoutineScheduled | 175-10-0330 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 4.000000 |  | Septic Tank #1 | Septic Tank #2 | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank #1-18"sludge 6"scum (Requires Pump Out) Septic Tank #2-4"sludge 0"scum/ Advantex Recirculation Tank-2"scum 0"scum/ Discharge Pump Tank to Trenches-2"sludge 0"scum/ Recirc. Pump intake cleaned/ AX-20 media in good condition, no ponding/ Controls, pumps, floats and alarms functioning properly/ No breakout or spongy areas on the drainfield. Separate Tank, grinder pump #2 is not working and requires replacement. Pump Model # E840 2HP (230 Volts) To be replaced at a later date. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/20/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
09/05/2023 | Alternative | RoutineScheduled | 09-192-117 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | SANDFILTER SYSTEM |  | Gravity | Gravity | Trenches | Chlorination | 200.000000 | ["Disinfection","Septic Tank Baffles","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Disinfection","Septic Tank Baffles","Dispersal System Operation","Level Sensor Operation"] | NA | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/05/2023 | 12:00 AM
05/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA |  |  | 7.500000 |  |  |  |  | 05/03/2023 | Sample Chamber | 17.000000 |  | 1600.000000 | 22.000000 |  |  | Attached to this report |  | Septic Tank-4"sludge 1"scum/ Microfast-0"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-358 ETM-12h 7m/ Pump2-349 ETM-11h 51m/ Peak-96/ High-24/ Duel UV-Light sleeves cleaned and bubbler working properly | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air release valve was damaged. It was replaced at time of inspection. Inlet tee is same as noted in original inspection, but does not appear to be causing an issue at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/14/2023 | Alternative | Follow-Up | 093-17-0011 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped out and cleaned the Clearstream tank and the pump tank. Replaced the replaced UV ballast and replaced the UV light bulb. Raised the aerator. Disconnected the pressure switch on the aerator and cut UV off due to the pumping of the tanks. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/14/2023 | Dec 30 1899 9:00AM
04/20/2023 |  | RoutineScheduled | SWP-05-154 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The air release valve & housing will be replaced the week of 4/24/2023. The sewer line is entering the septic tank at a slight uphill angle. It is not causing a problem at the present time but may need to be addressed in the future to prevent solids from accumulating in the line. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
12/15/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/15/2023 | Dec 30 1899 9:16AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Power surge last week tripped Microfast blower breaker. Breaker was reset and system should return to designed operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower breaker had tripped. It was reset and the blower is working as designed now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/13/2023 | Alternative |  | 10-125-001 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 09/13/2023 |  | 5.380000 |  |  | 6.400000 |  |  | Will be sent separately |  | BOD: 5.38 TSS: 6.40 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/13/2023 | 12:00 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20268 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
04/13/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Septic tank had minimal Scum and 12" sludge, In advantex recirc zone 12" sludge and 10" sludge on discharge end. Biofilter was very dirty-cleaned good- Alarms in history for filter clog-8-29-22, it was cleaned well then too -Floats tested good. ran in test mode. Discharge pump in alt status- days trended 4086 in memory start date 2-4-2-12- Flushed and brushed sprayers and Sprayed off media, also dirty. System is operational.. System had not alarms since september last year due to filter clog. 2024.3 hrs on pump run and 96447 cycles on recirc pump-- 1790 hrs and 9394 cycles on discahrge pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-01-281 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/10/2023 | 10:02 AM
11/20/2023 | Alternative | RoutineScheduled | 18-192-146 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [15 empty] | 4 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/20/2023 | 12:00 AM
04/26/2023 |  | Reportable Incident | 177-08-0220-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Owner requested 2nd opinion for problematic septic system. Tanks were pumped about 2 weeks ago. Owner said control panel had indicated alarm, but did not give an audible. None of the solenoids would operate automatically which led to high level alarms. Siemens processor indicated that system has been in peak mode almost twice as long as standard. Other operator had left solenoid valves manually open as a temporary solution and recommended replacing all wires in conduit. Blower was very hot and not running. Atu panel had been silenced and alarm bulb was burnt out. Replaced alarm horn and atu bulb, restored those alarm functions. Resting effluent level was about 4" above the media. Replaced 1/3 hp FPZ blower with a 1/2 hp blower (as recommended by Delta for deeper effluent setups). Also replaced a deformed 2" pvc 90* elbow and raised the blower base a few inches to decrease the likelihood of flooding in the event of a high level condition. The atu media was set too close to the outlet end of tank so that it is impossible to measure accumulated sludge in the clarifying end of the tank and makes pump-outs more difficult as well. Recommend moving the media back towards inlet end of tank. Installer (or perhaps other operator) had extended 12 ga wires in the hydraulic unit with butt splices in order to more easily reach the American Mfg wire harness and reconnected there with more butt splices. After removing half a roll of black tape, it was discovered that all of the butt spices had failed and wires were broken. American Mfg harness was discarded, 8" 12 ga extensions discarded, and all solenoids directly connected to the incoming 12 ga wires with wire nuts and dielectric grease as a corrosion inhibitor. Test cycles showed all solenoids working again, but also that both of the zone check valves were not closing properly. Clear evidence of groundwater infiltration observed at the septic tank inlet riser joints. Will send a repair proposal to the owner to address these remaining issues. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
06/23/2023 | Alternative | RoutineScheduled | 181-02-0012 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Recirculating Sand Filter | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | The system did not need to be pumped. The spin filter was pulled and cleaned. The controls were operating as designed. The sand filter was operating as designed. There was return effluent returning to the pump tank from the drip field so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 09:00 PM
02/14/2023 |  | RoutineScheduled | 177-14-0159-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Attached Growth Medium"] | NA | Pungent | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Sheets were very dirty and the odor was strong due to recirc thank needing pump out (due to grease and scum accumulation). Cleaned discharge pump intake and spider valve. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/10/2023 | Alternative | RoutineScheduled | 150-18-0020 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Level Sensor Operation","Effluent Screens","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | YES | [6 empty] | Aerator replaced due to non-function | [9 empty] | Pumped Out | Recommend pumping in 2-3 years | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 01:10 PM
01/24/2023 |  | Routine/Scheduled | 550-STS-6646 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/24/2023 |  | 15.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 7:20AM
06/07/2023 | Alternative | Reportable Incident | 147-17-0044 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Norweco Singulair ATU |  | Pump | Pressure | Mound | Not Applicable | 600.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | System repair conducted. Repaired damaged cleanout. Replaced failed aspirator Serviced system. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/19/2023 | Dec 30 1899 10:30AM
12/06/2023 | Alternative | RoutineScheduled | 09-160-0240 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 1.000000 | 1000 | MICROFAST |  | Pump | Pressure | Trenches | Not Applicable |  | [] | [] | [17 empty] | Inspected | - SAMPLE TAP NEEDS TO BE INSTALLED FOR FUTURE SAMPLE COLLECTION - OVERGROWTH ON DRAINFIELD NEEDS TO BE REMOVED FOR FUTURE MAINTENANCE VISITS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | cod | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
08/09/2023 | Alternative | Routine/Scheduled | 234-16-385 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 10:49AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
10/12/2023 | Alternative | RoutineScheduled | 151-05-318 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/12/2023 | Alternative | Reportable Incident | 157-05-039 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm call: -Came out for a consultation for an alarm going off. Opened system and system was at normal level. Found high level float flipped up on top of the weir. Spoke with Julie customer sister stated that she found a toilet running for an unknown amount of time. The system is a time dose system. Verified all components were working in the septic system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | 02:08 PM
03/14/2023 |  | RoutineScheduled | 099-STS-91695 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 03/14/2023 |  | 5.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Blower alarm was going off due to current point needing adjustment, adjusted ,tested and everything works good. Bottom trench was bleeding so adjusted dialflows so it should dry out soon, told customer to keep us posted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
03/23/2023 |  | Pump-Out Only | {FIPSCode}-STS-2132 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/23/2023 | Jan 1 1900 11:45AM
11/17/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0303-VU | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Pump is not easily accessible without entering the tank. Evidence of infiltration (wet roots) observed at inlet end of septic tank, buried wedge lid. A repair proposal will be provided to the owner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
09/07/2023 | Alternative | Routine/Scheduled | 149-STS-10673 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/07/2023 | Dec 30 1899 10:53AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/12/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0396-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
01/05/2023 | Alternative | RoutineScheduled | SD-10-247 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [8 empty] | 18329.000000 | [] | [] | [8 empty] | 01/05/2023 | Sample Tap | 6.000000 |  |  | 2.800000 | 4.700000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 12:00 AM
07/12/2023 | Alternative | RoutineScheduled | 132-18-0026 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 12:00 AM
09/29/2023 | Alternative | Pump-Out Only | R15-180-0067 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Montgomery Sanitation Services, Inc. | 1942001003 | Brittany | Conner | [9 empty] | [] | [] | [16 empty] | Will be sent separately | Pumped Out | - pumped/cleaned pump chamber - cleaned onsite filter - Advanced Environmental completing inspections, everything functional based on our scope, refer to Mr.Rice's report for more extensive results | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 12:00 AM
01/04/2023 |  | Initial Visit | 800-STS-13178 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm and red light - installed an aerator rebuild kit. Serviced system. Checked the pump, panel, and floats (ok). Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV light bulb, replaced the UV cord, and replaced the UV ballast. The timer is set to 3.5 minutes every 2 hours. Did not take samples due to the aerator not working on arrival. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/04/2022 | Jan 1 1900 10:00AM
09/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | Dec 30 1899 2:20PM
07/19/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-4754 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 8:35AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87436 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
06/13/2023 | Alternative |  | 09-163-0115 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Recirculation Pump","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 12:00 AM
07/05/2023 | Alternative | Reportable Incident | 147-15-0098 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Replaced the UV ballast and replaced the UV light cord. The septic tank needs to be pumped, all of the trash needs to be pumped out of the Clearstream tank, and the pump tank should be pumped out as well - dirty. The timer is set to 5 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | Dec 30 1899 3:45PM
10/04/2023 | Alternative | RoutineScheduled | 10-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-86742 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Two compartment microfast due to sludge levels homeowner to make arrangements. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-24805 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 05/17/2023 |  | 2.000000 |  | 4.000000 |  |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
06/01/2023 |  |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | YES | [17 empty] | 48" Liquid depth, 12" of sludge 0 in pump tank. Filter clean. Floats, Alarm, and pump operational. Peat is ok. Will need replenished or updated soon,22156 events, 431.94 hrs on pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 05:45 PM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
02/01/2023 | Alternative | Routine/Scheduled | 151-14-0054 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3500 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | 05:44 PM
03/02/2023 |  | RoutineScheduled | 175-06-0231 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
03/13/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Floats replaced. System should begin to function correctly shortly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/15/2023 | Alternative | Routine/Scheduled | 08-163-0100 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Normal level 7 in of sludge 1 in of solids No signs of infiltration Recirculation Tank Condition of above Component Notes for above Component Normal level 5 in of suspended solids Tested floats and pump all working as should However floats and pump are aged Pulled and cleaned pump All plumbing intact and moving water properly No signs of infiltration RSV (Recirculating Splitter Valve) Condition of above Component Notes for above Component Pulled sprayed off and flushed check ball and grommet Discharge/Pump Tank Condition of above Component Notes for above Component Normal level 7 in of suspended solids Tested floats and pump all working as should However floats and pump are aged All plumbing intact and pump moving water properly Orenco junction box is cut open No signs of infiltration Media Sheets Condition of above Component Notes for above Component Brushed and flushed laterals Sprayed off sheets clean Flushed module until water ran clear Control Panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Discharge pump pulled 11.7 amps Recirc pump pulled 11.7 amps All components working as should however panel is aged LPD Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 10:27AM
03/27/2023 |  |  | 2017-143-0100 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Eco flo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
06/02/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | Control Operation | Control Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 12:29 PM
01/06/2023 |  | Routine/Scheduled | 234-15-419 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 1:55PM
06/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
05/09/2023 | Alternative | RoutineScheduled | 133-STS-95396 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed UV ballast. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/22/2023 | Alternative | RoutineScheduled | 09-160-0149 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 2.000000 | 1500 | BioMicrobics MicroFAST 0.5 |  | Pump | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Replaced blower, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/27/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-14"sludge 4"scum/ Microfast ATU-16"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Control, pumps, floats and alarms functioning properly/ Counts: Pump1-1581 ETM-97h 30m/ Pump2-1516 ETM-93h 39m/On-3m 45s Off-10h / Peak Off-8h/ Peak cnts-25/ High cnts-17/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/15/2023 | Alternative | Reportable Incident | 234-12-32 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/11/2023 | Dec 30 1899 8:00AM
02/14/2023 |  | RoutineScheduled | 149-STS-20262 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | UV Bulb needs replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/13/2023 | 11:23 AM
11/17/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88941 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Disinfection" ,"Control Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Disinfection" ,"Attached Growth Medium" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. UV bulb replaced. RECIRC: HL-444, LL-17, OVERRIDE-1111. DISCHARGE: HL-7, LL-29, OVERRIDE-20. "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
06/05/2023 | Alternative | Follow-Up | C18-180-0082 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 |  | ATL |  | Pump | Gravity |  |  |  | [] | [] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | 12:00 AM
10/19/2023 | Alternative | Routine/Scheduled | 147-17-0108 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal level 3 in of sludge 1 in of solids No signs of infiltration -Discharge/Pump Tank: Normal level Less than 1 in of suspended solids Tested floats and pump all working as should Splice box intact Plumbing intact and pump moving water properly Riser showing signs of leaking -Aeration: Normal level aeration properly moving water Line running from aeration to trash tank intact and properly working -Air Pump/Blower: 120 volts coming in Blower pulled 1.96 amps -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Pump pulled 8.6 amps All components properly working -Distribution Box: Customer didn't want us to dig up at this time 14ft 8in from control panel 20in deep -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 12:57PM
11/30/2023 | Alternative | Follow-Up | 03-197-A16 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity |  | Chlorination | [10 empty] | No Tablets | [10 empty] | No tablets in the system | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/30/2023 | 12:00 AM
04/26/2023 | Alternative |  | SD-15-147 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [8 empty] | 04/26/2023 | Sample Tap | 115.000000 |  |  | 222.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
05/25/2023 |  | RoutineScheduled | 113-STS-25632 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 1.000000 | 1500 | MicroFast 0.625 |  | Gravity | Gravity | Trenches |  |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | NA | [7 empty] | 05/25/2023 | Sample Tap | 12.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20472 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [5 empty] | 06/08/2023 |  | 60.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 06:25 AM
03/02/2023 |  | RoutineScheduled | SD-06-133 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, the tank has started to collapse on the top. It should continue to be monitored. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/11/2023 | Alternative | RoutineScheduled | 09-192-012 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation"] |  | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/11/2023 | 12:00 AM
08/09/2023 | Alternative | Routine/Scheduled | 550-STS-6614 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 11:45AM
03/04/2023 |  |  | 2042-97-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | SBR |  | Pump | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | 7.900000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
01/16/2023 | Alternative | Reportable Incident | 073-STS-105150 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 Replaced access risers on septic tank and pump tank. Installed cannister style effluent screen in septic tank. Replaced pump, float sensors, plumbing and controls in pump tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/17/2023 | 07:00 AM
02/17/2023 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 01:19 PM
08/31/2023 | Alternative | RoutineScheduled | 109-07-0338 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Other conventional maintenance performed | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | Musty | [15 empty] | Inspected | Peat moss is in good condition Added 5 Peat moss bags to the system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | 09:30 PM
06/22/2023 | Alternative | Pump-Out Only | 033-10-0158-SWP | Caroline | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 450 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | SludgeScum Accumulation | SludgeScum Accumulation | N/A | [16 empty] | Pumped Out | Trash tank pumped out. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/22/2023 | 01:20 PM
03/23/2023 |  | RoutineScheduled | SWP-05-161 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/31/2023 | Alternative | Reportable Incident |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | Attached Growth Medium | NO | [17 empty] | Removed media drapes and mounting hardware. Replaced mounting hardware with new. Replaced media drapes with new. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | Dec 30 1899 11:00AM
11/17/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank Pumped | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 2.000000 | [8 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/14/2023 | Alternative | Routine/Scheduled | 109-07-0250 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 02:15 PM
08/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/16/2023 | Alternative | RoutineScheduled | 119-STS-95935 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/16/2023 |  | Follow-Up | SWP-05-545 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to replace broken effluent filter and inspected peat moss. Peat moss is no longer saturated. Running toliet has been corrected. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
12/17/2023 | Alternative | Reportable Incident | 03-120-0400A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the control panel in alarm condition indicating recirculation tank in high level. Checked and confirmed recirculation tank in high level. Put control panel in TEST mode and confirmed components were cycling properly. Noted that the RSV began to overflow. Checked inside discharge and noted inlet was clogged with roots. Homeowner gave written approval for repair. He has family coming in this week and wants repairs to be completed before the weekend. I disconnected audible alarm for the time being and it will need to be reconnected after repairs are completed. Repairs to be completed 12/19 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/18/2023 | Dec 30 1899 10:32AM
03/10/2023 | Alternative | Routine/Scheduled | 196-15-0040 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routien Service Primary septic tank - normal level - effluent screen serviced. Biofilter - peatmoss in good condition - raked / turned Pump Basin - float sensors, pump and controls operating. DBox - itnact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 10:00 AM
08/15/2023 | Alternative | RoutineScheduled | SD-03-11 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-6"sludge 0"scum/ Pump Tank-2"sludge/ No pump out needed at this time/Two Puraflo Modules were ponding/ Cleared the drainage holes and drained the modules then turned the peat in all 5 modules/ Peat is ok at this time but may require replacement next year/ Controls, pump, floats and alarms were functioning properly/ Counts: Pump-137867 ETM-0,338,078/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/12/2023 |  | Routine/Scheduled | 2006-143-0141 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 01:30 PM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There are four small trees planted near the end of the lines. Advised homeowner of potential issues and recommended moving them. Lower corner of the field on the house side appears to be evenly nitrified. Recommend homeowner monitor for changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/12/2023 | Alternative | Follow-Up Component Maintenance | 177-12-0076-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pump out. Reassembled components and water truck refilled back to proper levels. Replaced 2 valve covers in dripfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | alarm unplugged outlet pipe settled on tank repaired recirc line | This AOSS should now return to normal function after having provided the above state routine maintenance | 07/06/2023 | 08:40 AM
06/28/2023 | Alternative | Routine/Scheduled | 17-174-0174 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | Dec 30 1899 1:00PM
04/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
11/14/2023 | Alternative | RoutineScheduled | 08-113-162 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | [17 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/14/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0307-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Dusted off air filter. Compressor running at 1.55 amps. Treatment looks good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
02/28/2023 |  | RoutineScheduled | 033-STS-91677 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Dispersal System Operation" ,"Level Sensor Operation"] | ["Dispersal System Operation" ,"Level Sensor Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The broken return line and defective float have been repaired by the installer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
06/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 11:17 AM
06/07/2023 | Alternative | Follow-Up | C 800-17-0229 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Hooked up the pressure switch on the aerator and the UV. Installed an aerator rebuild kit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/07/2023 | Dec 30 1899 12:00PM
04/14/2023 |  |  | 06-142-0282 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Mircofast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 12:00 AM
09/08/2023 | Alternative | Reportable Incident Component Maintenance | 099-15-0093 SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed pump from wipes getting into pump intake. Replaced pump. Media floated due to high level. Will make follow up visit to address blower and media. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
05/10/2023 | Alternative | Reportable Incident | 136-05-0340 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | NO | [16 empty] | Pumped Out | System in failure - Pumped all components for storage. Septic tank has multiple fractures - effluent screen in bottom of tank - no riser access. BioFilter - flooded on arrival - peatmoss spent - requires replacing. Pump Basin - Plastic - crushed - Pump failure - float sensor failure - pump basin requires replacing. Dbox - fractured - below normal level. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/25/2023 | 09:00 AM
12/15/2023 | Alternative | Follow-Up | 133-STS-94950 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed float switch. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/22/2023 |  | RoutineScheduled | 179-STS-90003 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced uv bulb. Treatment Chrystal clear. RECIRC: HL 15, LL 22,, OVERRIDE 3177. DISCHARGE: HL 7, LL 21, OVERRIDE 41. "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
06/20/2023 | Alternative | Routine/Scheduled | 196-11-034 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 04:29 PM
10/24/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/07/2023 | Alternative | RoutineScheduled | VAG401984 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Gravity | Gravity | Discharge | UV |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The recirculating pump was pulled and sprayed off. The UV light was cleaned. The controls were operating as designed. The evaporation bed was operating as designed. There were no samples drawn at the time of visit because there was no discharge. The house is not being occupied at this time. The lids were secured. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/11/2023 | 08:20 PM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Middle Module is fully saturated and has standing water to the lip of the module | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/04/2023 | 06:02 AM
12/21/2023 | Alternative | RoutineScheduled | VAG408472 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Gravity | Discharge | UV |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [18 empty] | no disharge at this time | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/04/2024 | 12:00 AM
03/14/2023 | Alternative | Routine/Scheduled | 800-11-0087 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  |  |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Dec 30 1899 1:26PM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | [8 empty] | 09/14/2023 | Pump Chamber | 148.000000 | [5 empty] | Will be sent separately |  | BOD sample taken from inlet of pump tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 9:00AM
08/15/2023 | Alternative | RoutineScheduled | 101-18-0261 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | AquaSafe |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/20/2023 | Alternative | Routine/Scheduled | 095-STS-6947 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/20/2023 | Dec 30 1899 9:30AM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0361-SP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Septic Tank Needs Pumping | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/29/2023 | 03:58 AM
10/30/2023 | Alternative |  | 08-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | TIffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | MicroFast Tank needs pumping | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | Dec 30 1899 2:41PM
08/31/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes clogged with biomat - recommend replacing - spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - minor root infestation removed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | Dec 30 1899 11:30AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/17/2023 | Alternative |  | 09-142-0240 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
10/13/2023 | Alternative | Follow-Up | {FIPSCode}-STS-20069 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 | ATU | [10 empty] | None | Clear |  |  |  | 0.000000 | [11 empty] | Tablets in place | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12:00 AM
02/24/2023 | Alternative | Follow-Up | SD-04-210 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to inspect tanks and electrical components for the system. Infiltration on both and pump is not pumping at the proper rate.Proposal to be sent to correct these issues with the system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
04/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
08/14/2023 | Alternative | RoutineScheduled | 07-163-0038 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
12/26/2023 | Alternative | Reportable Incident Component Maintenance | {FIPSCode}-STS-84699 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in a low level alarm due to recirc tank being pumped down prior to my site visit. Discharge floats installed by another company were not set properly. Reset floats. Discharge pump keeps getting airlocked due sluge levels in pump tank or pump is pumping down hill. Pump tank to be pumped out and we need records for the system. Then another site visit to be made. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
05/02/2023 | Alternative |  | 18-100-0018 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [9 empty] | Sample Tap | 0.000000 |  | 248.100000 | 0.000000 | 2.400000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
08/30/2023 | Alternative | RoutineScheduled | 195-Discharge-15326 Greenway Rd. | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/30/2023 | 12:00 AM
04/28/2023 | Alternative |  | 195-STS-27191 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/28/2023 | 12:00 AM
05/30/2023 |  | Routine/Scheduled | 18-120-0330AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | Jan 1 1900 9:59AM
10/25/2023 | Alternative |  | SP-05-449 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/10/2023 |  | RoutineScheduled | 179-08-0248-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Whitewater ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
10/11/2023 | Alternative | RoutineScheduled | SD-11-263 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Distribution Pump Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Dispersal System Operation"] | YES | Sulphitic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 12:00 AM
11/29/2023 | Alternative |  | {FIPSCode}-STS-19119 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/29/2023 |  | 11.500000 |  |  | 6.000000 |  |  | Will be sent separately |  | BOD: 11.5 TSS: 6.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 12:00 AM
03/07/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | Jan 1 1900 12:26PM
03/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
04/01/2023 | Alternative | Routine/Scheduled | 06-160-0277 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | SludgeScum Accumulation | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/01/2023 | 01:30 PM
07/11/2023 | Alternative |  | SP-05-580 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
03/01/2023 |  | RoutineScheduled | 2045-02-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  |  |  | NA |  |  | 6.900000 | 15.100000 |  | 1.200000 | [9 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
08/10/2023 | Alternative | RoutineScheduled | 2018-143-0026 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Other"] | ["Other"] | [18 empty] | Replaced Orenco UV Bulb | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/21/2023 | Alternative | RoutineScheduled | VAG408017 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | [9 empty] | ["None"] | [] | [18 empty] | no discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/21/2023 | 12:00 AM
12/21/2023 | Alternative | RoutineScheduled | 181-13-0042 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was pulled and cleaned. The treatment unit was in good operating condition. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2024 | 05:50 PM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20291 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | Musty | Clear | 7.000000 |  |  | 3.600000 | [9 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 07/07/2023 | 06:25 AM
04/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/11/2023 | Alternative |  | 023-STS-42917 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 05/11/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | Jan 1 1900 1:15PM
01/13/2023 |  | RoutineScheduled | 13-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/13/2023 | 12:00 AM
09/22/2023 | Alternative | Routine/Scheduled | 023-STS-42774 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Pad | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [7 empty] | 11/02/2023 | Pump Chamber | 17.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | Dec 30 1899 11:30AM
03/06/2023 |  | RoutineScheduled | 2014-143-0183 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | EcoPOD |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/09/2023 | 12:00 AM
11/16/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-0166-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | NA | Septic | Cloudy | [5 empty] | 11/16/2023 |  | 220.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken, most likely will fail. Treatment did not look good due to blower not working (tripped outlet) reset outlet and blower started working 1.50 amps. Treatment should go back to normal in a few days. Small trees growing around D-box recommend to clear 10' around it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
07/10/2023 | Alternative | RoutineScheduled | 181-08-0188 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was cleaned. The six inch pipe had pulled up out of the unit so it was dug up and the grommet was reinstalled. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/31/2023 | 09:35 PM
01/26/2023 | Alternative | RoutineScheduled | SD-15-147 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [8 empty] | 01/26/2023 | Sample Tap | 139.000000 |  |  | 105.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
05/10/2023 |  |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/06/2023 | Alternative | RoutineScheduled | SD-05-149 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Installed new spin filter & effluent pump. Follow-up visit planned to complete system drawdown. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
10/23/2023 | Alternative | RoutineScheduled | 05-103-294 | Amelia | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Mound | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | Pungent | Black | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 9:20AM
04/20/2023 | Alternative | Routine/Scheduled | 800-STS-15061 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | Dec 30 1899 10:30AM
09/12/2023 | Alternative | RoutineScheduled | 18-113-093 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/12/2023 | 12:00 AM
07/20/2023 | Alternative | Reportable Incident | 17-163-0149 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NO | [17 empty] | System alarming high level discharge - found brass checkvalve had failed - replaced with new ... also found air release vent damaged by lawn care operations - replaced with new. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/24/2023 | Dec 30 1899 7:15AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Need to take a sample to verify if peat fiber needs replaced. Very broken down and sandy | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
06/23/2023 | Alternative | RoutineScheduled | 07-113-006 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets added 8 - Bio Max tablets added | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/23/2023 | 12:00 AM
03/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/13/2023 | 11:23 AM
12/08/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 1:05PM
04/24/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/14/2023 |  | RoutineScheduled | 163-STS-338170 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | PEAT MOSS |  | Pump | Gravity | Mound | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | SYSTEM DID NOT NEED TO BE PUMPED. SEPTIC TANK FILTER WAS CLEANED. CONTROLS WERE OPERATING AS DESIGNED. NO VISIBLE LEAKS IN THE MOUND SYSTEM. THE PEAT MOSS WAS RAKED AND THE TIPPING TRAYS WERE SPRAYED OFF. LIDS WERE SECURED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 09:45 PM
12/13/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser and changed the filter in the aerator. Meet with the pumping company and pumped the septic tank out and the sludge from the Clearstream tank. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 9:00AM
03/09/2023 |  | RoutineScheduled | 175-10-0117 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 2"scum/ Microfast-6"sludge/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats, hydraulic unit and alarms functioning properly/ Watermeter counts-66702.2/ No breakout or spongy areas on the drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/16/2023 | Alternative |  | 177-06-0003-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
01/26/2023 | Alternative | Reportable Incident | 073-STS-101524 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Repair - VDH Permit 136-22-0253 - GMP2018-02 Primary septic tank pumped empty and removed. Installed new 1000 gallon primary septic tank with effluent screen. Installed new 4" PVC sewer with clean out. Installed new 4" PVC Conveyance line. Installed new 8 port concrete DBox. Excavated existing laterals - installed new gravel & dispersal piping. Relocated public water line to residence which crossed existing laterals. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/30/2023 | 06:45 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | SD-06-52 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
04/19/2023 |  | RoutineScheduled | 179-14-0316-SASR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 3.06 amps. treatment is crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
07/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 12:00 AM
02/07/2023 |  | RoutineScheduled | 02-197-351 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 12:00 AM
02/20/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
01/09/2023 |  | Routine/Scheduled | 234-17-444 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 11:25AM
05/30/2023 |  | RoutineScheduled | 132-16-0042 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Pressure | Mound | Not Applicable | 1000.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
02/17/2023 | Alternative | RoutineScheduled | 154-04-0628 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
06/01/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3343 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Jan 1 1900 12:25PM
11/03/2023 | Alternative |  | ST-05-228 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/28/2023 | Alternative | Initial Visit | 036-STS-34267 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, panel, & and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1 minute every 2.25 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | Dec 30 1899 10:45AM
04/20/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2897 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | Jan 1 1900 7:30AM
03/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 6.000000 |  | Septic Tank #1 | Septic Tank #2 | Pump | Pressure | Pad | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO |  |  | 7.800000 |  |  |  |  | 03/30/2023 | Sample Chamber | 1.000000 |  |  | 7.000000 |  |  | Attached to this report |  | Septic Tank #1-0"sludge 0"scum/ Septic Tank #2/ EZ-Treat Tank #1-2"sludge 0"scum/ EZ-Treat #2-3"sludge 0"sludge/ EZ-Treat #3-3"sludge 0"scum/ Pump Tank to LPD Pad site-2"sludge 0"scum/ Tanks were just recently pumped out/ Controls, pumps, floats and alarms all functioning properly/ Counts: cc1-13930 ETM-20855/ cc2-0016254 ETM-20769/ Discharge Pumps to LPD Pad-Pump1-707 ETM-145h 52m/ Pump2-669 ETM-138h 36m/ Peak-19/ High-17/ No breakout or spongy areas on the Pad site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/17/2023 | Alternative | RoutineScheduled | 13-142-0125 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/08/2023 | Alternative | RoutineScheduled | 181-08-0154 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 12:00 AM
11/03/2023 | Alternative |  | 033-06-0215-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/30/2023 | Alternative | RoutineScheduled | 136-06-0187 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump | Pressure |  |  |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/13/2023 |  | RoutineScheduled | 03-125-300 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Attached Growth Medium","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/13/2023 | 12:00 AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/27/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Pressurge Gauge replaced | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
05/04/2023 | Alternative | Routine/Scheduled | 151-05-310 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 06:52 PM
05/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Dispersal System Operation"] | ["Effluent Screens" ,"Dispersal System Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-83761 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
06/29/2023 | Alternative | Reportable Incident | 147-15-0086 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Mound | UV | 450.000000 | Control Operation | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | System in high level - overflowing from riser - single circuit from house panel powering controls, compressor, discharge pump - breaker in house tripped - recommend electrician add new 15amp circuit to power control panel. Restored power - let system pump self down to high level vs. alarm level. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | Dec 30 1899 7:15AM
01/05/2023 |  | RoutineScheduled | 08-163-0013 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton |  |  | Biomicrobics Microfast |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Auxiliary Filter"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | 12:00 AM
02/27/2023 |  |  | 099-17-0122 SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled | 17-100-0154 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Pressure | Mound | UV | 600.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | PUMPED SEPTIC TANK EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 02:10 PM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 182-12-0244 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | NA | [7 empty] | 10/11/2023 |  | 19.000000 | [5 empty] | Will be sent separately | Inspected | Lab Normal Treatment tank pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
09/20/2023 | Alternative | Routine/Scheduled | 800-06-0399 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Noted minor root infiltration around base of risers. -RSV: Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media modules. Checked and confirmed spray height is good. Media lid hinges are failing. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. Removed root infiltration -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | Dec 30 1899 2:22PM
02/28/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Panel silence button not working | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
06/29/2023 | Alternative | RoutineScheduled | 15-142-0208 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [18 empty] | Replaced bad discharge pump with a new one on 6-29-23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/28/2023 | Alternative | RoutineScheduled | 96-100-0924 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1500 | PURAFLO |  | Pump | Gravity | Mound | Not Applicable |  | [] | [] | NA | [17 empty] | SLUDGE JUDGE REVEALED 8-9" FROM BOTTOM, 1-2" FROM TOP REPLACED PEAT RECENLTY NEW N98 SEWAGE PUMP, TD1 PANEL AND REISERS INSTALLED AND RECENTLY PUMPED SEWAGE EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | 01:35 PM
01/05/2023 |  |  | 2012-143-0076 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | Replace agitator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/01/2023 | 12:00 AM
01/06/2023 |  | Routine/Scheduled | 234-16-29 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | Replaced timer and pump relay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 8:40AM
08/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1000 | Septic | Micro fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/01/2023 | Alternative | RoutineScheduled | VAG401576 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | NA | Musty | Clear | [15 empty] | no discharge during visit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
04/04/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/10/2023 |  | RoutineScheduled | 175-16-0299 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
04/17/2023 |  | Routine/Scheduled |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Annual Service. Processing Tank - RSV, recirc pump ^ effluent screen serviced. Treatment Module - media drapes & spray grid serviced. U.V. - bulb and housing serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | Jan 1 1900 7:00AM
08/29/2023 | Alternative | Routine/Scheduled | NYII-AZMPW2 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 2:10PM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/27/2023 | Alternative | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 01:36 PM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 12:49 PM
08/09/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 08/09/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:30 PM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 12:00 AM
10/17/2023 | Alternative | Initial Visit |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 3.400000 |  | 2.000000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The timer is set to 5 minutes every 1 hour 55 minutes. Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 4:30PM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance | ST-05-11 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The peat in the Puraflo modules is in good condition but has settled. Also, there was standing water in the sample chamber. There was no evidence of water surfacing in the pad site and the pad did not appear to be holding water when probed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
04/12/2023 |  |  | 157-13-0069 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | UV |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:00 AM
04/17/2023 |  | RoutineScheduled | 2008-143-0126 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Effluent Screens","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:00 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Tree that was next to the distribution boxes in the past has been cut down. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/27/2023 | Alternative | Reportable Incident | -STS-15910 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 3.000000 | [7 empty] | Owner called due to the light being on - toilet was hung up - no alarm on arrival. Serviced system. Checked the pump, panel, and floats (ok). Changed the filter in the aerator. The Clearstream tank and septic tank need to be pumped out. Took 5 year BOD sample. The timer is set to 4 minutes every 2.5 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | Dec 30 1899 1:45PM
02/27/2023 |  |  | 099-16-0108 SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
06/19/2023 | Alternative | RoutineScheduled | 175-04-0537 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-2"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Puraflo Peat turned in all 5 modules and in good condition at this time/ Counts: Pump-040299 ETM-0076035 On-53s Off-2h 35 gal. per dose / No breakout or spongy areas on the Pad site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/21/2023 | Alternative | Reportable Incident | 166-05-789 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | -Installation of new Orenco MVP control panel. Connection to existing electrical. -Installation of 2 new Floats | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/26/2023 | 08:46 AM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0991 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
08/25/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Gravity | Trenches |  | 600.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 11:28 AM
05/01/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | alarm was off | This AOSS should now return to normal function after having provided the above state routine maintenance | 06/21/2023 | 03:35 PM
05/19/2023 | Alternative | RoutineScheduled | C10-180-0013 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Level Sensor Operation"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Septic zone -1" scum - 8-10" sludge- Recirc zone 1" scum - 16" sludge Newish color, Discharge 12-14" sludge- Pump runs slow, Cleaned Biofilter(Very Dirty-backed up), cleaned effluent filter, clogged and backed up- Pulled and cleaned-pumps, Flushed and brushed sprayer manifold, sprayed off media, float switches operational, Returned on May 26th to replace the discharge on float due to its failure.. Both pumps are opperational. Pulled recirculation pump PF300511 anbd cleaned it very dirty . Good Spray after service. Cleaned Discharge pump- we will observe the level and decide after next year inspection if it needs pumping next year..Alarm in history cleared after service. recirc pump run time 2443.6 hours and 30415 cycles and discharge pump run time 3772.2 hours and 94668 cycles. System has had issue with infiltration in the past. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
09/11/2023 | Alternative | Routine/Scheduled | 550-STS-6317 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | Dec 30 1899 1:00PM
08/11/2023 | Alternative | RoutineScheduled | SD-10-167 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | Pura-flo | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 09:00 AM
04/18/2023 |  | Routine/Scheduled | 041-STS-260797 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/18/2023 | Jan 1 1900 4:05PM
03/08/2023 |  | RoutineScheduled | 175-02-0387 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
03/06/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
05/23/2023 |  | Routine/Scheduled | 06-142-0552 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 750.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing tank - RSV, recirc pump and effluent screen serviced. Treatment Modules (2) - media drapes & spray grids serviced. Pump Tank - float sensors, pump and controls operating. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Jan 1 1900 9:30AM
10/18/2023 | Alternative | Routine/Scheduled | 04-160-0233 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 04:00 PM
02/02/2023 |  | RoutineScheduled | 177-STS-88666 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Replaced blower panel & raised blower housing 8". | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
03/09/2023 |  | RoutineScheduled | 179-STS-88638 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank lid has some cracks. Strongly recommend before it becomes a safety hazard. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Distribution box has lots of roots in in. Restricting flow from the modules to the field. Alarm was not functioning. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
07/26/2023 | Alternative | Reportable Incident | 150-15-0041 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Pad | UV | 450.000000 | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | N/A | [17 empty] | System alarming over weekend due to blown diaphragms in compressor. Compressor replaced with new - U.V. disinfection bulb replaced. System due for full service in October. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/27/2023 | 09:15 AM
11/10/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 6.000000 |  | 20.000000 | [5 empty] | Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | Dec 30 1899 12:00PM
12/14/2023 | Alternative | Routine/Scheduled | 800-STS-13809 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 1:15PM
11/28/2023 | Alternative | RoutineScheduled | 2016-143-0067 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [17 empty] | Pumped Out | Replaced Blower | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/07/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | 12:00 AM
03/02/2023 | Alternative | Pump-Out Only Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank Pumped | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim |  | 1250 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/05/2023 | Dec 30 1899 12:00PM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
05/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Micro Fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-356 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
09/22/2023 | Alternative | RoutineScheduled | 07-197-A8 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | FAST |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/22/2023 | 12:00 AM
11/02/2023 | Alternative | Follow-Up |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Multiflo FTB |  | Pump | Gravity | Trenches |  | 450.000000 | Distribution Pump Operation | Distribution Pump Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/22/2023 | 12:33 PM
04/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Other"] | ["BlowerCompressorAerator Operation","Other"] | [8 empty] | 05/16/2023 | Sample Chamber | 8.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Microfast-0"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Blower air filter cleaned and blower working correctly/ Counts: Pump1-51 ETM-1h 39m/ Pump2-41 ETM-1h 28m/ High-29/ Peak-30/ Outlet riser of the ATU is leaking and requires resealing/ No breakout or spongy areas on the drainfield. Returned on 4/27/2023 and resealed risers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 |  | RoutineScheduled | 02-163-0142 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton |  |  | Advantex |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","Effluent Screens","Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
09/15/2023 | Alternative | Follow-Up | 175-97-0239 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Other"] | ["Other"] | [18 empty] | Follow up: Patch the pump tank damaged concrete riser/ Replaced the junction box and rewired the floats and pumps/ Replaced the LPD Globe Valve Handles and cleaned the inside of the valve. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski |  |  | 1 |  | Pump | Pressure | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [17 empty] | 1 Pump and 1 check valve replaced- top replaced on Pressure Valve Clean Pump chamber for access/ Homeowner selling property | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/15/2023 | Dec 30 1899 3:30PM
04/28/2023 | Alternative | RoutineScheduled | 031-STS-26638 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Septic Tank | Anua SBR-Single Batch Reactor | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Musty | [15 empty] | Inspected | Sludge levels--trace scum and 6-20" sludge trace- Side port 5-6" trace sludge, 2nd visit, Aerator 926:26 hours, Sludge 39:11 hours and discharge 16:44 hours - contacted company rep who is sending new alarm unit to replace the bad one. Drainfield maintained by owner looks good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
11/30/2023 | Alternative | Pump-Out Only |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | Dec 30 1899 1:30PM
01/20/2023 |  | RoutineScheduled | 12-125-036 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 2 Chlorine 7 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/20/2023 | 12:00 AM
12/26/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0166-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Effluent filter was clogged but able to clean | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
08/14/2023 | Alternative | Routine/Scheduled | 800-05-0295 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | Dec 30 1899 2:11PM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"SludgeScum Accumulation"] | NO | [15 empty] | Will be sent separately | Inspected | Pump chamber was full when I arrived and alarm had been silenced. Pump chamber needs to be pumped out and inspected for ground water infiltration. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/13/2024 | Dec 30 1899 11:49AM
11/17/2023 | Alternative | Routine/Scheduled | 15-172-0330A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/17/2023 | Dec 30 1899 9:53AM
04/18/2023 |  | RoutineScheduled | 88-184-93 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 11 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/18/2023 | 12:00 AM
02/10/2023 |  | Reportable Incident | 177-11-0225-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Nibbler dozing tank had a bad float (off) replaced. Ran pump for couple minutes to get tank out of high level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
12/21/2023 | Alternative |  | 101-15-0496 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | John & Mattice | Jensen | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | Dec 30 1899 12:15PM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance | 107-02-0307 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Valve box lid replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
12/28/2023 | Alternative |  | 175-05-0011 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Septic and pumping | 1942001330 | Michelle | McKim | 1.000000 | 2000 |  |  | Pump | Gravity | Mound | Not Applicable |  | [] | ["SludgeScum Accumulation","Level Sensor Operation","Septic Tank Baffles","Distribution Pump Operation","Dispersal System Operation","BlowerCompressorAerator Operation","Control Operation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/12/2024 | 08:30 AM
03/16/2023 |  | RoutineScheduled | 179-10-0098-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media showing its age, evaluate next year. Riser on pump tank has a cracked, gorilla tape sealing it holding good, customer wants us to call before we come out next year with price for new riser to get it done same day of inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
08/29/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-4989 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 11:35AM
03/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance | SD-03-111 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
04/28/2023 |  |  | VAG408422 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST ATU | Constructed Wetlands | Gravity | Gravity | Discharge |  |  | ["Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation"] |  | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/07/2023 | 10:30 AM
10/23/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 8.420000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 02:30 PM
04/04/2023 |  | RoutineScheduled | 165-STS-336759 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","SludgeScum Accumulation","Septic Tank Baffles","Dispersal System Operation"] | ["Septic Tank Baffles","Auxiliary Filter","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
07/27/2023 | Alternative |  | 02-113-176 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/27/2023 |  | 9.700000 |  |  | 6.800000 |  |  | Will be sent separately |  | BOD: 9.70 TSS: 6.80 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/27/2023 | 12:00 AM
02/01/2023 |  |  | 033-06-0392-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
07/31/2023 | Alternative | Routine/Scheduled | 550-STS-6575 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | Dec 30 1899 11:20AM
09/28/2023 | Alternative | RoutineScheduled |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 3.000000 | 4500 | Bio Microbics 4.0 | Bio Microbics 4.5 | Pump | Pressure | Drip | Not Applicable | 2500.000000 | ["Other"] | ["Other"] |  | Musty | Clear | 5.900000 | 4.800000 |  |  |  | 09/28/2023 | Pump Chamber | 14.000000 |  |  | 3.300000 | 11.000000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 10:15 AM
05/23/2023 |  |  |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecopod | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected | Recommend that the grease traps be pumped as soon as possible | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled | 101-04-0759 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/23/2023 | 12:00 AM
07/11/2023 | Alternative | Pump-Out Only | 159-13-0151 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Multiflo FTB |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - pumped septic tank / trash tank only as recommended during Real Estate Inspection - System due for full maintenance - new owner has concerns about standing water in yard. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 10:30 AM
03/07/2023 |  | RoutineScheduled | SWP-05-448 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
03/20/2023 |  | RoutineScheduled | 179-STS-87383 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Blower running at 3.02 amps. Measured 33 - 35 psi on return line pressure gauge. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
04/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
05/07/2023 |  | Initial Visit | VPDES-92-02 | Madison | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic | Singulair | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | None | Clear | [14 empty] | Pumped Out |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/16/2023 | 12:00 PM
11/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | Dec 30 1899 3:50PM
01/28/2023 | Alternative |  | 132-04-0061 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Matthew | Aldridge | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/01/2023 |  | Follow-Up | 179-STS-90029 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  |  |  | NA | [7 empty] | 02/01/2023 |  | 15.000000 |  | 1.800000 |  |  |  | Will be sent separately | Inspected | BOD failed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/04/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 6" of accumulated solids in septic tank. Cleaned septic tank filter. Flushed treatment unit spray manifold. 0" of solids in recirculation portion of treatment unit. 2" of solids in discharge portion of treatment unit. Cleaned recirculation pump intake screen. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | 07:03 PM
06/19/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 9:00AM
08/03/2023 | Alternative | RoutineScheduled | 03-160-0378 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | [16 empty] | Inspected | - blower is not functioning, needs to be replaced - unable to hear alarm nor confirm that is it working - recommend both tanks be pumped and cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/05/2023 | 12:00 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-15-0087-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/23/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | McKim Septic & Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | NA | [16 empty] | Pumped Out | Pumped out septic and atu microfast | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/28/2023 | Dec 30 1899 3:00PM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-08-0305 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | dirt needs to be off pvc pipes and blower rec removing bushes due to roots | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
09/22/2023 | Alternative | Routine/Scheduled | 02-163-0065 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Customer had it pumped beginning of the week. Less than 1in of sludge and solids. Pulled and cleaned filter. -Aeration: Tank had been pumped and refilled. Less than 1in of sludge and solids. Pulled and cleaned weir. Non serviceable air line. High level float full of water. Riser has root intrusion -Air Pump/Blower: Pulled and cleaned air filter. Air pressure sensor working as it should. Customer broke the light and is getting the parts to fix it today. -Control Panel: 120 volts. Air pump pulled 1.5 amps. Customer is fixing the alarm light, getting parts in today. -Distribution Box: Found below normal level, due to system had been pumped. Found 4 lines taking water. 3 of the 4 lines have roots growing down them. Pulled what I could out. Roots growing in around corregated header lines -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | Dec 30 1899 1:54PM
01/12/2023 | Alternative | Reportable Incident | 073-STS-101859 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2400 | None | None | Gravity | Gravity | Trenches | Not Applicable | 1200.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | COSS - Repair - VDH Permit 136-22-339 - GMP2018-02 One tank pumped empty, crushed and removed. Installed new 1200 gallon concrete, mid-seam tank in same location. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/16/2023 | 07:00 AM
04/20/2023 |  | RoutineScheduled | 153-STS-20356 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Environmental CONST, SVC | 1942001123 | bill | tucker | 1.000000 | 1500 | Miro fast |  | Pump | Pressure | Drip | UV | 450.000000 | ["None"] | ["None"] | YES | Musty | Clear | [15 empty] | system is working as per design. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/20/2023 | 09:00 AM
05/17/2023 |  | RoutineScheduled | 153-STS-20346 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Other"] | ["Other"] | YES | [17 empty] | Septic Tank-4"sludge 2"scum/ EZ-Treat Recirculation Tank-0"sludge 0"scum/ Need pump out of the Septic- Recirc Tank due to issues with the bacteria/ Pump Tank-0"sludge 0"scum/ Controls, pump, float and alarms functioning properly/ Recirc. pump intake cleaned/ Counts: Pump-001565 ETM-000508/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/07/2023 | Alternative | Routine/Scheduled |  | Frederick | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Sandfilter, Recirculating |  | Pump | Pressure | Discharge | Chlorination | 600.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [18 empty] | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 08/17/2023 | 01:00 PM
05/02/2023 |  |  | 99-184-5002 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/02/2023 |  | 1.300000 |  |  | 2.330000 |  |  | Will be sent separately |  | BOD: 2.33 TSS: 1.30 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Trim Trees back from all lids and blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
08/12/2023 | Alternative | RoutineScheduled | 109-05-0545 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 500 | Orenco Advantex AX20 |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 24" of accumulated solids in septic tank. The need for a pump out will be determined next year, new owners since last inspection. Cleaned recirculation pump basket filter. Flushed both treatment unit's spray manifolds. Tested floats, pump and alarm. treatment unit lid located closest to walkway was damaged during pavement preparation. The lid was removed at the time of inspection and was covered by a sheet of plywood. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 07:03 PM
07/19/2023 | Alternative | RoutineScheduled | SD-11-370 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | PuraFlo | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["Control Operation","SludgeScum Accumulation"] | ["Control Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled | VAG401764 | Bath | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | NA | [17 empty] | The system did need to be pumped, however the house is vacant through the winter and the land owner requested to wait until the spring to pump the system. The blower filter was pulled and cleaned. The treatment unit was in good operating condition. The wet lands bed was in good operating condition. The chlorine and de-chlorine tablets were added to the tablet feeders. The controls were operating as designed. There were no samples drawn because there were no discharge at the time of inspection. The lids were secured. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/17/2024 | 05:40 PM
01/27/2023 |  | Reportable Incident | 177-10-0037-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EcoPod | none | Pump | Gravity | Pad | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in high level. Met pumper onsite pumped out pump tank and inspected. No damage to tank seen. Check valve was slowly letting water drain back into the tank. Replaced check valve and discharge pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
04/25/2023 |  | Routine/Scheduled | 234-13-346 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 12:45PM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/17/2023 | 12:46 PM
11/13/2023 | Alternative | RoutineScheduled | 195-STS-27344 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/18/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 9.900000 |  | 2.000000 | [5 empty] | Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | Dec 30 1899 8:00AM
11/22/2023 | Alternative | Reportable Incident | 033-STS-92431 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | James Lee Miller III | 1942001468 | Kevin | Blasing | [29 empty] | Arrived on site to give pricing for 4 module puraflo. Did not give quotes | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 09:08 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/22/2023 | Alternative | Routine/Scheduled | 05-190-036 | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - surge box lid fractured - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/01/2023 | Dec 30 1899 7:30AM
01/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/07/2023 |  | RoutineScheduled | SWP-04-124 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
06/19/2023 | Alternative | Routine/Scheduled | 800-06-0386 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 1:45PM
06/04/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. 8" of solids in discharge pump tank. Cleaned recirculation pump solids basket filter. Cleaned drip field manifold spin filter. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 07:03 PM
11/22/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/29/2024 | 01:02 PM
04/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | all 6 pods are full of effluent. Need to further investigate as to why? | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
10/20/2023 | Alternative | RoutineScheduled | 89-113-155 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/20/2023 | 12:00 AM
07/26/2023 | Alternative | RoutineScheduled | 165-STS-333675 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | [9 empty] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
03/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Great Falls Septic | 2705051738 | Joshua | Hott | 1.000000 | 1875 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Over saturated need to install pure flow system pumps. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
11/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | UV Bulb replaced while on site. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/06/2023 | Dec 30 1899 9:34AM
10/16/2023 | Alternative |  | 099-16-0022 SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0324 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Disinfection" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/15/2023 | 01:44 PM
10/31/2023 | Alternative | RoutineScheduled | 133-STS-96766 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filter, system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/10/2023 |  | RoutineScheduled | 10-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","SludgeScum Accumulation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 6 Dechlorine 1 discharge sign | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/10/2023 | 12:00 AM
01/19/2023 |  | Reportable Incident |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"SludgeScum Accumulation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Tank in high level due to failed pump. Tank pumped by Powell's Plumbing. Cleaned and removed all sludge and debris. Spin filter was very dirty again. Extended the spin filter rinse line a couple of feet past the pump so that the effluent would not get churned up by the splashing. It is believed that this churning up of solids close to the pump intake is what was causing the spin filter to get so dirty. Removed the failed pump and installed a used, loaner pump until the new one is received. Replaced the air filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
07/07/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was replaced and the aeration component of the system appears to be functioning as designed at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
10/10/2023 | Alternative | Routine/Scheduled | 12-142-0160 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Outlet tee appears to be intact. Due for pump out. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed water level sensors are functioning properly. Flushed and cleaned disk filter. -Aeration: Water level normal. Confirmed aeration is occurring -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly -Drip Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 2:58PM
07/07/2023 | Alternative | Routine/Scheduled | 128.00.207 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen servcied. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. LPP Field = no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | 08:30 AM
05/24/2023 |  |  | 33-STS-88948 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Fuji | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/25/2023 |  | RoutineScheduled | 033-STS-88967 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance | 175-12-0049 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | new filter, bottom and middle float, blowers panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air blower needs replaced not working. The microfast tank needs pumped out and 1 lateral end is broken and needs fixed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
02/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/28/2023 | Alternative | Routine/Scheduled | 2011-143-0139 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/28/2023 | 03:51 PM
08/30/2023 | Alternative | RoutineScheduled | 175-18-0280 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-10"sludge 6"scum/ Microfast-14"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time but a pump out may be needed next year/ Blower air filter cleaned and blower is working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-3651 ETM-521h 35m/ Secondary Counts-1/ High-14 On-15m Off-6h/ Watermeter-022,484.9/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/03/2023 |  | Routine/Scheduled | 234-16-93 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced timer enable float and UV cord | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | Jan 1 1900 2:35PM
11/23/2023 | Alternative |  | 132-05-0123 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Jennifer | Lyons | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/25/2023 | Alternative | RoutineScheduled | SD-15-088 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Recirculation Pump" ,"Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Cleaned 2 brass nozzles; one was completely clogged and not spraying. Plugged alarm horn wire back in. Showed owner how to check float screen in processor if alarms reoccur. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
06/23/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/25/2023 | Alternative | Follow-Up | 093-16-0133 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped out the septic tank and trash from the Clearstream tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Dec 30 1899 12:00PM
08/03/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89434 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection and replaced UV bulb. System was in alarm due to enable float being stuck on letting the system get into a low level. Replaced enable float. Recirc H/L: 7 and L/L: 9 Dis H/L: 6 and L/L: 37 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | SD-13-115 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Gravity | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Attached Growth Medium"] | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Attached Growth Medium"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
10/18/2023 | Alternative | RoutineScheduled | 015-STS-334226 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Septic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
05/23/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump was replaced and the system appears to be functioning as designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/22/2023 | Alternative | Reportable Incident | 119-STS-105959 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced degraded Dbox with new 8 port concrete DBox. Spliced to existing Conveyance Line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | 12:00 PM
03/07/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 12:00 AM
10/20/2023 | Alternative | Routine/Scheduled | 150-06-237 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge pump has exceeded life expectancy. Discharge pump plumbing has exceeded life expectancy. Discharge floats have exceeded life expectancy. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 01:58 PM
01/27/2023 | Alternative |  | 132-07-0051 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Robert | Allen | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/10/2023 | Alternative |  | 033-18-0050-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/26/2023 | Alternative | Routine/Scheduled | 04-120-0183A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 5 Modules (white) - Peatmoss in poor condition - raked / turned. Dbox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | Dec 30 1899 9:30AM
12/05/2023 | Alternative | RoutineScheduled | 101-04-0570 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Gravity | Gravity | Trenches | Not Applicable | 150.000000 | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 11:00 AM
03/10/2023 |  | RoutineScheduled | 86-197-244 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/10/2023 | 12:00 AM
10/30/2023 | Alternative | Routine/Scheduled | 041-STS-260467 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | Dec 30 1899 1:14PM
04/13/2023 |  | Routine/Scheduled | 133 05 1201 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 01:45 PM
09/14/2023 | Alternative | RoutineScheduled | 16-183-005 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/14/2023 | 12:00 AM
01/09/2023 |  | Routine/Scheduled | 196-11-088 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 50.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 05:36 PM
06/28/2023 | Alternative | Routine/Scheduled | 228-19-0046 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | Dec 30 1899 12:30PM
09/19/2023 | Alternative | Routine/Scheduled | 15-160-0097 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | EcoPod |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 04:45 PM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0533-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Could not givr contract due to infiltration on both tanks proposal to be sent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
05/31/2023 |  | RoutineScheduled | 175-05-0141 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank- 4"sludge 2"scum/ Microfast-6"sludge / Pump Tank-0"sludge / No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-28187 ETM-280452/ No breakout or spongy areas on the drip mini- mound. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/09/2023 |  | Reportable Incident | SP-05-117 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High water alarm sounded on atu control panel (red light on). Cleaned dirty brush filter which dropped the effluent level and cleared the alarm. Pump tank at normal level. Owner said inside alarm did not sound. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
01/31/2023 |  | Reportable Incident | 153-STS-20269 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation","BlowerCompressorAerator Operation"] | ["Dispersal System Operation","BlowerCompressorAerator Operation"] | NA | [17 empty] | Service call only: Repair- Installed 2 solenoids for zones 1&2/ Replaced faulty water meter current reading is 0, former reading on the old meter was 1,041,611/ Replaced old blower with new Microfast Blower. System now functing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
03/22/2023 |  | Routine/Scheduled | 01-120-0841A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/22/2023 | Jan 1 1900 5:31PM
06/07/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
10/23/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 9:25AM
08/01/2023 | Alternative |  | 17-113-126 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/01/2023 |  | 2.390000 |  |  | 1.400000 |  |  | Will be sent separately |  | BOD: 2.39 TSS: 1.40 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/01/2023 | 12:00 AM
05/04/2023 | Alternative | Initial Visit | C06-180-0233 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 500 | BioMicrobics MicroFast |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | YES | [17 empty] | Initial visit. Septic tank recently pumped out because of concerns with solids in the discharge pump tank. 0" of accumulated solids in septic tank. 0" of solids in treatment unit. 6" of solids in discharge pump tank. Drip field spin filter very clean. Blower providing adequate aeration. Tested pump. Homeowner indicated that water softener was connected to the AOSS. Advised homeowner to disconnect water softener from AOSS to prevent toxicity to bacteria and bulk flows potentially washing out solids. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Jan 1 1900 7:03PM
12/13/2023 | Alternative | Routine/Scheduled | A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Puraflo |  | Pump | Gravity | Pad |  |  | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/13/2023 | Dec 30 1899 9:33AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-91639 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [5 empty] | 10/26/2023 |  | 18.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Treatment is clear but could be better, left copy of Do's and don'ts. Blower 3.01 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
04/13/2023 |  | Routine/Scheduled | 133 13 0314 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 11:00 AM
02/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/03/2023 |  | Routine/Scheduled | 234-16-14 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | Jan 1 1900 1:00PM
08/30/2023 | Alternative | RoutineScheduled | 181-06-0300 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 2.000000 | 2500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. Septic system did not need to be pumped. No apparent leaks in system or drain field area. Control panel, blower, and all alarms functioning properly. Lids were properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/16/2023 | 09:35 AM
05/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/28/2023 |  | Pump-Out Only | 199-17-0009 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | NO | [16 empty] | Pumped Out | AOSS - Pumpout of trash tank as recommended during last service event. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Jan 1 1900 11:15AM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0908 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Recommend adding a riser to grade at the septic tank inlet. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
05/02/2023 |  | RoutineScheduled | 175-06-0127 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
02/01/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.200000 |  | 30.000000 |  |  | 02/01/2023 |  | 40.000000 |  |  | 26.200000 |  |  |  |  | Will revisit and resample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:00 AM
02/02/2023 |  |  | 2004-143-0115 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected | The filter on the outlet had been removed and was sitting by the riser. We cleaned it and re-installed it like it should be. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
05/07/2023 | Alternative | RoutineScheduled | 001-STS-92824 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJICLEAN |  | Pump | Pressure | Mound | UV | 300.000000 | [] | [] | [18 empty] | EVERYTHIN WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/11/2023 | 12:25 PM
07/05/2023 | Alternative | Reportable Incident | 234-13-297 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | Dec 30 1899 1:00PM
11/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 2250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/14/2023 |  | Follow-Up | 550-STS-6402 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 2.000000 | [7 empty] | Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | Jan 1 1900 12:00PM
08/10/2023 | Alternative | Routine/Scheduled |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level - recommend pumpout. Aeration tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - normal level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | Dec 30 1899 12:45PM
11/07/2023 | Alternative | RoutineScheduled |  | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 12:00 AM
10/11/2023 | Alternative | RoutineScheduled | 2016-143-0262 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The aerator was not functioning and was replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408261 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Chlorination |  | ["Control Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Alarm on control panel not operating and needs repaired. Contact us if want this performed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/11/2023 | 11:17 AM
11/02/2023 | Alternative | Routine/Scheduled | C102-06-0008 | Alleghany | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | Control Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/02/2023 | Dec 30 1899 3:00PM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
12/18/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Trenches | Not Applicable | 300.000000 | ["None"] | ["Attached Growth Medium","Control Operation","Disinfection","Distribution Pump Operation","Dispersal System Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
10/04/2023 | Alternative | Initial Visit | 810-STS-4057 | Virginia Beach | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 11.000000 |  | 2.000000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the UV light bulb. Changed the filter in the aerator and changed the mesh screen in the spinfilter (full of paint). All of the tanks need to be pumped out to paint in the tanks. The septic tank needs a 24" Tuf-Tite lid. The timer is set to 5 minutes every 1 hour. Took initial BOD and Fecal samples. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/04/2023 | Dec 30 1899 11:30AM
02/28/2023 |  | RoutineScheduled | 177-STS-88733 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | EZ Treat Sandfilter | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/11/2024 | 01:04 PM
07/13/2023 | Alternative | RoutineScheduled Component Maintenance | 177-13-0289-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Effluent Screens" ,"Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
08/29/2023 | Alternative | Reportable Incident | 228-14-0398 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | Control Operation | Control Operation | N/A | [17 empty] | Replaced timer | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/29/2023 | Dec 30 1899 5:30PM
02/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/06/2023 | Alternative | Routine/Scheduled | 12-160-0170 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | EcoPod |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 11:30 AM
05/22/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [9 empty] | Distribution Pump Operation | Distribution Pump Operation | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 10:33 AM
12/20/2023 | Alternative | RoutineScheduled | 03-142-0438 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
03/13/2023 |  | RoutineScheduled | 003-STS-31417 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/19/2023 | 12:00 AM
11/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Gravity |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 10:55AM
09/25/2023 | Alternative | RoutineScheduled | 13-184-004 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | PRESBY |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Dispersal System Operation","SludgeScum Accumulation"] | ["Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | 12:00 AM
01/10/2023 |  | RoutineScheduled | 195-STS-26571 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Ez Treat |  | Pump | Pressure | Discharge | UV | 200.000000 | ["Attached Growth Medium","Disinfection","Auxiliary Filter","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Disinfection","Auxiliary Filter","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/10/2023 | 12:00 AM
01/11/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.400000 |  |  |  |  | 01/11/2023 |  | 217.000000 |  |  | 106.200000 |  |  |  |  | Sludge at 50%- Advised client to pump and we will resample. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | 12:15 PM
08/04/2023 | Alternative | Pump-Out Only |  | Warren | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 1.000000 | 1000 | [7 empty] | [] | ["Other"] | NA | [16 empty] | Pumped Out | Fuji tank all compartments pumped out and hosed out. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 08/06/2023 | 04:30 PM
12/14/2023 | Alternative | Follow-Up Component Maintenance | 177-07-0324-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new blower, blower control panel, diaphragm, and headworks box heater. Raised blower to prevent flooding. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
03/31/2023 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced E191 effluent pump, 2" check valve & (4) control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
09/13/2023 | Alternative | RoutineScheduled | 04-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/13/2023 | 12:00 AM
08/18/2023 | Alternative | RoutineScheduled | 107-04-0553 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
04/24/2023 |  | Initial Visit | 107-05-0673 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | blower running hot. removed blockage in FAST | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/22/2023 | 12:00 AM
07/26/2023 | Alternative |  | 06-195-518-DIS | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 |  | 5.410000 |  |  | 4.300000 |  |  | Will be sent separately |  | BOD: 5.41 TSS: 4.30 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/26/2023 | 12:00 AM
05/09/2023 |  | RoutineScheduled | 199-12-0048 | York | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Clearstream |  | Gravity | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/09/2023 | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation","BlowerCompressorAerator Operation"] | ["Level Sensor Operation","BlowerCompressorAerator Operation"] | NA | [7 empty] | 10/18/2023 | Sample Chamber | 78.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 4"scum/ Microfast-6"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned/ Blower settings were incorrect, corrected the settings and blower to now run continuously/ Found faulty outside alarm and alarm float replaced during the inspection/ Controls, pumps, floats and alarms are now functioning properly/ Counts: Pump1-2636 ETM-67h 49m/ Pump2-2601 ETM-66h 59m/ Peak-368/ High-52077/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
07/13/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
05/08/2023 |  |  | 2013-143-0106 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-335570 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired pipe in advantex pod | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM
09/29/2023 | Alternative | Pump-Out Only | 147-19-0055 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | 9/29/23 Truck 606 * Arrived for Pump Out * Pumped 500 Gallons from Septic Tank * Light Solids Medium Sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 10:23AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/03/2023 |  |  | 2003-143-0265 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
01/10/2023 | Alternative | Reportable Incident | SD-14-116 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced faulty pump relay. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled | 04-197-164 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/08/2023 | 12:00 AM
06/15/2023 | Alternative | RoutineScheduled | 103-STS-94415 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/13/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | septic | puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation"] | YES | [17 empty] | 0 scum, 8" of sludge in septic tank. little loose sludge in pump tank. Filter clean, peat moss looks good, raked peat and walked field looks good. 40696 events 1104.21 hrs on pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 01:00 PM
06/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/09/2023 |  | Routine/Scheduled | 196-10-002 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 05:43 PM
01/09/2023 |  | RoutineScheduled | 18-197-049 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ATL |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Auxiliary Filter","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank filter was clogged and level was very high. Filter was cleaned and the level returned to normal levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/13/2023 | Alternative | Routine/Scheduled | 151-90-0098 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 60.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 12:07 PM
10/19/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 12:00 AM
04/11/2023 |  | Initial Visit | 067-STS-39006 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Initial start-up inspection. Tightened loose union fittings, and reconnected wire connections for discharge pump. Set recirculation pump timers and override timers per homeowners indicated anticipated use. Manually ran recirculation pump and discharge pump to get water levels in treatment unit to normal levels. Set recirculation pump flow rate. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 07:03 PM
01/27/2023 | Alternative |  | 132-06-0277 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Steve | Glass | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/15/2023 |  | RoutineScheduled | {FIPSCode}-STS-73734 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Replaced uv lamp, cleaned the sleeve, and rinsed out the housing (pretty dirty). Treated effluent is cloudy, not clear. Advised owner to cut back on household disinfectants and laundry sanitizers. Drip system is a continuous flush type so the drip rate must be calculated as an average (charging rate included), and the flush rate cannot be measured at all. After a 5.25 minute test cycle today, the effluent level only dropped 5/8" (13.5 gals). The programmed run time of 5.4 minutes is supposed to move 25 gallons. In December of 2021, the rate was calculated at 2.7 gpm. So far, the owners said they haven't noticed the reduction and have not gotten any high level alarms in quite a while. In the past 30 days, the system averaged 7.2 cycles per day at a run time of 4.8 minutes. Drip tubing will need to be bleach-flushed if the rate drops any further. The 6" valve box that houses both AR valves is broken and the lid is gone. It's really nothing more than a debris blocker, so no impact on daily function. Recommend replacement with a 10" round valve box and lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
05/17/2023 | Alternative | Initial Visit | 136-06-0002 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Primary septic tank - normal level - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Splitter Box - plastic - splits to two separate absorption fields. DBox #1 - plastic - intact. Dbox #2 - plastic - intact - minor root infestation - removed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
10/27/2023 | Alternative | Routine/Scheduled | -STS-15908 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Completed real estate inspection Type of System Clearstream/aquaworx Depth to the top of the Septic Tank 0-12" below grade Riser present? Yes Was Septic Tank pumped? Yes Tank Level Normal operating level Condition of Lid: Intact Condition of Outlet Tee Satisfactory How many gallons were pumped? 500 Depth to the top of the Discharge Tank 0-12" below grade Riser present? Yes Was the Discharge Tank pumped? Yes How many gallons were pumped? 200 Condition of Lid: Intact Type of Electrical Connection: ? Junction Box Aeration: Was tank pumped at time of inspection? No Does tank require pumping? No Sludge Judge Levels Lite sludge no solids Was alarm present? Yes Was the air pump/blower serviced at time of inspection? Yes Overall function of the Blower: Satisfactory Was the control panel powered at time of inspection? Yes Were alarms tested at time of inspection? Yes Overall function of Control Panels Satisfactory Was the field flushed during inspection? Yes | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | Dec 30 1899 8:30AM
07/17/2023 | Alternative | Routine/Scheduled | 151-11-0043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | None | None | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Alternative Dispersal Only - ELJEN Synthetic Mound. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. No indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | 07:45 AM
08/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Riser and lid were hit by mower and need replaced. Piece of plywood is covering tank opening. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | 02:41 PM
03/30/2023 |  | Routine/Scheduled | 234-19-006 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | Jan 1 1900 1:20PM
05/25/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | UV bulb, chord & plug replaced. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/15/2023 | Dec 30 1899 12:05PM
12/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 4.000000 |  | Septic / Ecopod ATU Treatment Tank | EZ-Treat Recirculation Tank to Discharge Pump Tank | Pump | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | [18 empty] | Septic Tank-6"sludge 0"scum/ Ecopod ATU-4"sludge 0"scum/ EZ-Treat Recirculation Tank- 3"sludge 0"scum/ Pump Tank to Discharge-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Norweco UV-Light sleeve cleaned and light is functioning properly/ Controls, pumps, floats and alarms are functioning properly/ Counts: EZ-Treat Pump-59809/ Discharge Counts: Pump1-3239 ETM-98h 56m/ Pump2-3100 ETM-95h 53m/ Zoeller Pumps (N-140) On-1m 12s Off-2h 59m / Peak-49/ High-53 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/18/2023 | Alternative |  | 132-19-0049 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Austin | Heyne | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-88859 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. media is partially clogged with filamentus bacteria but treatment is clear, recommend to chemical clean it (tank most likely will need pump out next year). Blower 2.95 amps. HL-4, LL-13, OVERRIDE-3. "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
11/20/2023 | Alternative |  | 027-STS-17146 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/20/2023 |  | 5.880000 |  |  | 2.000000 |  |  | Will be sent separately |  | BOD: 5.88 TSS: 2.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 12:00 AM
04/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | drain line from modules to pump chamber had broken. DSS repaired. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/15/2023 | Alternative | RoutineScheduled | 119-STS-100551 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt | Charcoal filter changed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
03/28/2023 | Alternative |  | 109-STS-31520 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Frank | Ballif | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/28/2023 | Alternative |  | {FIPSCode}-STS-59726 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
07/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/24/2023 |  | Reportable Incident |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo |  | Gravity | Gravity | Discharge | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | [16 empty] | Inspected | Septic tank 1" scum layer and 28" sludge on bottom, May want to consider arranging a pump out this fall. Treatment unit 2-3" scum on deck and light clear effluent, trace sludge, may get deck pumped off at same time the septic is pumped,, owner cuts drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
03/13/2023 |  | Follow-Up | SWP-05-877 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Added junction box on post U.F. wire and ran single strand wire to existing interior splice box. Added pump blocks under pump in pump tank. Assisted pumper with pump out of pump tank and refilled with water to proper operating level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
04/20/2023 |  | Routine/Scheduled | 075-STS-32891 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/20/2023 | Jan 1 1900 11:02AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/05/2023 | Alternative |  | 06-113-243 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/05/2023 |  | 4.270000 |  |  | 3.330000 |  |  | Will be sent separately |  | BOD: 4.27 TSS: 3.33 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
09/15/2023 | Alternative | RoutineScheduled | 2059-99-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | SBR |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NA | Musty | Clear | 7.400000 |  |  | 1.200000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/16/2023 | 12:00 AM
09/27/2023 | Alternative | RoutineScheduled | 061-STS-24869 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | trash | microfast | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 10:00 AM
07/11/2023 | Alternative | Initial Visit | 181-10-0025 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | [] | NA | [17 empty] | The system did need to be pumped but the land owner requested it to be pumped at a later date because he requested access risers be installed on the septic tank at the time of pumping. The system is however operating as designed. The blower filter was cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 10:50 PM
11/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 12:45PM
08/22/2023 | Alternative | Routine/Scheduled |  | Richmond City | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Richmond | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Microfast |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/22/2023 | Dec 30 1899 5:49PM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0201-SR | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens"] | ["Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | The concrete lid on the outlet of the septic tank is deteriorating and should be replaced. The peat in the Puraflo modules has deteriorated. Peat replacement is an option, or we would recommend consideration of a different treatment system. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/01/2023 | 06:26 AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 182-13-0274 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 11/13/2023 |  | 29.000000 | [5 empty] | Will be sent separately | Inspected | Replaced blower panel | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM
03/17/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/01/2023 | Alternative | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Cajun Aire ATU |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 07:30 AM
11/16/2023 | Alternative | Follow-Up Component Maintenance | 099-10-0003-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to check drip rates after repairs. Drip rate has increased to 9.675. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
02/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
07/17/2023 | Alternative | RoutineScheduled | 199-09-0068 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 | 1000 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 12:00 AM
05/02/2023 |  | Initial Visit | 182-08-0414 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | ["Attached Growth Medium","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 12:00 AM
05/05/2023 | Alternative | Routine/Scheduled | 149-STS-10702 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | Dec 30 1899 10:00AM
08/18/2023 | Alternative | Pump-Out Only |  | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation","None"] | NO | [16 empty] | Pumped Out | Pumped pump tank only. Homeowner does own maintenance - pumped SLUDGE from pump tank. Low pressure pipe system - no other maintenance performed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/21/2023 | 10:00 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
10/12/2023 | Alternative | Pump-Out Only | 15-137-0070 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Multiflo ATU |  | Pump | Pressure | Drip | Not Applicable |  | SludgeScum Accumulation | SludgeScum Accumulation | N/A | [16 empty] | Pumped Out | Septic tank pumped out | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/27/2023 | Dec 30 1899 8:54AM
12/04/2023 | Alternative | Follow-Up | 02-197-A2 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination | [10 empty] | tablets are now installed | [10 empty] | tablets now stocked | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 12/04/2023 | 12:00 AM
10/03/2023 | Alternative |  | SWP-05-755 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
02/22/2023 |  | Routine/Scheduled | 234-13-294 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 11:00AM
10/18/2023 | Alternative | Routine/Scheduled | 136-09-0108 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Annual Maintenance: -Septic Tank: Normal Level 24" of sludge and 1" of solids No riser present on tank Nomaigns of infiltration -Discharge/Pump Tank: Normal Level 1" of suspended solids All floats and pump are functioning properly however floats are Aged and attached to plumbing Plumbing is aged Signs of leaks around forcemain Riser has signs of leaks Junction box had moisture in it. Pump pulled 7.23amps -Aeration: Normal Level 30" of suspended solids Pulled and cleaned weir and diffuser -Air Pump/Blower: Air pump wasn't working upon arrival due to broken diaphragms Replace air pump on site. Air pump pulling 1.21amps Air pressure sensor functioning properly All audible and visual alarms are functioning properly -Control Panel Alarm box: 120v coming into alarm box All audible and visual alarms are functioning properly -Distribution Box: Plastic distribution box at grade in good condition with 4 lines balanced and taking water. All seals are intact nomsigns of cracks -Drain Field: No signs of surfacing Repair (10/23): -Installation of a new 2-Breaker Control Panel mounted on a Post includes installation of a wood Post -Installation of 3 new Floats(2 in discharge and 1 in aeration) Installation of a Float Tree Assembly to secure Floats in discharge -Installation of a new Air Pump -Reseal the force main Pipe: - Manually excavate the exterior of the Tank up to 24" to access the force main Pipe - Parge the interior and exterior of the Tank around the force main Pipe - Backfill excavated area -Installation of 6" - 12" Riser on Pump Tank -Installation of 6"-12" Riser on the Septic Tank -Installation of 6" - 12" Riser on Aeration Tank -Installation of a Plumbing Kit Pump out and refill (10/23): * Arrived for pump out and refill * Pumped 2000 gallons from septic and aeration tanks * Light solids and heavy sludge * Refilled aeration tank | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | 11:28 AM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-496 & SWP-02-989 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. System was on low level alarm due to clogged RSV, cleaned and used all lot of water to clean sheets, pump and biotube filter so System went back to normal. 3 drainfield lines backing up into D-box most likely due to root since drainfield is over grown. Drainfield needs clearing and lines camera snake to find the problem. HL-526, LL-416, OVERRIDE-5571. Recirc tank needs pumping due to sludge. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
03/28/2023 |  | RoutineScheduled | 95-192-211 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/28/2023 | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88775 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Septic Tank Baffles" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Recirc pump intake was partially clogged, cleaned. 1 spray nozzle was clogged, cleaned. Recirc tank needs pump out due to solids and trash ( tampons and wipes). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
04/18/2023 | Alternative | RoutineScheduled | 061-STS-25724 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 |  | Follow-Up | 175-04-0584 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Advantex sheets. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
08/09/2023 | Alternative |  | 101-03-0410 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Thomas & Linda | Lively | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/06/2023 |  | Routine/Scheduled | 093-STS-14136 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream, cleaned the filter in the aerator, and cleaned the UV light bulb. Changed the mesh screen in the spinfilter. Meet with the pumping company to pump and clean the pump tank and pumped the trash out of the Clearstream tank. There is visible wetness on the drainfield - most likely from rain - once it dries need to keep an eye on it. The timer is set to 4.5 minutes every 1 hour. Need to go back and cut the UV back on, perform a draw down test, set pressures, and flush out the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/06/2023 | Jan 1 1900 11:00AM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | 179-18-0429-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the distribution box lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
06/06/2023 | Alternative | RoutineScheduled | 127-STS-33041 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic /Atu tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
01/27/2023 | Alternative | RoutineScheduled | SD-07-421 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Effluent up into the risers. Gravity system, drainfield is saturated and soggy. Replaced "bugbag" for maintenance. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/01/2023 | 06:07 AM
07/20/2023 | Alternative | Routine/Scheduled | 093-07-0233 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | Dec 30 1899 10:00AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0199-SR | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Whitewater ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | The air pump is not working and should be replaced. We also recommend replacing the cracked shut-off valve in the Pump Tank. We also recommend mowing the drip dispersal area and maintaining it in a mowed condition. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/01/2023 | 06:26 AM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89257 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots in splitter box 2 lines closer to woods, removed some and added root-x. Media partially clogged with grease and solids, treatment is crystal clear but we recommend chemical clean. Will send proposal. HL-4, LL-11, OVERRIDE-0. "R" CNTS BACK TO ZERO. Blower 2.99 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
07/07/2023 | Alternative | Routine/Scheduled | 093-18-0098 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Biofilter - concrete - peatmoss in fair condition - raked / turned. Pump Basin - float sensors, pump and controls operating. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 8:45AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/20/2023 |  | RoutineScheduled | 02-125-270 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 2 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/20/2023 | 12:00 AM
06/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/26/2023 | 09:53 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS removed roots and resealed distribution box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | EcoPod | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Zone 1+2 solenoids are not functioning correctly. Strongly recommend thinning out vegetation around panels and tank access. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-87782 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Presale inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 04:50 AM
09/27/2023 | Alternative | RoutineScheduled | 107-98-0273 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 2400.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/15/2023 | 04:40 PM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/07/2023 | Alternative | RoutineScheduled | SD-06-78 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 65.600000 | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 05:55 PM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0351 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
01/18/2023 |  | Routine/Scheduled | LEGACY | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - possible fracture - lots of "sand" present - float sensors, pump and controls operating. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | Jan 1 1900 8:15AM
03/28/2023 |  | Reportable Incident | 2009-143-0063 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Hoot |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [17 empty] | Alarm event - hiblow compressor failure - compressor replaced with new and system restored to proper operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/29/2023 | 10:15 AM
01/09/2023 | Alternative | Reportable Incident | SD-06-05 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed N137 effluent pump, 2" brass check valve control floats & replaced concrete riser lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
04/11/2023 | Alternative | RoutineScheduled | 115-14-0298 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Aqua klear |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","BlowerCompressorAerator Operation"] | ["Effluent Screens","BlowerCompressorAerator Operation"] | NA | Musty | [15 empty] | Inspected | Sludge level- under 1" Scum & 10" Sludge in Septic tank. Pump Tank 4-6" sludge- Aquaklear Treatment unit uptop hill 14" Sludge. Cleaned air filter, Blower appears it is working but may need replacmeent soon it looks to be the original. Alarm silcence button on blower is rusted and needs replacement soon . Air pump appears to operate as is. The home the effluent pump and alarm are operational - control panel data- 9167 vs 7,763 Doses = 1404 doses this year an increase from 665 the previous year. Pump Run time 158HR:35min vs 132hr:52min = about 25.6 hours an increase from 11 hours the pervious year. vinyl Air hose for blower alarm box is brittle from sun and needs replacement. Cleaned septic tank effluent filter whcih was backed up about 6inches. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 09:30 AM
06/22/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0225-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 4.01 amps. Peak counts-6, Etm-1h23m, HL -7. Recommend installing air filter for blower inside housing when blower gets replaced. Gallons per minute are about a gallon higher than design but there is no wet spots on drip field or water coming back to return. Customer said septic tank was pumped out not to long ago, pump tank will need pump out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
06/19/2023 | Alternative | Routine/Scheduled | 800-10-0051 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 2:45PM
12/05/2023 | Alternative |  | 18-113-003 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/05/2023 |  | 9.220000 |  |  | 2.300000 |  |  | Will be sent separately |  | BOD: 9.22 TSS: 2.30 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
05/26/2023 | Alternative | RoutineScheduled | 04-100-0779 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1250 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | EVERYTHING WORKING GREAT. PEAT IS FULL AND LOOKS NEW. TANK DOES NOT NEED PUMPED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 10:55 AM
05/12/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Enviromental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1500 & 800 | Advantex |  | Pump | Pressure | Drip | Not Applicable | 100.000000 | ["Dispersal System Operation","Effluent Screens"] | ["Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | 5:00pm
12/19/2023 | Alternative | RoutineScheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Distribution Pump Operation","SludgeScum Accumulation","Dispersal System Operation","Level Sensor Operation","Effluent Screens"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 9:00AM
09/13/2023 | Alternative | RoutineScheduled | 12-125-066 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/13/2023 | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
05/16/2023 | Alternative | RoutineScheduled | 05-160-0172 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | Premier Tech Eco Flow E500 |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Auxiliary Filter"] | ["Attached Growth Medium","Auxiliary Filter"] | NA | [17 empty] | System is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/17/2023 | 12:00 AM
05/12/2023 |  | Follow-Up | 175-15-0249 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [17 empty] | Service call to replace faulty Microfast Blower VFC200P-5T on 5/12/2023. Chemical cleaning and pump out done on 5/17/2023/ Reset ph balance. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | 182-05-0268 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 09/11/2023 |  | 19.000000 | [5 empty] | Will be sent separately | Inspected | recommend clean out blower box | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
10/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 12:05PM
07/27/2023 | Alternative | Routine/Scheduled | 115-STS-96591 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Purasys |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Sequential Batch Reactor - sludge return operating. Aeration - submersible aerator serviced. Discharge PUmp - float sensors, pump and controls operating. DBox - concrete - intact - 8 laterals all accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 07:30 AM
05/24/2023 | Alternative | Routine/Scheduled | 07-160-0123 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 02:45 PM
04/10/2023 |  |  | 2005-143-0164 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3300 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","SludgeScum Accumulation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | None | Clear | 7.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 11:30 AM
10/27/2023 | Alternative | RoutineScheduled | VAG408071 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | Constructed Wetlands |  | Gravity | Gravity | Discharge | Chlorination |  | [] | ["Disinfection"] | NA | None | [16 empty] | Not discharging at time of inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/12/2023 | 09:10 AM
09/27/2023 | Alternative |  | 033-06-0539-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
05/02/2023 | Alternative | Routine/Scheduled | 093-06-0162 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Dec 30 1899 11:40AM
03/14/2023 |  | RoutineScheduled | 175-04-0536 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
03/13/2023 | Alternative | Routine/Scheduled | 128-08-126 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | [8 empty] | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - plastic - bottom bulging noted - float sensors, pump and controls operating. BioFilter - peatmoss spent - ponding present - raked / turned best possible - recommend replacement of biofilter media. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 08:00 AM
07/11/2023 | Alternative | Routine/Scheduled | 18-120-0310AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Trenches | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. U.V. Disinfection - Bulb and housing serviced. Pump Tank - float sensors, pump and control operating. LPP - no indications of surfacing - some erosion present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 11:00AM
06/03/2023 | Alternative | RoutineScheduled | 175-04-0388 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | EcoVirginia LLC | 1942001235 | William | Poindexter | 3.000000 |  | septic | ATU | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | Musty | Clear | [15 empty] | WM: 1940310gal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | 12:00 AM
08/07/2023 | Alternative | Reportable Incident | 2085-03-153 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | Service call only: Alarm due to faulty Redundant off float. Replaced the float and now functioning properly. Counts: Pump-013944 ETM-0022415 On-1m Off-2h | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/13/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Puraflo | Pump | Gravity | Trenches |  |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 0 scum, 8" of sludge in septic tank, Pump tank has very little loose. Pump, alarms, and floats operational, peat is in great shape,good flow, d-box is good. 17670 everts am 1847 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 01:00 PM
03/08/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
02/24/2023 | Alternative |  | 128-15-0067 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Advantex |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 12:00 AM
01/16/2023 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Recommend pumpout of processing tank 1500 gallons + Refill. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | Jan 1 1900 7:30AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0227-SWT | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 2.94 amps. Peak 10. Treatment crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
04/26/2023 |  | RoutineScheduled | 18-192-139 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/26/2023 | 12:00 AM
04/03/2023 | Alternative | RoutineScheduled | SD-05-036 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Septic Tank, Advantex Tank and Pump Tanks due to scum & sludge accumulation in the tanks. This will require refilling the Siphon Tank with water when pumping is completed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
02/10/2023 | Alternative | RoutineScheduled | 91-197-5001 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/10/2023 | 12:00 AM
10/26/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 1:10PM
08/14/2023 | Alternative | Routine/Scheduled |  | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | 08/14/2023 - pumped septic tank empty for peatmoss media changeout. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/17/2023 | 12:15 PM
02/24/2023 |  | Routine/Scheduled | {FIPSCode}-STS-5275 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/24/2023 | Jan 1 1900 8:30AM
08/30/2023 | Alternative | Reportable Incident | 104-07-0333 | Amherst | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Other conventional maintenance performed | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Musty | [15 empty] | Inspected | System began to alarm daily and we visited for the alarm call. We replaced the bottom float on the discharge side and got the water level to correct it self after running in test mode. Could not get the recirculation pump to run even after corect level on discharge side and was not the stock pump, it has had extreme long run times due to infiltration as times. after trying to make the pump work decided to replace it with brand new pump. Was able to get a pump and replace it on the same day. System began to pump water normally and has not called since our visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 09:30 PM
06/15/2023 |  |  | 033-09-0117-ST | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
01/31/2023 |  |  | 16-142-0198 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EZ Treat | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
05/25/2023 | Alternative | RoutineScheduled | 177-STS-89799 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 05/25/2023 | [10 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-02-466 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted previously, the peat in the Pureflo modules have deteriorated and are no longer providing treatment. We would recommend replacing the peat or installing a different treatment unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
02/15/2023 |  | RoutineScheduled | SWP-02-797 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
11/16/2023 | Alternative | Routine/Scheduled | 147-16-0071 | Williamsburg | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The Clearstream tank and the septic tank need to be pumped out. There is visible wetness on the drainfield - multiple spots - needs to be addressed. The timer is set to 4 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/16/2023 | Dec 30 1899 11:15AM
03/27/2023 | Alternative | RoutineScheduled | 04-160-0449 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | [] | NA | Septic | Black | [14 empty] | Inspected | - recommend pumping/cleaning septic tank due to high sludge (there was a solid 24in of sludge in tank) - tank was serviced last year, need for pumping is caused by lack of good bacteria in system / overuse - servicing tank with such high sludge levels is to prevent sludge for entering outlet line to drainfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/13/2023 | 12:00 AM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
08/09/2023 | Alternative | RoutineScheduled | SD-07-186 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1250 | septic | Puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 07:30 AM
01/03/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | Septic Tank-12"sludge 3"scum/ Microfast-13"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ Need the Septic-Microfast Tank needs pump out/ Blower air filter cleaned and blower working properly/ UV-Light bulb is faulty and requires replacement/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-2111 ETM-298h 39m/ High-5/ Peak-7 ETM-59h 45m On-9m Off-2h 24m Returned on 3/8/2023 and replaced the UV-Light and tested- functioning properly at this time. Will return in 2 weeks to pull sample. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/14/2023 | Alternative | RoutineScheduled | 179-16-0421-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-2 0-2 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear | [14 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 10:00 AM
02/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | Dec 30 1899 10:55AM
10/03/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.700000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 12:35 PM
03/22/2023 |  | RoutineScheduled | 16-183-183 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/22/2023 | 12:00 AM
10/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 10/17/2023 | Sample Chamber | 4.000000 | [5 empty] | Attached to this report |  | Septic Tank-3"sludge 2"scum/ Microfast-0"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-49 ETM-4h 30m/ Pump2-48 ETM-4h 24m/ Peak-14/ High level-7/ No breakout or spongy areas on the LPD Pad Site and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/24/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Septic zone 1" Scum layer on top & 12" Sludge layer on bottom, Treatment zone trace scum and trace sludge. Cleaned blower air filter, appears to have Good aeration. Drainfield appears dry. Owner keeps field cut. Alarm is operatioanl | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
08/15/2023 | Alternative | RoutineScheduled | 12-113-145 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Septic Tank Baffles","Dispersal System Operation","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/15/2023 | 12:00 AM
03/03/2023 | Alternative | Routine/Scheduled | 093-16-0191 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Mound | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | System reported to be alarming - found system in normal level - Effluent screen serviced. Aeration tank - mixing present. Pump tank - pressure sensor functioning | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | Dec 30 1899 7:00AM
08/21/2023 | Alternative | Routine/Scheduled | 07-142-0182 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches | Not Applicable | 250.000000 | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | N/A | [17 empty] | Blower filter was cleaned. Discharge high level was tested and worked correctly. Little trees growing around distribution box should be removed to prevent root infiltration. Discharge pump counters: Event= 57553 Time= 788.28h | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | Dec 30 1899 9:08AM
04/19/2023 |  | Follow-Up | 179-STS-89429 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Met with homeowner to evalute fence post being on header lines. Home owner stated he paid a company to locate septic components before fence was installed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/05/2023 | 07:56 AM
12/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/11/2023 | Alternative | Routine/Scheduled | 10-163-0022 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Clearstream ATU |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | [17 empty] | Cleaned Tee weir. Replaced compressor filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | Dec 30 1899 12:21PM
03/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/29/2023 |  | Routine/Scheduled | {FIPSCode}-STS-4034 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Jan 1 1900 10:25AM
08/28/2023 | Alternative | Routine/Scheduled |  | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing tank - recommend pumpout and refill - RSV, recirc pump and effluent screen servcied. Treatment Module - media drapes & spray grid serviced. Pump tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | 08:15 AM
08/15/2023 | Alternative | RoutineScheduled | 027-STS-17667 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/15/2023 | 12:00 AM
05/03/2023 |  | Routine/Scheduled | 08-120-0540A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/03/2023 | Jan 1 1900 4:02PM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | 061-17-122 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [5 empty] | 09/27/2023 | Pump Chamber | 6.000000 | [5 empty] | Will be sent separately | Inspected | Annual inspection. Treated effluent in pump tank looks very good. FPZ 1/3 hp blower is working hard at 3.87 amps (max is 3.4 amps). High level count at 15. Panel has run quite a few peak cycles since last year's inspection (72 cycles total, 2903:42 etm). Suspect peak float may be sticking on at times. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
11/07/2023 | Alternative | Routine/Scheduled | 136-02-380 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 12" of sludge and 1" of solids Pulled and cleaned filter Crock riser has signs of leaking -Discharge/Pump Tank: Normal level Less than 1" of suspended solids All floats and pump functioning properly However they are aged Plumbing is aged Crock riser has root intrusion -Aeration: Normal level Pulled and cleaned weir Less than 1" of suspended solids Non serviceable airline Aged alarm float not functioning -Air Pump/Blower: Pulled and cleaned air filter Air pump is functioning properly However it is Aged Air pump. Pulling 1.54amps -Control Panel: Panel has 120v All audible and visual alarms are functioning properly Pump 12.15amps Panel is Aged and starting to deteriorate -Distribution Box: Plastic distribution box 6" below grade in good condition with 8 lines balanced and taking water -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 11:05 AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [17 empty] | Septic Tank-10"sludge 1"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms function properly/ Counts: Pump1-023445 ETM-0209205/ Pump2-023741 ETM-0209768/ 50 gal. per cycle/ Pump- 52 gpm/ On-58s Off-2h / Coconut husk peat in good/ No breakout or spongy areas on the drainfield.condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/11/2023 | Alternative | RoutineScheduled | SD-10-307 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | Pura Flo | Pump | Gravity |  |  | 52.000000 | ["SludgeScum Accumulation","Effluent Screens"] | ["Effluent Screens"] | YES | Sulphitic | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 03:55 PM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0309 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | valve box lid replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
03/27/2023 |  | RoutineScheduled | 175-05-0136 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 6"scum/ Microfast-12"sludge 0"scum/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats, hydraulic unit and alarms all functioning properly/ Counts: Pump-5546 ETM-671h 34m/ High-19/ Peak-3 On-7m 23s Off-2h 19m/ Watermeter-0,307,868.6/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/31/2023 | Alternative | Routine/Scheduled | 196-11-082 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 06:26 PM
05/15/2023 |  | Routine/Scheduled | 234-14-381 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | Jan 1 1900 9:00AM
11/22/2023 | Alternative | RoutineScheduled | 075-STS-32703 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 2500 | 1000 | 750 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Distribution Pump Operation","SludgeScum Accumulation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 12:00 AM
01/30/2023 | Alternative | RoutineScheduled | 115-17-0257 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | septic zone Scum level-Trace- 8-14" sludge in Septic zone of tank - Recirculation zone 6" sludge - Discharge Tank 8" sludge- Cleaned Biofilter-moderately dirty, Brushed and flushed manifold, cleaned RSV, sprayed off media tested float switches, flushed system. Cleaned Spin Filter, Ran in test mode, Alarm functional. 10.7 amps pulled on Recirc pump, 11.3-11.5 amps on Discharge pump, Good spray pattern in treatment tank- Discahrge Gallon Meter reading - 171,520 gallons | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 09:30 AM
01/09/2023 | Alternative | Routine/Scheduled | 157-05-207 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - Peatmoss in fair condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 11:15 AM
01/19/2023 |  |  | 2017-143-0043 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | We delayed sending this report waiting to see if the homeowner would get the blower replaced. As of today he has not replaced it. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/14/2023 | 12:00 AM
09/06/2023 | Alternative | RoutineScheduled | 08-192-262 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 7 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/06/2023 | 12:00 AM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0666 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Force main needs repairing sewage on ground surface. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/15/2023 | 01:44 PM
09/12/2023 | Alternative | RoutineScheduled | 107-09-0199 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  | Gravity |  | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
02/01/2023 |  | RoutineScheduled | 175-17-0121 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/13/2023 | 08:47 AM
02/28/2023 |  | Routine/Scheduled | 228-10-0460 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | Jan 1 1900 11:25AM
11/11/2023 | Alternative | Follow-Up | 115-01-0441 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Septic Tank | Puraflow | Pump | Gravity | Trenches | Not Applicable |  | ["Other"] | ["Other"] | [18 empty] | Puraflow pod media was removed (total of 3 pods) and replaced with new media. New updated spray rails installed. New D box lid installed. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/20/2023 | 12:00 AM
03/30/2023 |  | Routine/Scheduled | 23-16-359 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | Jan 1 1900 12:55PM
12/27/2023 | Alternative | RoutineScheduled | 121-STS-13687 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | - LPD system is not functioning, recommend repairing LPD system as it does not appear to be discharging into drainfield adequately - pumped/cleaned septic tank and pump chamber - need signed maintenance agreements to proceed with repairs | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/28/2023 | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 12/13/2023 |  | 4.000000 | [5 empty] | Will be sent separately | Inspected | Programmed board Repaired pump, beacon and gasket Lab sample normal | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Mirco fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 10/30/2023 | Sample Chamber | 22.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/10/2023 | Alternative | RoutineScheduled | 07-197-A15 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/10/2023 | 12:00 AM
01/19/2023 |  | Reportable Incident | 18-174-0106 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the red light being on for about a week - pump tank was empty and pump was running - replaced relay and wired pump through float. Serviced system. Checked the floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the UV light bulb and replaced the UV light cord. The septic tank needs to be pumped out and when doing so pump the Clearstream tank. The timer is set to 3 minutes every 2 hours. Could not take samples due to there not being enough water. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/19/2023 | Jan 1 1900 3:15PM
03/07/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Solution added to media filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/20/2023 | Alternative | Routine/Scheduled | 800-STS-15291 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | Dec 30 1899 1:15PM
11/14/2023 | Alternative | RoutineScheduled | 023-STS-42917 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Western Virginia Water Authority | 1942001145 | Michael | Doss | [9 empty] | [] | [] | NA | None | Clear | [5 empty] | 11/14/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 1:45PM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-355 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Distribution box under drive way. The headers possibly under shed. Pod has multiple cracks. Not detrimental. large crack on end of pod on bottom half further from road, ground water flowing in on opposite side of pod. estimate is been given. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
10/13/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/13/2023 | Dec 30 1899 11:47AM
10/02/2023 | Alternative | RoutineScheduled | 06-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 4 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/02/2023 | 12:00 AM
07/24/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0176 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | Clear | [5 empty] | 07/24/2023 | Sample Chamber | 31.000000 | [5 empty] | Will be sent separately | Inspected | On site for annual inspection and 5-year sampling. Pump tank was in high level. Repaired burnt hot wire connection in splice box at pump tank. Replaced high level alarm float and alarm horn for outside alarm. Capped off 2" remote vent for atu that owner had installed. Line was undersized, too long, and was running uphill at the end. Media appears to be partially clogged. Owner already has a pump-out scheduled. Collected BOD sample. Results came back at 31 mg/L, probably due to tank needing pumping. Will review effluent level in atu next year and check clarity to see if chemical cleaning is recommended. Properly repaired broken ARV that had been previously repaired with a 1" Fernco by the owner (it had started to leak). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
11/20/2023 | Alternative | Routine/Scheduled | 02-163-0038 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level 1" of Solids with 12" of sludge Pulled and cleaned rsv -Recirculation Tank: At normal level Pulled and cleaned pump, floats and filter Filter was very dirty Tank has 24" of sludge -Discharge/Pump Tank: At normal level Pulled and cleaned pump and spin filter Riser showing signs of leaking -Media Sheets: Lid is bowing and has no locking strut Sheets are bridged and ponding water Brushed and flushed laterals and sprayed off sheets -Control Panel: Panel is aged but working Recirc pulling 12amps Discharge pulling 11.7amps -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | Dec 30 1899 3:09PM
05/08/2023 | Alternative | Follow-Up Component Maintenance | 177-STS-92825 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Avergae daily flow; 269 gallons. The system is operating at average daily flow and still failing. Still saturated. A new disposal site is required. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/26/2023 | 07:01 AM
02/09/2023 | Alternative | Reportable Incident | 136-09-0080 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - muted it. Serviced system. Cleaned the filter in the Clearstream . Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a new Clearstream aerator motor (new serial # 21030575). The septic tank needs additional risers on it to be properly inspected. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/09/2023 | 11:00 AM
04/08/2023 |  |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
01/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
07/31/2023 | Alternative | RoutineScheduled | 031-STS-29652 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 3.000000 | 5500 | Septic Tank | EZ-Treat | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | NA | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The EZ-Treat pods were both opened and sprayed off. The spray nozzles were taken out and cleaned. At the time of visit it was discovered that an apparent lightening strike had cause the three floats in the equalization tank to go bad. The three floats were replaced. The other controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/08/2023 | 04:15 PM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 04/20/2023 |  | 7.000000 |  | 13.000000 |  |  |  | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
06/30/2023 | Alternative | Initial Visit Component Maintenance | 177-17-0250-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | UV bulb will be replaced by installer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
05/18/2023 |  | RoutineScheduled | 177-10-0041-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Effluent had been close to the lid in septic tank, evidence of overflowing. Cleaned very dirty effluent filter. Also cleaned very dirty biotube filter, RSV, and Advantex sheets and laterals (5 years since last service). Replaced failed R.O. float switch in recirc tank. Reconnected wire for alarm horn in the drip control panel and replaced the alarm bulb (supplied by owner). Inspected tanks as best possible (limited to what was showing above effluent level). Inlet tee missing at septic tank sewer line. Will need to dig up buried wedge lid to install a new tee. Recommend installing a riser to grade at that time. Evidence of infiltration in pump tank at inlet end midseam (roots), and at buried wedge inlet end lid. Drip rate notably higher than on previous visits, but no surfacing effluent seen. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
11/17/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-803 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | As noted previously, there are roots growing in at the base of the risers on the Advantex tanks and pump tank. If you get alarms during periods of heavy rain, we recommend excavating by machine and resealing the risers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-88849 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Effluent Screens" ,"Distribution Pump Operation" ,"Recirculation Pump"] | YES | Sulphitic | Dark Brown | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
01/15/2023 |  | RoutineScheduled |  | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | sand filter | Gravity | Pressure | Discharge | Chlorination |  | [] | [] |  | None | Clear | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/17/2023 | 08:25 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed at this time. There are three emitter spots near the far side of the drainfield that appear highly nitrified but it might just be less cover as the line ends. Recommend homeowner monitor and notify if there are any changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | Dec 30 1899 1:15PM
06/06/2023 | Alternative | Initial Visit | VAG408003 | Rockbridge | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | The inspection was for a real estate sale. The 1500 gallon MicroFast tank was pumped out and cleaned. The tank was inspected and was working as designed. The blower however, had a tee in the line with a ball valve that was open all the way. This was allowing all the air to go to the post treatment check port instead of most of the air going to the MicroFast unit. The effluent was not getting any treatment from the Microfast media. This problem was corrected at the time of inspection. The evaporation bed was operating as designed but, It is recommended to add more mulch to the bed. The controls were operating as designed. There was enough chlorine and de-chlorine tablets in the feeders so I didn't have to add any tablets. There was no discharge at the time of inspection so there was no sample draws taken. With the air blower problem, it wasn't any field test taken. The lids were secured. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 06/08/2023 | 11:00 PM
07/27/2023 | Alternative | Pump-Out Only | 166-07-226 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Pressure |  |  | 450.000000 | Attached Growth Medium | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Pumpout for peatmoss biofilter changeout scheduled for week of 07/31 - 08/04. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/31/2023 | 06:15 AM
08/11/2023 | Alternative | RoutineScheduled | 86-192-068 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/11/2023 | 12:00 AM
12/06/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
04/17/2023 |  | Reportable Incident |  | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 4.000000 | 9000 | None | None | Pump | Pressure | Trenches | Not Applicable | 2200.000000 | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out | Contacted by restaurant management regarding leak at one of the absorption fields. - System reportedly pumped on the 14th by "others", and removed 4000 gallons. Pumped this date by Millers and removed an additional 4000 gallons. Pump #1 not operating - cannot dose / pressurize LPP to find leak. Pump #2 operates - but appears to dose the second LPP field. Evidence that there is surfacing effluent which is located in a different location than repairs made last year this time. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/18/2023 | Jan 1 1900 7:00AM
09/08/2023 | Alternative | Routine/Scheduled | 11-120-0234AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | - Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. - Aeration: Water level normal. Checked and confirmed aeration is occurring. Flushed and cleaned effluent screen. Not due for pump out - Air Pump/Blower: Checked and found diaphragms have failed. Homeowner gave approval to upgrade aerator. Upgraded aerator while on site. Checked and confirmed aerator is functioning properly. - Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact - Condition: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 10:09AM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-494 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
12/19/2023 | Alternative | Reportable Incident | 08-142-0306 | Goochland | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Other"] | ["Other"] | [18 empty] | Replaced broken 2" air line from blower to the tank | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12:00 AM
08/30/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 1250 | Orenco Advantex |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - recommend pumpout - no refill required Processing tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Drip Field - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | Dec 30 1899 10:00AM
05/15/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | 11:24 AM
12/19/2023 | Alternative | Routine/Scheduled | 041-STS-261625 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 10:30AM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408382 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Chlorination |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
11/14/2023 | Alternative | Routine/Scheduled | 228-07-0782 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 12:15PM
07/21/2023 | Alternative | Routine/Scheduled | 800-07-0086 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | Dec 30 1899 8:00AM
01/16/2023 |  | RoutineScheduled | 00-120-0623A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2000 | 1000 | 1000 | Pump | Pressure | Mound | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Cloudy | 7.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 12:00AM
08/04/2023 | Alternative | RoutineScheduled | 181-01-0230 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only |  | Pump | Pressure | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | The system did not need to be pumped. The effluent and spin filters were both pulled and cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 12:40 PM
01/24/2023 |  | RoutineScheduled | 175-15-0116 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-4"sludge 4"scum/ Microfast-2"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-12454 ETM-1404h/ High-148/ Water Meter-0,184,467/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/30/2023 | Alternative | RoutineScheduled | 067-STS-39488 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 4000 | EZ Treat Filter |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | 4th Quarter 2023 inspection. First Grease Trap - First section - 2" crust, 14" on bottom. Second section - skim crust, 12" on bottom. Septic Tank - First section - 6" crust, 18" on bottom Second Section - 2" crust, 4" on bottom. FEQ tank - first section - no crust, 12" on bottom, second section - no crust, 2" on bottom. Recirculation Tank - First section - 0" crust, 12" on bottom Second section - 0" crust, 12" on bottom. Discharge Pump Tank - First section - 0" crust, 2" on bottom Second section - 0" crust, 0" on bottom. Cleaned Filters on grease trap and septic tank. All treatment unit spray nozzles spraying unclogged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2024 | 07:03 PM
02/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | EcoPod | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | 7.400000 | 23.600000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 03/14/2023 | Dec 30 1899 10:46AM
05/11/2023 |  | RoutineScheduled | 179-19-0157-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend cutting back the growth along the bottom of the drip dispersal area and maintaining it in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-0188-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
03/30/2023 |  |  | 2017-143-0051 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 12:00 AM
01/26/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Installed effluent filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 02:21 PM
12/01/2023 | Alternative | RoutineScheduled | C-122-17-0024 | Craig | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | BioMicrobics Microfast 0.5 |  | Gravity | Gravity | Trenches | UV | 250.000000 | ["None"] | ["None"] | NA | [17 empty] | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/03/2023 | 12:00 AM
04/25/2023 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Fuji |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | Routine Service. Primary Septic Tank - normal level Processing Tank - trash tank - normal level Processing Tank - Aeration Tank - mixing present - compressor serviced. Processing Tank - Clarifier - sludge return operating. Pump Tank - float sensors, pump and controls operating. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 1:00PM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Hydro-Action ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/13/2023 | Alternative | RoutineScheduled | 98-197-A5 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 0.000000 | [6 empty] | Chlorination |  |  |  |  | None | Clear | 5.500000 | 3.500000 |  | 0.000000 | No tablets | [10 empty] | No tablets low DO | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/15/2023 | Alternative | Routine/Scheduled | 159-12-104 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 4.000000 | 4000 | Clearstream | Clearstream | Pump | Pressure | Trenches | Not Applicable | 2000.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Grease Trap - Chinese Restaurant - requires effluent screen replacement. Primary septic tank - Chinese - serviced effluent screen. Pump Tank - Chinese Rest. float sensors, pump and controls operating. Grease Trap - The Table Rest. - effluent screen serviced. Primary septic tank - The Table Rest. - effluent screen serviced. Pump tank - The Table Rest. - float sensors, pump and controls operating. Aeration #1 - normal level - mixing present - compressor serviced. Aeration #2 - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 07:30 AM
07/08/2023 | Alternative | Reportable Incident | 136-13-0059 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | System reported backing up into residence. FOG clogging building sewer and inlet to septic tank Pumped empty and jetted sewer line clearing clog. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | 09:00 AM
08/16/2023 | Alternative | Reportable Incident |  | Hanover | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Discharge | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | System flooded and in alarm condition on arrival. Stuck toilet flapper flooded system - conducted routine service Processing Tank - RSV, recirc pump & effluent screen serviced - operated in test mode to pull system out of high level condition. U.V. - bulb and housing serviced - Pump Tank - float sensors,pump and controls operating - operated in test mode to pull system out of high level condition. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 08/21/2023 | Dec 30 1899 7:45AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/15/2023 | Alternative | RoutineScheduled | 159-10-0013 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
05/22/2023 |  | RoutineScheduled |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable | 350.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | Jan 1 1900 3:45PM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities Salcor UV unit needs new head board & bulb. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance | SD-07-039 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-318 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Clear | [13 empty] | Will be sent separately | Inspected | We continue to recommend adding topsoil where the infiltrators in the drain field are exposed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
03/14/2023 |  | Routine/Scheduled | 550-STS-6535 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Jan 1 1900 1:40PM
03/15/2023 | Alternative | RoutineScheduled | 159-11-159 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | YES | [16 empty] | Exempt | Audio on alarm repair | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
10/05/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches |  | 750.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 10:47 AM
06/17/2023 | Alternative | RoutineScheduled | 2129-10-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | UV | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 6.800000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/02/2023 | 12:00 AM
02/20/2023 |  | Routine/Scheduled | MS39 Lot 17A | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | Jan 1 1900 12:20PM
04/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | 099-18-0122 C-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced uv bulb. Ax20 Unit vent broken by mower. 3 Valve cover at drip broken by mower. Customer ask for price for replacing, proposal will be sent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-58 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
06/09/2023 | Alternative | Follow-Up Component Maintenance | SWT-03-344 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There has been 3 site visits made to follow up on the contactor sticking when we preformed a routine inspection on this septic system on March 17th 2023. The contactor has not had the same issue in 3 and a half months. The contactor could have gotten stuck due to a power on or around the time of the routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
07/20/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Fast | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | 3' liquid depth with 2" of scum and 10' of sludge. rest of tank no sludge, pump tank no sludge. Blower, alarms, floats, and pump working. Field is dry. 513 pump cycles, 45hrs, 52 min run time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 10:30 AM
04/12/2023 |  |  |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0067 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 7.400000 | 25.700000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 08/15/2023 | 01:44 PM
09/06/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | Western Virginia Water Authority | 1942001140 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 09/06/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 03:15 PM
06/01/2023 | Alternative | RoutineScheduled | 09-160-0019 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 |  | Aquasafe |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled | 12-142-0079 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/03/2023 |  | RoutineScheduled | 107-02-0829 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","SludgeScum Accumulation","Attached Growth Medium","Level Sensor Operation"] | ["Attached Growth Medium","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | 10:25 AM
05/15/2023 |  |  | 03-183-252 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/15/2023 |  | 4.340000 |  |  | 2.200000 |  |  | Will be sent separately |  | BOD: 4.34 TSS: 2.20 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/15/2023 | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled | 107-18-0027 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 5000 | Septic Tank Only | EZ Treat | Pump | Pressure | Drip | Not Applicable |  | ["Recirculation Pump","Effluent Screens"] | ["Recirculation Pump","Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The EZ Treat pods were sprayed down and cleaned. There was two recirculating pumps bad at the time of visit so they were pulled and replaced the same day. The controls were operating as designed. There was return effluent returning to the pump tank so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/11/2023 | 09:25 PM
11/14/2023 | Alternative | RoutineScheduled | 109-08-0297 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Quanics |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | [] | NA | [16 empty] | Inspected | Cleaned the effluent filter water level was slightly lower then normal. Media looks good, good spray pattern and the float switches all tested ok, Pump counter 18348 Cycles ; Run time - meter 956:10. System appears operational | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/28/2023 | 09:30 AM
10/09/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.220000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 03:45 PM
04/13/2023 |  | RoutineScheduled | 043-05-0066 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 | 1125 | Septic |  | Pump | Pressure | Trenches |  |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [18 empty] | No scum or sludge . Was just pumped out. pump and alarm working. Field dry and looks good. Filter clean. 135.02 Hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 09:30 AM
12/04/2023 | Alternative | RoutineScheduled | 107-01-0564 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Level Sensor Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Level Sensor Operation"] | [18 empty] | wet spot in drip field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | SD-09-313 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Once again, drip pump was encased in a crusty material resembling calcium deposits. Amazing that it could take in enough effluent for a proper dose. Assuming that was the case as owner did not call in any high level alarms in the past year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
04/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
07/26/2023 | Alternative | Routine/Scheduled | 128-04-172 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls operating. Drip Field - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 09:15 AM
01/26/2023 |  | Routine/Scheduled | 07-142-0347 | Hanover | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Discharge | UV | 450.000000 | Disinfection | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. UV Disinfection - dual bulb system - one bulb failed requires replacing. Discharge point - clear of debris and free flowing. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/30/2023 | Jan 1 1900 7:15AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/01/2023 | Alternative | RoutineScheduled | 154-17-0375 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 182-16-0015 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/10/2023 |  | 3.000000 | [5 empty] | Will be sent separately | Inspected | Lan normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-25994 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"SludgeScum Accumulation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | System needs pumped out due to system being off since client moved in. Turned system on and checked all component's and they are operational. Due to it being off no treatment has occurred so pumping of complete system is required. Sample was taken at time of visit per county's requirement as part of the 180 day inspection. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
10/27/2023 | Alternative | Routine/Scheduled | 115-STS-92778 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Above normal Level due to clogged filter. Pulled and cleaned filter ans water Level returned to normal level Less than 1" of sludge and less than 1"of solids -Discharge/Pump Tank: Normal Level All floats and pump are functioning properly Pulled and cleaned pump and floats Less than 1"of suspended solids Uv assembly is not working -Aeration: Normal Level 1" of suspended solids Pulled and cleaned weir and diffuser. Diffuser is 80% clogged Alarm float is functioning properly -Air Pump/Blower: Air pump housing is clear of debris Cleaned air filter. Air pump pulled .54amps -Control Panel: 120v coming into panel Discharge pump pulling 3.41amps Timer is functioning properly. Panel in alarm due uv assembly not working. -LPD: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 08:19 AM
12/19/2023 | Alternative |  | 101-12-0337 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | George & Rose | Dalimonte | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Drip system appears to be functioning exactly as designed. Field shows perfect emitter spacing. If viewed from Spinks Ferry, it might appear that there is a nitrified streak coming from the pump chamber riser down, but during inspection, there were no signs of any malfunction, sewage on the ground, or any other explanation for the discoloration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/26/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 3:05PM
11/02/2023 | Alternative |  | 10-142-0141 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/11/2023 | Alternative |  | 159-14-0086 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1250 | Ecopod |  | Pump | Pressure | Pad | Not Applicable |  | ["Auxiliary Filter","Control Operation"] | ["Control Operation","Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | 12:00 AM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-91905 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | There is some green striping in the dispersal area, but there was not enough water to fully test the drip dispersal system. A follow-up visit is planned to add water if necessary and test the dispersal system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 |  |  | {FIPSCode}-STS-6213 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Cloverleaf Environmental Consulting, Inc | 1942001135 | Robert | Charnley |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/14/2023 | Alternative | RoutineScheduled | 177-10-0281-SR | Spotsylvania | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 08/14/2023 | [9 empty] | E-Coli reported 304mpn/100ml | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
11/03/2023 | Alternative | Routine/Scheduled | 087-STS-6641 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | 11:00 AM
03/27/2023 |  | RoutineScheduled | SP-05-680 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 1500 | 750 | 750 | Pump | Gravity | Pad | Not Applicable | 300.000000 | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | 01:30 PM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2024 | 11:49 AM
03/09/2023 |  | Routine/Scheduled | 08-163-0154 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level - no access riser present. Aeration Tank - mixing present - compressor serviced. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | Jan 1 1900 8:15AM
08/18/2023 | Alternative | RoutineScheduled | 02-197-122 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 AM
06/14/2023 | Alternative | Routine/Scheduled | S07-180-0090 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Jan 1 1900 11:15AM
04/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/23/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
11/22/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | 12:00 AM
01/09/2023 |  | Routine/Scheduled | 136-00-072 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - tank out of true - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 11:00 AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/22/2023 | Alternative | Reportable Incident | 093-11-0089 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced float and pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/23/2023 | Dec 30 1899 2:30PM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/30/2023 | Alternative | RoutineScheduled | 1182-94-0516 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium"] | ["BlowerCompressorAerator Operation","Attached Growth Medium"] | [18 empty] | Blower replaced and FAST blockage repaired | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/11/2023 | 12:00 AM
04/04/2023 |  | RoutineScheduled | 43-STS-32185 | Clarke | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lord Fairfax | McKim Septic & Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/08/2023 | 02:25 PM
07/28/2023 | Alternative | Reportable Incident | 234-15-49 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/28/2023 | Dec 30 1899 9:00AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/28/2023 | Alternative | RoutineScheduled | 10-173-009 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Norweco |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | Dec 30 1899 9:00AM
08/17/2023 | Alternative | RoutineScheduled | 179-16-0003-SWP | Stafford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [7 empty] | 08/17/2023 | Sample Chamber | 6.000000 | [5 empty] | Attached to this report |  | Septic Tank-8"sludge 6"scum/ Microfast .625-10"sludge 0"scum/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Found faulty On & Off Floats and were replaced on 8/21/2023/ Controls, pump, floats and alarms now functioning properly/ Counts: Pump-2814 ETM-16965/ High-16/ Watermeter-13,601.3/ No breakout or spongy areas on the Geoflow Drip Field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/21/2023 | Alternative | RoutineScheduled | 2010-143-0034 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/13/2023 | Alternative |  | 00-125-011 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 09/13/2023 |  | 5.360000 |  |  | 3.300000 |  |  | Will be sent separately |  | BOD: 5.36 TSS: 3.30 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/13/2023 | 12:00 AM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | 177-18-0164-SWP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Effluent Screens" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | The Advantex recirculation pump does not have enough pressure to provide proper treatment. We recommend replacing the pump. Additionally, there is effluent coming to the surface in the drip dispersal area. 9/19 - MWebb will reach out to provider for updates, then send NOAV if needed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/01/2023 | 07:38 AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/26/2023 | Alternative | Reportable Incident | 157-09-0111 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to some bubbling. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the float in the Clearstream. Pumped out the septic tank, pumped out the pump tank, and pumped down the Clearstream tank. The timer is set to 8 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/26/2023 | 04:00 PM
05/15/2023 |  | RoutineScheduled | 175-06-0564 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [17 empty] | Septic Tank-2"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-23803 ETM-40287 On-58s Off-3h/ Turned Puraflo Peat in all 5 modules and in good condition/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/09/2023 | Alternative | Reportable Incident | S-175-18-0003 | Southampton | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Someone called due to an alarm and light for a couple of days. Cleaned the filters in both Clearstreams and cleaned the filter in the septic tank. Changed the diffuser in one Clearstream and cleaned the diffuser in the other Clearstream. Installed aerator rebuild kits on both aerators. Changed both aerator filters and changed the mesh screen in the spinfilter. Replaced the UV light bulb, replaced the UV cord, and replaced the alarm light bulb. Could on locate on vacuum breaker. There is visible wetness on the drainfield. Also, there is holes on the drainfield and a piece of drip tubing was found - all needs to be repaired. The timer is set to 4.5 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/09/2023 | Dec 30 1899 10:30AM
09/22/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | Dec 30 1899 10:55AM
05/02/2023 | Alternative | RoutineScheduled | 18-100-0472 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [8 empty] | 05/02/2023 | Sample Tap | 4.000000 |  | 4.100000 | 20.000000 | 2.200000 | 14.500000 | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/07/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Panel was rewired and aerator was reaplaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/27/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Ashleys Septic Service | 1942001160 | Shane | Majewski | 1.000000 | [8 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | replace 2 Floats | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/10/2023 | Dec 30 1899 11:40AM
02/22/2023 |  | Follow-Up | 175-15-0036 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed Microfast blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
01/30/2023 |  | RoutineScheduled | 177-13-0263-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
04/07/2023 |  | RoutineScheduled | 175-03-0567 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | 12:00 AM
02/23/2023 |  | Routine/Scheduled | 234-17-19 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced Salcor Bulb, Ballast and Cord | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | Jan 1 1900 5:00PM
12/06/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
08/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Filter was clogged and cleaned | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
02/14/2023 |  | Follow-Up | 175-12-0084 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  |  |  | NA | [7 empty] | 02/14/2023 |  | 4.000000 |  | 1.800000 |  |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0070 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Distribution Pump Operation"] | ["Disinfection" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Broken gate valve in pump chamber causing system to not pressurize and allowing proper dosing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
04/21/2023 | Alternative | RoutineScheduled | 09-160-0128 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Inspected | -completed 2023 inspection - replaced blower onsite, everything appears to be functioning as designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/24/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Fuji | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/12/2023 | Alternative | Reportable Incident | 023-STS-43204 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Delta Environmental DF60 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Level Sensor Operation","Control Operation"] | ["Effluent Screens","Level Sensor Operation","Control Operation"] | NA | [16 empty] | Inspected | System has been reinstalled and relocated. Installer returned to repair a line which had settled going into the treatment tank. System pipes are now even and pump and alarm are opperational. Septic tank minimal scum and 10" sludge, treatment tank 12" light trace of sludge, pump tank 4-5" trace of sludge, Blower good, cleaned airfilter, floats checked good alarm test good, New Pump meter reads 2.13 hours and 63 cycles | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
01/13/2023 |  | Routine/Scheduled | 09-160-0230 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/13/2023 | 03:00 PM
01/18/2023 |  | RoutineScheduled | VAG401341 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.700000 |  | 25.000000 |  |  | 01/18/2023 |  | 17.000000 |  |  | 186.700000 |  |  |  |  | Client has been advised to have the system pumped, and we will resample. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/14/2023 | 08:00 AM
05/09/2023 |  | Routine/Scheduled | 234-15-217 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | Jan 1 1900 8:00AM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
06/15/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Advantex | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | YES | [7 empty] | 06/15/2023 | Pump Chamber | 3.220000 | [5 empty] | Attached to this report |  | 0 scum, 2" of sludge. Field is dry with no leaks, filters cleaned. pump, floats and alarm working. dist, pump 389 events and 139h 53 min run time, recirc. pump 19752 events, 319hrs 32 min run time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | 11:25 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/04/2023 | Alternative | RoutineScheduled | 085-STS-31566 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/10/2023 |  | Follow-Up | 179-16-0179-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to pump out both tanks. Rt unit was in high level and alarm horn in the panel was disconnected. Rt unit panel was only running 2 cycles a day which was 74 gallons on average max limit is 45 cycles. Reprogramed the circuit board. Made a follow up visit a week later no more alarms. The septic tank had alot of grease, flushable wipes, paint and signs of fabric softner usage. this needs to stop immediately as all things things abuse a septic system. I spoke with the tentant about this. Advised the home owner and rental agency as well. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-95-358 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Zone 1 rates are good only a few 10th's lower than normal and flush rate 1.5 lower than it should be. Zone 2 rates are good slightly Above design. Roots from large evergreen are running over the ground in zone 1, there is a very good chance that this roots are crushing or kinked tubing. The tree should be removed and tubing and loops uncover to inspect. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92421 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
09/18/2023 | Alternative | RoutineScheduled | 2013-143-0166 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/14/2023 | Alternative | Routine/Scheduled |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip Field - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 01:00 PM
08/02/2023 | Alternative | RoutineScheduled | 185-STS-17130 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | R & R Enterprises, Inc | 1942001111 | William | Robinson | 1.000000 | 1000 | AS-500 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | Dec 30 1899 12:00AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
11/02/2023 | Alternative | Routine/Scheduled | 151-15-0072 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 42.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 05:47 PM
10/19/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. Effluent filter installed or maintained | Pending Review | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | trouble shootiong and replacement of bottom float on recirc side, it is now responding correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/21/2023 | 09:30 AM
08/07/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced plastic riser on splitter box per FXCHD. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/29/2023 | Dec 30 1899 3:58AM
01/12/2023 |  | Follow-Up | 175-07-0311 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Met local pumper on site. Removed the recirc pump, floats, biotube filter, and pump vault to give pumper good access. Cleaned and reinstalled all parts. Had owner run fresh water into tank until the bottom recirc float was floating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
03/31/2023 |  |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 04:00 PM
11/16/2023 | Alternative |  | 16-184-5001 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/16/2023 |  | 2.580000 |  |  | 1.600000 |  |  | Will be sent separately |  | BOD: 2.58 TSS: 1.60 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 12:00 AM
02/22/2023 |  | Routine/Scheduled | 087-STS-6617 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/22/2023 | 11:56 AM
02/21/2023 |  | Routine/Scheduled | 2013-143-0047 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Bionest |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Cleaned air filter. Tested float operation. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | 11:42 AM
10/27/2023 | Alternative | Routine/Scheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Sandfilter, Recirculating |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 10:36 AM
05/26/2023 |  | RoutineScheduled | SWP-05-276 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment crystal clear. 2 cracks on Eco flow pod 1 small, 1 medium size and barely leaks when water running above ground, recommend fixing when media gets replaced. Added RootX to d-box due to tree being close to tox and to half inch of water standing in clean out close to box. Recommend digging box if it gets worse or when peat gets replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
03/06/2023 |  | RoutineScheduled | 10-125-157 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/06/2023 | 12:00 AM
05/30/2023 | Alternative | RoutineScheduled | 175-16-0203 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 8"scum/ Microfast-18"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-5733 ETM-985h 14m/ Dose-37.5 On-11m 21s Off-2h/ Peak counts-4 ETM-46h 54m/ Watermeter-0,536,685.9/ Zone rates: Z1-3.3 / Z2-3.3/ Z3-3.2/ Z4-3.2/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/27/2023 | Alternative | Routine/Scheduled | S 800-17-0207 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | Dec 30 1899 11:48AM
12/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-00-0086 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
10/30/2023 | Alternative | Follow-Up Component Maintenance | 179-11-0181-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Re-plumbed drain piping from pods to distribution box. Replaced distribution box and headers with high quality components. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
02/03/2023 |  |  | 2013-143-0133 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | We are pumping the solids tank 2/9/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
04/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
05/01/2023 | Alternative | Routine/Scheduled | 061-STS-21156 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | EZ Treat Sandfilter |  | Pump | Gravity | Trenches |  | 300.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 12:10 PM
05/18/2023 | Alternative | RoutineScheduled | 2018-143-0126 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [18 empty] | Replaced ReCirc pump | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/11/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/04/2023 | 12:00 AM
03/02/2023 | Alternative | RoutineScheduled | SD-05-247 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank due to scum & sludge accumulation in the tank. It may be advisable to pump the aerobic treatment unit at the same time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
08/17/2023 | Alternative | Routine/Scheduled |  | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Biofilter - media spent - requires replacing - raked best able. Pump Basin - float sensors, pump and controls operating. Dbox - intact | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/21/2023 | 09:30 AM
03/02/2023 |  |  | 177-06-0192 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
05/12/2023 | Alternative | Pump-Out Only | 136-06-0104 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Owner has an alternative onsite sewage system. Requested pumpout of septic tank only ... denied any additional services. Unknown service provider. Marked as functioning - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 12:15 PM
07/28/2023 | Alternative | RoutineScheduled Component Maintenance | SP-01-593 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Check valve for zone number 2 stock open and check valve for zone number 1 not shutting down completely so is not dozing correctly, both need to be replaced. Not much splashing going on in the microfast unit, recommend to dig up air line to check for leaks or replace air line. Outstanding proposal for replacing hydronic unit. Will send proposal for repairs. Sanitary wipes in septic tank. Treatment is clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
03/27/2023 |  | RoutineScheduled | 177-14-0221-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
01/12/2023 | Alternative | RoutineScheduled | 151-07-0310 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 2.000000 | 1000 | Clearstream | Clearstream | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 12:00 AM
12/03/2023 | Alternative | Routine/Scheduled | 093-13-0058 | Isle Of Wight | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Due for pump out. Refill not required. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and transducer is functioning properly. Flushed and cleaned vortex filter. No quick disconnect union for discharge pump -Aeration: Water level normal. Flushed and cleaned weir. Non-serviceable airline for diffuser. Due for pump out. Refill is required for proper operation and to prevent damage to components. -Air Pump/Blower: Not functioning -Control Panel: Audible alarm is not functioning properly. Visual alarm is not functioning properly. Panel door is broken -Drip Field: Found no signs of surfacing on dispersal field | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/13/2023 | Dec 30 1899 9:12AM
09/25/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 1:00PM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/01/2023 |  |  | 177-16-0197-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
02/02/2023 |  | RoutineScheduled | 03-125-082 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Fast |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/02/2023 | 12:00 AM
11/30/2023 | Alternative | RoutineScheduled | 151-17-002 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service | 1942001034 | Kent | Cuthbertson | 4.000000 | 45000 | 15000 | 15000 | Pump | Gravity | Trenches | UV | 19697.000000 | ["None"] | ["None"] | YES | [8 empty] | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 03:00 PM
11/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 06/13/2023 | Sample Chamber | 22.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/20/2023 |  | Routine/Scheduled | 128-06-132 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - Dosing - float sensors, pump and controls operating. BioFilter - fiberglass patch intact - peatmoss in poor condition. Pump Basin- Discharge - float sensors, pump and controls operating. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 08:30 AM
02/07/2023 |  | RoutineScheduled | 163-STS-337090 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was cleaned. The textile sheets were sprayed off. The two pumps were pulled and the effluent screens were sprayed off. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/11/2023 | 01:00 PM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
10/22/2023 | Alternative | RoutineScheduled | SD-96-13 | Culpeper | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1000 | septic | Multi-flo | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Cloudy | 6.900000 |  |  | 1.010000 |  | 10/22/2023 | Sample Chamber | 7.000000 |  |  | 38.300000 |  |  | Attached to this report |  | Tss is high. Need to do some work on the sand filter to get the flow moving better. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/06/2023 | 07:00 AM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0065 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Blower needs replacing. Conveyance line between septic tank and ATU needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/29/2023 | 03:58 AM
12/18/2023 | Alternative |  | 88-184-93 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/18/2023 |  | 2.810000 |  |  | 4.930000 |  |  | Will be sent separately |  | BOD: 2.81 TSS: 4.93 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
08/08/2023 | Alternative | Routine/Scheduled |  | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss in fair condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 08:30 AM
11/13/2023 | Alternative | Routine/Scheduled | 093-18-0024 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 10:51AM
09/01/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Gravity | Trenches |  | 600.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:35 PM
02/16/2023 |  | RoutineScheduled | SWP-04-116 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex tank & pump tank due to sludge accumulation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
10/25/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV Bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/15/2023 | Dec 30 1899 2:02PM
07/17/2023 | Alternative | Reportable Incident | 17-120-0035AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 7.000000 | [7 empty] | Owner called due to the light being on - H20 running from house - left toilet test kit. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the buzzer. The timer is set to 2 minutes every 2 hours. Took 5 year BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 3:30PM
08/10/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-1772 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 10:55AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/10/2023 |  | Routine/Scheduled | PPIE-B3TLDP | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The grade on the pipe for the Clearstream is settled - need to dig up between the Clearstream tank and pump tank to get the pipe straight. The timer is set to 6.5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 8:45AM
08/22/2023 | Alternative | RoutineScheduled | SWP-01-241 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 1.000000 | 1250 | 0-4 | 0-0 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 6.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 02:00 PM
03/16/2023 | Alternative | Reportable Incident | 136-xx-legacy | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Pressure | Trenches | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Found system flooded - pumped 1000 gallons from treatment system to restore operation. Found circuit breakers tripped / OFF at residence. Primary septic tank - effluent screen serviced. Processing Tank - recirc - pump, spray grid and media drapes serviced. U.V. - bulb and housing serviced. Processing Tank - discharge - pump, float sensors & controls operating. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/20/2023 | 08:00 AM
04/20/2023 |  | Follow-Up | 550-STS-6650 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped and cleaned the Clearstream tank, septic tank, and pump tank due to them having paint in the tanks. Disconnected the pressure switch on the aerator, UV alarm, and UV power - need to hook up once there is enough water in tanks. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/20/2023 | Jan 1 1900 8:00AM
11/02/2023 | Alternative | Reportable Incident | 05-120-0304 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Repairs: -Installation of 6" Effluent Filter in Septic Tank -Installation of a used Tipping Bucket in the Ecoflo Treatment Module -Installation of 3 new Floats Installation of a Float Tree Assembly to secure Floats -Installation of 1 new Float -Installation of 18" Riser on the Septic Tank ****-Replacement of Ecoflo Biofilter - includes: - Purchase & delivery of new Biofilter (specialty peat moss) - Pumping of Septic Tank - Removal of existing Biofilter using a specialty Vacuum Truck - Disposal of existing Biofilter - Installation of the new Biofilter -Installation of a high-head Turbine Pump includes: - Removal & disposal of spent Pump - Manufacturer Warranty -American Onsite 2-Zone Drip Control Panel -American Onsite 2-Zone Automatic Headworks Assembly ***COMPLETE SA WHEN DONE WITH REPAIRS**** Annual Maintenance: -Septic Tank: Below normal level, was just pumped Replaced riser and filter on site -Discharge/Pump Tank: Below normal level, was just pumped Installed new turbine pump and floats on site -Peat Moss: Peat was replaced on site Tipping bucket replaced on site -Control Panel: Panel replaced on site -Drain Field And headworx: Headworx replaced on site Drainfield showing no signs of surfacing | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/06/2023 | Dec 30 1899 11:07AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 182-19-0017 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | reccomend keep drainfield mowed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-193 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Outstanding proposal for adding riser to inlet side septic tank to get rid of roots. Peat showing its age may need replacement soon, evaluate next year. recommend to dig up d-box at time of peat replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
05/26/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired broken force main in pump tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | Dec 30 1899 1:44PM
05/03/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/16/2023 |  | RoutineScheduled | 101-17-0638 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
03/08/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Advantex | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | .5' Scum, 6" of sludge in septic tank,0 scum little loose sludge in outlet side. Field looks good. Pumps, floats, alarms are all operational. 2509 discharge pump cycles 35h 54m run time. 23096 recirc pump cycles 1078 h 57m run time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:10 PM
04/03/2023 |  | Reportable Incident |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced deteriorated DBox with new 8 port concrete dbox. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 06:30 AM
12/08/2023 | Alternative | RoutineScheduled | 041-STS-260653 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 |  |  | Gravity | Gravity | Mound | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | YES | None | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | 12:00 AM
05/19/2023 | Alternative | Reportable Incident | 128-08-070 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Rebuilt compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/18/2023 |  | RoutineScheduled | 101-05-0445 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity |  | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/23/2023 | 12:00 AM
09/21/2023 | Alternative | RoutineScheduled | 182-17-0012 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | [5 empty] | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | repairs made 10/30 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | 12:00 AM
07/18/2023 | Alternative | Routine/Scheduled | 228-09-0358A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 9:25AM
11/09/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Norweco Singulair ATU |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Effluent Screens"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 12:40 PM
09/26/2023 | Alternative | RoutineScheduled | 07-142-0141 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 500 | Advantex |  | Pump | Pressure | Trenches |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Septic Tank Baffles","Level Sensor Operation","Effluent Screens","Distribution Pump Operation","Dispersal System Operation","Control Operation"] | YES | [6 empty] | Thin crust accummulation, recommend pumping next year | [9 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | Dec 30 1899 1:00PM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 06:33 AM
10/26/2023 | Alternative | Routine/Scheduled | 228-14-0398 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 10:00AM
04/12/2023 |  | Reportable Incident | 057-STS-92764 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called about an alarm for a month or two. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The pressure switch on the aerator is not hooked up - should be. Replaced the alarm light bulb. The timer is set to 8 minutes every 2 hours. Everything needs to be pumped out and cleaned and flush the drip tubing. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/12/2023 | 09:30 AM
10/19/2023 | Alternative | Follow-Up Component Maintenance | SD-14-303 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Pulled RSV from recirc tank and then removed bottom cap and toy plastic ball. Cleaned RSV cage, replaced missing plastic sphere (now has 2) and installed new rubber tip. Ran recirc pump for 30 seconds, verified effluent flowed over to discharge tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
08/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 08/29/2023 | Sample Chamber | 18.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/08/2023 | Alternative | Routine/Scheduled | 04-160-0020 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/08/2023 | 11:00 AM
07/05/2023 | Alternative | RoutineScheduled | 109-04-0683 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Bio Microbics Micro-Fast |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Sludge level-scum layer over 1" and septic zone 12"-16 sludge in Septic zone of tank - 16" sludge in Side port. Blower Alarm operational, cleaned blower filter. No Pumping needed this year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/30/2023 | 09:30 AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 2002-93-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | 6.900000 | 7.300000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 10/16/2023 | 12:58 PM
11/06/2023 | Alternative | Follow-Up | 04-197-A18 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | [33 empty] | System is dead no tablets | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 182-18-0085 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired air vent Recommend moving sandbox away from system and swing for health and safety concerns | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
10/06/2023 | Alternative | Routine/Scheduled | 03-120-0390A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. Noted signs of leaking fixtures from residence -Recirculation Tank: Water level high due to leaking toilet within resistance. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Noted signs of root infiltration around base of risers and along the top seam of the tank -RSV: Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. Media has exceeded life expectancy. Media lid safety support struts have failed. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 12:42PM
08/23/2023 | Alternative | Routine/Scheduled | 16-137-0043 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 2.000000 | 1250 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Pump alarm checked. Pump operation checked. Peat checked. System appears to be operating normally. Etm 543.46, ct 27839. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | Dec 30 1899 11:00AM
01/14/2023 |  | Routine/Scheduled | 800-12-0100 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/14/2023 | Jan 1 1900 10:47AM
02/27/2023 |  | Initial Visit |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["Septic Tank Baffles","Dispersal System Operation"] | ["Dispersal System Operation","Septic Tank Baffles"] | [18 empty] | adjusted pressure. baffle cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Advantex should be pumped and manifold needs to be cleaned to function properly. Air release valve in the field is broken and there is effluent surfacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
07/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation"] | [] | NA | [17 empty] | Septic Tank-10"sludge 8"scum/ Microfast-14"sludge/ Pump Tank-2"sludge/ Pump out needed on the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-1407 ETM-62h 19m/ Pump2-1323 ETM-58h 32m/ Peak-16/ High-19 On-2m 45s Standard Off-8h Peak Off-6h 24m/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/03/2023 |  | RoutineScheduled | 179-09-0184-SP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The peat has settled in all five modules and is holding water. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | 07:17 AM
01/31/2023 | Alternative | RoutineScheduled | 109-STS-32932 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
12/21/2023 | Alternative | RoutineScheduled | 182-02-0488 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | recommend pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2024 | 12:00 AM
01/26/2023 | Alternative |  | 150-07-0208 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected | System is now working correctly. The breaker was off so the pump was not running. Turned it on and pump working properly. She did say it had tripped the breaker so we told her it might be going bad. It hasn't tripped while we were here. No apparent drain field issues. Th peat in all four pods looks good . Had a few small roots. Suggested septic root killer to her and told her to keep the area around the pods cut down | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/03/2023 | 12:00 AM
04/20/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [7 empty] | 04/20/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 175-19-0161 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 10:33 AM
02/25/2023 |  | RoutineScheduled | 05-125-147 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/25/2023 | 12:00 AM
07/15/2023 | Alternative | RoutineScheduled | 109-92-1130 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Low Pressure Dosing System |  | Pump | Pressure | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Annual inspection. 16" of accumulated solids in septic tank. 10" of "fluffy" solids in discharge pump tank. Flushed all eight (8) low pressure lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 07:03 PM
08/10/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | 2023 Annual, cleaned, nothing to report | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled | 165-STS-336783 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Recirculation Pump","Dispersal System Operation"] | ["Auxiliary Filter","Recirculation Pump","Dispersal System Operation"] | [18 empty] | Missing 10' round cover for air relief. RCV ball stuck causing low level alarm. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/19/2023 | 12:00 AM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance | SD-11-325 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Owner had local pumper (Butler) pump out the septic tank about a month ago. Drip rates last year were just a little over half of what they were at start up. Replaced one of the pressure regulators (zone 4, closest to street) as a test because the regulators are known to loose accuracy and sometimes restrict flow. All zones were almost identical to last year so no improvement from changing the regulator. Next step is to uncover the drip manifolds and look for crushed or kinked tubing caused by settling or roots. After that is done, additional topsoil should be added to cover the manifolds to protect from freezing. Drip dose is roughly 20 gallons compared to the design of 35 gallons. Owners are not yet impacted by this as they don't use much water. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
04/12/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | new timer installed | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
03/06/2023 |  | RoutineScheduled | 175-16-0208 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Adjusted run time to 5m46s to get rid of full 262.5 gallon dose. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
01/23/2023 |  |  | 033-16-0077-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Multi-Flo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/19/2023 | Alternative | RoutineScheduled | -STS-43348 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Sludge levels-- 2-4" Scum- 20-24" sludge in Septic zone of tank. Discharge 5-10" sludge- Pump tank no access- Owner should arrange us to come back and meet a pumper out this fall or spring ahead of the routine inspection. Removed and cleaned RSV (noted-loose handle- may need to replace in future to new design). Cleaned Biofilter, sprayer manifold and sprayed off media. Flushed and Brushed headers and ran pump until water ran clear. All floats tested ok, alarm ok. - COunters Discharge. Ct 153,107 vs 148529cycles last year, ETM 153,571mins vs 148954 Min - Rec. ct 329,531 cycles vs 311,652 cycles or 17,879cycles and the recirc pump run time was 150,868min vs 141,810 min last year. about 151 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0255 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0105 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled | 099-17-0085-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | 2.000000 |  | MicroFast |  |  |  | Drip |  |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation","Other"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/08/2023 |  | Routine/Scheduled | NYII-B37KJJ | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | Jan 1 1900 2:10PM
07/14/2023 | Alternative | Routine/Scheduled | 01-177-1233 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable |  | None | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 10:00 AM
06/29/2023 | Alternative | Initial Visit | 550-STS-6722 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - light is now off. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Fixed the grade on the pipe in the Clearstream. Needs 1 valve box with lid. It was raining at the time of service and could not check out the drainfield or mound. The timer is set to 5 minutes every 2 hours. Did not take initial samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | Dec 30 1899 11:30AM
01/12/2023 |  | RoutineScheduled | 14-137-0077 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton |  |  | Advantex AXRT |  | Pump | Pressure |  |  |  | [] | ["Attached Growth Medium","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","Auxiliary Filter"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2023 | 12:00 AM
03/01/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The d-box was replaced and backfilled. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 2 of the pods were not able to be opened due to bushes growing between them. Home owner needs to remove bushes so we can open pods | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
02/27/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Aquarobic Mini Plant | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 12:03 PM
04/26/2023 |  | RoutineScheduled | 153-STS-20271 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | 7.100000 | 5.600000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 05/15/2023 | 12:48 PM
10/18/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [9 empty] | 83.000000 |  | 4700.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | Dec 30 1899 1:00PM
06/21/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-2787 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | UV is not working | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/21/2023 | Dec 30 1899 9:50AM
08/23/2023 | Alternative | RoutineScheduled | 175-10-0197 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | EcoVirginia LLC | 1942001235 | William | Poindexter | 2.000000 |  | Septic | Puraflo | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Level Sensor Operation"] | ["Effluent Screens","Level Sensor Operation"] | YES | None | [17 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/23/2023 | Alternative | RoutineScheduled | 105-09-0109 | Appomattox | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Delta Whitewater | Gravity | Gravity | Discharge | UV | 350.000000 | ["Effluent Screens"] | ["Effluent Screens","SludgeScum Accumulation","BlowerCompressorAerator Operation","Disinfection"] | YES | None | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/23/2023 | 05:15 PM
08/25/2023 | Alternative | Routine/Scheduled |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | 01:00 PM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The aerator was not functioning and was replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
05/12/2023 | Alternative | RoutineScheduled | C-06-111-0134 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | EcoPod-N |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic tank 1-2" scum layer and 6-10" sludge, Ecopod treatment good aeration. Septic tank No open access lid installed- It was Pumped 2 years ago by Sinks Septic, Treatment tank no scum and fine sludge trace. Identified an slgiht air leak, at pvc union needs glue or a screwable 2 pc pvc union to make it easy to access. System is fully operational and does not need pumping this year! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
03/31/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [8 empty] | 1468.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
06/02/2023 | Alternative | Routine/Scheduled | 2003-143-0306 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump tank - float sensors, pump and controls operating. Dbox intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 12:30 PM
06/02/2023 | Alternative | Reportable Incident | 073-STS-105721 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Repalced distribution box with new. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 12:30 PM
01/13/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.600000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
02/17/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Replaced both Solenoid control valves, reattached wiring and tested function of both the valve and they both were opperational. Pump Count 45781, Time pumped 50133 min, HLA 122, Sec. count 6253, P.F.86, Flow meter 457,700g, 20 psi on pressure gauge when running | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/01/2023 | 09:30 AM
06/14/2023 | Alternative | RoutineScheduled | 182-04-0335 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Best 1 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | scheduled for septic pumpout | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | 12:00 AM
06/15/2023 | Alternative | Follow-Up Component Maintenance | 099-10-0117-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [7 empty] | 06/15/2023 |  | 101.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
10/14/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | BioCoir |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Annual inspection. 8" solids crust on top of septic tank, mostly grease and toilet paper. 6" of solids on the bottom of the septic tank. Good aeration in treatment unit. Tested discharge pump controls and alarm. A pump out of the septic tank and discharge pump needs to be scheduled. This will be the first pump out since installation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2024 | 07:03 PM
08/29/2023 | Alternative | Routine/Scheduled | 11-142-0304 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Biomicrobics Retrofast | Puraflo | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. BioMicrobics RetroFast - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls operating. Biofilter - 4 Modules- peatmoss in poor condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | Dec 30 1899 7:45AM
11/14/2023 | Alternative | Routine/Scheduled | 05-160-0224 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 04:00 PM
01/09/2023 |  | RoutineScheduled | 17-152-009 | Lee | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | Clearstream |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-91611 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Disinfection" ,"Distribution Pump Operation"] | ["Disinfection" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
03/01/2023 |  | RoutineScheduled | 11-125-138 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Recirculation Pump","Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 12:00 AM
11/06/2023 | Alternative | RoutineScheduled | 166-06-589 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | checked sludge, cleaned filter, checked peat | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/29/2023 | Alternative | RoutineScheduled Component Maintenance | 175-99-0361 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [5 empty] | 08/29/2023 |  | 19.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
07/20/2023 | Alternative | Pump-Out Only | 151-11-0043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | None | None | Pump | Pressure | Pad | Not Applicable | 450.000000 |  | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Pumped primary septic tank. full service conducted 07/17/2023 - Eljen Synthetic sand filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 06:45 AM
01/31/2023 | Alternative | RoutineScheduled | 154-03-0039 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
04/06/2023 |  | Routine/Scheduled | 234-14-307 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [15 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | Jan 1 1900 1:00PM
07/12/2023 | Alternative | RoutineScheduled | 015-STS-336864 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Pressure | Mound | Not Applicable | 750.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 12:00 AM
01/26/2023 |  | Routine/Scheduled | 12-12-0202A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/26/2023 | Jan 1 1900 8:54AM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/13/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | [8 empty] | 12/13/2023 | [9 empty] | 180 day inspection BOD <2. TSS <1 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
02/23/2023 |  | Routine/Scheduled | 234-13-463 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | Jan 1 1900 3:55PM
03/10/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
06/16/2023 | Alternative | Routine/Scheduled | 2005-143-0074 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump and effluent screen serviced. TReatment Module - media drapes & spray grid serviced. PUmp Tank - float sensors, pump and controls operating. Drip Field - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 09:00 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/16/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | ["Control Operation"] |  | Musty | Cloudy | 7.610000 |  |  |  |  | 01/16/2023 |  | 12.000000 |  |  | 19.900000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:00 AM
05/25/2023 |  | RoutineScheduled |  | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 3.000000 | 2800 | Advantex RT unit |  | Pump | Pressure | Drip | Not Applicable | 250.000000 | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Recirculation Pump","Effluent Screens","Attached Growth Medium","Control Operation"] | YES | Sulphitic | Clear | [15 empty] | The entire system is in compliance with the health departement regs, and approved plans. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
12/06/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
03/22/2023 |  | Reportable Incident | 124-STS-2379 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Owner called due to an alarm going off and light is on. Meet with the pumping company and pumped out the septic tank and Clearstream tank. Replaced the relay in the panel. Disconnected the pressure switch on the aerator and cut the UV off due to the pumping. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/22/2023 | Jan 1 1900 7:45AM
02/22/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/09/2023 |  | Routine/Scheduled | 18-120-0148AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Advanced Septic |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - PuraSys SBR - Primary septic tank - normal level - recommend pumpout. Processing Tank - sludge return operating. Processing Tank - Aeration unit mixing present - serviced. Processing Tank - dosing pump, float sensors & controls operating. Surge Box & Dbox fractured - recommend replacing both. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | Jan 1 1900 7:30AM
02/01/2023 |  | Routine/Scheduled | 800-11-0117 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | Jan 1 1900 12:13PM
12/08/2023 | Alternative | Routine/Scheduled | 085-STS-33270 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/08/2023 | Dec 30 1899 11:53AM
05/15/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-51967 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | [7 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | Float replacement | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:00 AM
06/09/2023 | Alternative | Routine/Scheduled | 166-04-824 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | Control Operation | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Alarm Event - Processing tank - high level - recirc pump, RSV and effluent screen serviced. Found Control panel not functioning - able to pump tanks down in HAND. Treatment Module - media drapes & spray grid serviced. Pump Tank - high level - float sensors, and pump functioning. 06/15/2023 - control panel replaced - timer settings adjusted. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/20/2023 | 06:45 AM
03/23/2023 | Alternative | RoutineScheduled | 139-09-0125 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Replaced burnt out alarm bulb for septic panel and moved switch from silence to normal (in this condition, owner would have been unaware of any alarm conditions). Replaced missing clean-out cap and plug, raised it about 9" so lawn service won't run over it. Septic tank needs pumping and needs to have a 24" lid to grade in place of the wedge lid with 6" pipe (poor access). The pump tank has evidence of infiltration at the buried inlet wedge lid, hole/ crack in sidewall near midseam, and where the two 3/4" pvc lines were stuffed through the same 4" hole (mud visible). No water came through return line after running pump about 45 seconds (normally almost instantly). Spin filter was relatively clean but had some mud inside. Started checking out the automatic headworks and discovered 5 failed glue joints as well as a break in the 3/4" force main (from settling). Ended up replacing about 20 pvc fittings to restore the headworks. Found the flow meter buried under 2" of gravel and mud with a very loose threaded inlet connection. Removed and flushed meter, then reinstalled with brass meter couplings. Found another leak (failed glue joint at inlet side of field flush valve) during test cycle. Repaired that and removed gravel/grit from under the diaphragm. Filter flush valve also needed cleaning, but could not access one bolt for filter flush valve. Out of daylight. Returned 3/24 and cleaned filter flush valve. Finally ready to run full length test cycle. Pump shut off after about a minute, then restarted about 2 minutes later. Repeated several times. Verified proper voltage to pump. Replaced pump with same model. Zoeller Tri-check assembly in horizontal position was too heavy for 3/4" force main (already repaired once). Replaced it with individual components. Recommend running 2" pipe all the way through tank wall before bushing down to 3/4", and running 3/4" return line through a separate knock-out in side wall. Cleaned field flush valve again. Last test cycle was good for 9.1 gpm (11.5 flushing) at 9.10 amps. Will try to obtain design records from health department and will send repair proposal to owner for remaining work. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
05/03/2023 | Alternative | Initial Visit | 128-12-069 | Essex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Trenches | UV | 450.000000 | ["Control Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - ALARM - previous service provider = J. Pinnix. Tanks in high level - UV Failure tripping pump circuit breaker - disconnected UV system and pumped system to normal operating level. Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. UV system failure Pump Tank - float sensors, pump and controls operating. Recommend replacing pump control panel and UV system . | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/04/2023 | 06:45 AM
02/15/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 3.000000 |  | septic | 4 Puraflo pods | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 0 Scum, 12" of sludge in septic tank, 0 sludge in 1st pump tank, Peat in Puraflo pods is ok a little low. raked the peat out and leveled out. sample box in good shape. 2nd pump tank good, ran all pumps. Walked field no leaks. return pressure at 35 with little return. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 09:00 AM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance | SD-11-18 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Control Operation"] | ["Recirculation Pump" ,"Control Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Influent level high in septic tank due to very dirty septic filter. The spinner nozzle closer to the pumps had fallen out of the manifold causing poor distribution of the effluent onto the sheets. Disassembled the nozzle and reinserted into the manifold, normal spray pattern restored. In the past 30 days, system averaged 2 discharge cycles per day at 2.8 minutes each. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
12/05/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | BioWheel |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | November 2023 monthly report. Total flow for month of November 2023 - 23,648 gallons. Average daily flow- 788 gallons per day. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 07:03 PM
05/12/2023 |  | RoutineScheduled | 179-15-0214-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Recirculation Pump" ,"Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Minor bridging near tops of sheets from septic slime, not "worm dirt". Treated effluent looked reasonably good. Pinhole clogged in zone return diaphragm causing intermittant flushing. Cleaned and reamed diaphragm, valve working correctly again. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
06/14/2023 | Alternative | Routine/Scheduled | 234-15-44 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 10:55AM
12/23/2023 | Alternative | RoutineScheduled | 109-07-0396 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 750 | MultiFlo ATU |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. 4" of solids in treatment unit. Good aeration. 6" of solids in discharge pump tank. The treatment unit, septic tank and discharge pump tank may need to be pumped out next year. Very good treatment quality. Cleaned drip manifold solids spin filter. Tested floats, pump and alarms. Pressure bell is a little "clunky" in terms of picking up tank level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2024 | 07:03 PM
06/12/2023 | Alternative | Routine/Scheduled | 151-06-0337 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable | 750.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump TAnk - float sensors, pump and controls operating. Biofilter - SIX Modules - Peat moss in poor to fair condition - raked / turned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 02:45 PM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/29/2023 | 12:05 PM
11/10/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/10/2023 | Dec 30 1899 8:53AM
02/20/2023 | Alternative | Initial Visit | 171-09-0022 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  | Gravity | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","Auxiliary Filter"] | ["Dispersal System Operation","BlowerCompressorAerator Operation","Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
11/03/2023 | Alternative | Routine/Scheduled | 166-03-819 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Advanced Septic |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | 06:03 PM
07/18/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-3708 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 12:15PM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
05/23/2023 |  | RoutineScheduled | 196.04.041 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Assure Plumbing & Septic LLC | 1942001502 | Wayne | Fishel | 3.000000 | 1000 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["None"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 12:00 PM
04/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast |  | Pump | Pressure | Drip | UV |  | ["Disinfection","Attached Growth Medium","SludgeScum Accumulation"] | ["Disinfection"] | NA | [17 empty] | Septic Tank-12"sludge 8"scum/ Microfast-14"sludge/ Pump Tank-0"sludge/ Pump out required on the Septic Microfast Tank due to sludge levels/ Blower air filter cleaned and blower working correctly/ Recommend replacement of the contactor in the control box, detaching from the din rail but still functioning / Controls, pump, floats and alarms functioning properly/ UV-Light sleeve cleaned, Replaced the light and ballast and now functioning properly/ Counts: Pump-4385 ETM-1058h 38m On -15m Off-3h Peak Off-1h 48m / Peak-15 ETM-100h 15m/ High-27/ Watermeter-0,200,662.9/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/16/2023 |  | Routine/Scheduled | 13-142-0083 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/16/2023 | Jan 1 1900 2:47PM
03/02/2023 | Alternative | Reportable Incident | 150-15-0018 | King William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator and changed the mesh screen in the spinfilter. The UV is not working - needs to be addressed. Repaired the return (it was broken). The septic tank needs to be pumped out. There is visible wetness on the drainfield - once it dries need to keep an eye on it. The timer is set to 11 minutes every 1 hour. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/02/2023 | 11:00 AM
05/30/2023 | Alternative | Routine/Scheduled | 151-02-514 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - residence - normal level - effluent screen serviced. Primary septic tank - cottage - normal level - effluent screen serviced. Pump Tank - Cottage - float sensors, pump and controls operating. BioFilter - peatmoss rootbound - unable to rake / turn - recommend replacing. Pump Basin - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 01:15 PM
10/12/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 10:55AM
10/02/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-17112 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/03/2023 | 12:00 AM
10/16/2023 | Alternative | RoutineScheduled | 115-06-0107 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. Effluent filter installed or maintained | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Best1 AWS 500 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","BlowerCompressorAerator Operation","Auxiliary Filter"] | ["Effluent Screens","BlowerCompressorAerator Operation","Auxiliary Filter"] | NA | Musty | [15 empty] | Inspected | Blower Alarm is operational. The Blower, Air filter and Effluent filter brush were cleaned. Sludge levels in 1000G septic tank-Scum layer minimal on top and 16-24" settled sludge in septic zone(about 3/4 full), Aeration zone has a just trace of sludge and discharge zone has a trace of sludge (both zones basically still empty). History- system was last pumped Dec 2020/Jan 2021, after an initial visit in December 2020 discovered and electrical surge or lightning fried the components we replaced the blower motor, control panel and damaged tank lids. The system was pumped by Foutz Septic. In futrure when water is avaiable you may get the tank pumped and refill it afterwards with water. The system should mix up and sludge spead throughout after useage returns but the tank should be pumped after useage returns and waters available. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/17/2023 | 05:30 PM
02/06/2023 |  | Reportable Incident |  | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | AOSS - Initial Visit - ALARM / Reportable Incident. NO SERVICE CONDUCTED - Unknown service provider. Repaired fractured forcemain adjacent to driveway where utility contractor trenched through. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/07/2023 | 07:30 AM
03/06/2023 |  | RoutineScheduled | 175-08-0071 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
04/17/2023 |  | Reportable Incident |  | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Upgraded pump and controls. Installed new access risers on septic tank and pump tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/18/2023 | 08:15 AM
12/29/2023 | Alternative | Reportable Incident | 179-14-022 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Came out for septic consult on Microfast Customer stated there was a sewage smell coming from the back deck area Found that the aeration has 12 in of suspended solids causing smell to come from the vent Switched the cap from the inspection port with the vent grate from the pipe above treatment Told customer to inform us if the smell is still present Customer would like estimates for charcoal filter and pumping and refill | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 09:53 AM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens" ,"SludgeScum Accumulation"] |  | NO | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Panel is not working properly due to damaged wires. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | Dec 30 1899 2:02PM
08/31/2023 | Alternative | RoutineScheduled | 16-183-006 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | FAST |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | 12:00 AM
06/16/2023 | Alternative | Routine/Scheduled | 149-STS-10570 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/16/2023 | Dec 30 1899 12:25PM
05/15/2023 | Alternative | RoutineScheduled | 115-05-0351 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | [15 empty] | Inspected | Sludge level-under1" Scum & 10" Sludge in Septic tank. Water level 1 ft low in septic tank- home has little water useage. Pump Chamber -sludge. Effluent screen was clean and dry above water level. Alarm functional and pump is operational, Peat was moist and the tipping tray dry. System has not had much useage, No ponding in peat moss. Pump tank union leaking @ quick slip lock union in pump tank due to age, best to repair when and if the pumps fails. Owner should fine a company to seal the mid seam septic tank water level appears at midseam. system is operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
04/19/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/05/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
06/30/2023 | Alternative |  | 099-18-0138 SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
08/22/2023 | Alternative | Initial Visit | 550-STS-6526 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 17.000000 |  | 2900.000000 | [5 empty] | Serviced system. Checked the panel and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the relay, replaced the P-20 pump (new serial # 2211-140056), and replaced the alarm float. Wired pump through the pump float. Installed a 3/4" brass check valve on pump headworks. The timer was set at 5 minutes every 1 hour changed it to 2 minutes every 2 hours. Took initial BOD and Fecal samples. NOTE - Fecal sample was high - system should function properly after service. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/22/2023 | Dec 30 1899 10:30AM
04/10/2023 | Alternative | Reportable Incident | 047-16-020 | Culpeper | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 |  | septic |  | Gravity | Gravity | Trenches |  |  | [] | [] | [18 empty] | See Attached | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/20/2023 | 03:10 PM
03/31/2023 | Alternative | RoutineScheduled | 07-174-0195 | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3250 | 1250 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","SludgeScum Accumulation","Distribution Pump Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | YES | None | Clear | 6.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | 12:00 AM
10/30/2023 | Alternative |  | 033-15-0078-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/27/2023 |  | Reportable Incident |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | None | None | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced damaged / failing DBox with new. Spliced to existing Conveyance Line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | Jan 1 1900 6:30AM
09/20/2023 | Alternative | RoutineScheduled | 031-STS-24106 | Campbell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central | Acres of Virginia, Inc. | 1922001044 | Melvin | Collins | 1.000000 | 1500 | Septic Tank | Aquaklear | Gravity | Gravity | Discharge | UV | 450.000000 | ["None"] | ["None"] |  | Septic | Cloudy | 7.100000 |  |  |  |  | 09/27/2023 | Sample Tap | 25.800000 |  | 860.000000 | 30.000000 | 122.000000 | 14.700000 | Will be sent separately |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/23/2023 | 01:00 PM
06/29/2023 | Alternative | RoutineScheduled | 107-11-0200 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | [] | [18 empty] | Need to trim around system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 05:15 PM
09/18/2023 | Alternative | RoutineScheduled | 128-11-053 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | checked sludge, cleaned filters, flushed drip lines | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping micro fast. Strongly recommend clearing/mowing drainfield area before any brush gets too large. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/08/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Jan 1 1900 12:26PM
11/22/2023 | Alternative | RoutineScheduled | 06-172-0056A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1000 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | Dec 30 1899 3:00AM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0005-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Distribution Pump Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Control Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
08/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Alleghany-Roanoke | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Aquasafe |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [8 empty] | 08/15/2023 | Sample Tap | [6 empty] | Attached to this report | Inspected | Located in Montgomery County. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
03/21/2023 |  | RoutineScheduled | 05-113-278 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/21/2023 | 12:00 AM
10/25/2023 | Alternative | RoutineScheduled | 09-160-0240 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 12:00 AM
02/06/2023 |  | Routine/Scheduled | 550-STS-6440 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 11:45AM
04/14/2023 |  |  | 124-STS-2379 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Rappahannock |  | 1942001165 | Michele | Ware | [9 empty] | [] | [] | [17 empty] | Inspected | No inspection details or site visit entered and address is not on septic system AND/OR we have records on it. Believe this was entered by mistake. MWEBB 4/14/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/11/2021 | 06:12 AM
06/20/2023 | Alternative | Routine/Scheduled | 136-06-0185 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 12:15 PM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0017-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
12/14/2023 | Alternative | RoutineScheduled | 179-STS-91692 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 2000 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | NO | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2024 | 02:00 PM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89535 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Recirculation Pump" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Recirculation Pump" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
08/05/2023 | Alternative | RoutineScheduled | 107-09-0259 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
08/31/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. biofilter - peat moss in good condition - raked / turned. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | Dec 30 1899 11:30AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-92415 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Bio Barrier | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
01/12/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | Jan 1 1900 8:47AM
10/19/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | Dec 30 1899 10:40AM
11/16/2023 | Alternative | RoutineScheduled | 153-STS-20286 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Blower filter cleaned but found the air line was broken, Repaired and now functioning properly/ Septic Tank-12"sludge 0"scum/ Microfast-14"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ Recommend pump out of the Septic - Microfast Tank due to color and time air line was broken/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-4675/ Pump Run Time-536/ Hand -9/ High-46/ No breakout or spongy areas on the drip field and dosing properly. Returned on 12/27/2023 : The Septic-Microfast Tank does not require a chemical cleaning. Pump out has been done and Microfast ATU is clear and functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/20/2023 |  | Reportable Incident |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | [9 empty] | ["Distribution Pump Operation","Level Sensor Operation"] | ["Distribution Pump Operation","Level Sensor Operation"] | YES | [17 empty] | peplaced N140 Zoeller pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 PM
07/14/2023 | Alternative | Routine/Scheduled | 03-120-0053A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced - recommend pumpout. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 9:30AM
07/21/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0238 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Bio Barrier | none | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
04/13/2023 |  | Routine/Scheduled | 133 07 0102 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 02:15 PM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Drip system appears to be functioning exactly as designed. Field shows perfect emitter spacing. If viewed from Spinks Ferry, it might appear that there is a nitrified streak coming from the pump chamber riser down, but during inspection, there were no signs of any malfunction, sewage on the ground, or any other explanation for the discoloration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/10/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [6 empty] | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/29/2023 | 01:58 PM
10/10/2023 | Alternative | Reportable Incident | TELS-BC6JQN | Southampton | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit - should be raised full of ants. The timer is set to 2 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/10/2023 | Dec 30 1899 3:45PM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | 099-06-0272-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
02/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/13/2023 | Alternative | Reportable Incident | 16-120-0489ACR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Upon arrival, I found the primary pump tank in high level. I checked the floats and found the pump enable float working intermittently. Homeowner gave approval to replace floats in pump station. I replaced floats while on site. I checked and confirmed floats are functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | Dec 30 1899 3:45PM
03/10/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Pumps will not alternate. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | Jan 1 1900 7:20PM
07/25/2023 | Alternative | Follow-Up | 121-STS-13581 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | - follow up for system, everything functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 12:00 AM
06/29/2023 | Alternative | Follow-Up Component Maintenance | 175-17-0438 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Installed Norewco UV Unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/30/2023 | 10:30 AM
02/23/2023 |  | Reportable Incident |  | Bedford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | AquaKlear |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Start up call after replacement of the home with New home. Found Pump tank, pump opperational by float. Alarm float and buzzer not operational. Did not located the septic tank or no access was provided at grade. Did not locate the blower motor for the Aquaklear. Did not located the Aquaklear treatment tank. It needs a blower mr and accesible lids on the septic and treatment tanks. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/24/2023 | 09:30 AM
04/26/2023 |  | Routine/Scheduled | 550-STS-6640 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 9:35AM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | UV bulb replaced while onsite. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/20/2023 | Dec 30 1899 2:30PM
09/28/2023 | Alternative | RoutineScheduled |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | trash | Microfast | Gravity | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/29/2023 | 09:15 AM
11/09/2023 | Alternative | RoutineScheduled | 133-STS-95412 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, system check - okay, replaced broken audible alarm | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/10/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-84200 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Found broken wire for zone #1 solenoid, fixed. Wet spot in drip field due to a bad adapter, replaced. Recommend replacing both solenoids for zone valves in the near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
07/25/2023 | Alternative |  | 13-113-145 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/25/2023 |  | 2.940000 |  |  | 4.000000 |  |  | Will be sent separately |  | BOD: 2.94 TSS: 4.00 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/25/2023 | 12:00 AM
02/24/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 10:50 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0126 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [null] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Multiflo |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic tank minimal scum 1-2" & 12" sludge - MultiFlo 3" scum on deck and 2-6" sludge in treatment. May need to pump this year- Pump tank 4"trace- Pump runs good, alarm operational, aspirator in multiflo providing good aeration. Multiflo . Pump Count 13850 vs 13488 (362 cycles since last visit) ETM 57115min vs 56350 vs 55858 min (765 min or12.75 Hours since last reading) System does not need pumping now, maybe 6 months to a year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/28/2023 | Alternative | Reportable Incident | 157-01-160 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a red light. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a rebuild kit on the aerator. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/28/2023 | 09:30 AM
10/24/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Owner called due to an alarm - no alarm on arrival. Replaced gauges 1 -50 lb & 1 - 100 lb, set pressures, and performed a draw down test. The timer is at 6 mins 2 hrs. Hooked up the pressure switch and the UV. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/24/2023 | Dec 30 1899 12:00PM
03/12/2023 | Alternative | RoutineScheduled | SD-06-068 | Orange | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2600 | septic | Advantex | Gravity | Pressure | Discharge | Chlorination |  | [] | [] | YES | Musty | Cloudy | 6.800000 |  |  | 1.020000 | eff do. 5.5 | 03/13/2023 | Pump Chamber | 35.000000 | 0.000000 |  | 10.600000 |  |  | Attached to this report |  | BOD was a little high. Hosed down textile in advantex pod. Should help with the BOD | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 03/28/2023 | 08:20 AM
02/20/2023 |  | Initial Visit | 15-172-0274AR | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Inspection / Service. Previous Service Provider = Dominion Onsite Primary septic tank - normal level - some root intrusion at riser. Processing Tank - Normal level - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 7:45AM
03/05/2023 |  | Follow-Up | 041-STS-260277 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/05/2023 | Jan 1 1900 9:00AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/31/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | septic | Fast | Pump | Pressure | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | 2" of scum an 24" of sludge in septic tank, 0 scum and 14" of loose sludge in fast side. Recommend pumping system. Blower, alarms, pump, floats all working, Field good and dry. 758 Cycles, 34hr 16 min run time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 08:30 AM
09/18/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Dispersal System Operation","Control Operation"] | ["Control Operation","Dispersal System Operation"] | [18 empty] | Alarm service call only: Found primary fuse blown in the control box and a faulty solenoid for filter #1. Replaced both and system now working properly. Counts: High-57 Peak-53 ETM-366h 59m/ Pump-5982 ETM-1382h 42m | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/13/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Inspection completed overgrowth has been removed. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 06:01 AM
02/07/2023 |  | Routine/Scheduled | 550-STS-6614 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | Jan 1 1900 8:30AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 |  | RoutineScheduled | 147-05-0082 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 4.000000 |  | Puraflo |  | Pump | Gravity | Pad |  |  | [] | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","Auxiliary Filter"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87440 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 2.71 amps. Treatment crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
02/13/2023 |  | Follow-Up | 179-09-0162-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank pumped out by others prior to peat replacement. Degraded peat was removed by hand with pitch forks and new peat was installed. Peat was purchased from Wright Ready Mix. Degraded peat was disposed at Spotsylvania Refuse. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
01/30/2023 |  | RoutineScheduled | SWP-05-172 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
09/11/2023 | Alternative | RoutineScheduled | 182-06-0062 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation","Dispersal System Operation"] | ["Distribution Pump Operation","Dispersal System Operation","Auxiliary Filter"] | [18 empty] | Pump and filter clogged | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/11/2023 | 12:00 AM
05/17/2023 |  | Routine/Scheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:00AM
05/10/2023 |  | RoutineScheduled | 175-04-0706 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs new recirculation pump & pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
02/21/2023 |  | Routine/Scheduled | 041-STS-259111 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/21/2023 | Jan 1 1900 3:10PM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0183-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | There is tall grass on some areas of the drainfield. We recommend that the drainfield be mowed and maintained in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
03/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Dec 30 1899 12:26PM
01/03/2023 |  | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | Jan 1 1900 9:00AM
09/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [7 empty] | 09/19/2023 | Sample Chamber | 14.000000 |  | 220.000000 |  |  |  | Attached to this report |  | BOD Sample was good / Fecal Coliform is high but we cleaned the UV-Light sleeve. Septic Tank-4"sludge 1"scum/ Microfast Tank-5"sludge 0"scum/ Pump Tank-0"sludge / No pump out needed at this time/ Blower air filter cleaned and working correctly/ Counts: Pump Cycles-1578/ Pump Run Time-68h 45m On-9m 52s Off-2h 14m/ High-level-27/ Watermeter-0022103.5/ No breakout or spongy areas on the drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/11/2023 |  | RoutineScheduled | 179-STS-91866 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
04/20/2023 | Alternative | Reportable Incident | 800-06-0161 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | None | None | NO | [17 empty] | Techs on property to restore operation to the audible alarm. https://www.bryantandlassiter.com/ - service company out of North Carolina, did a "real estate inspection", pumped the processing tank, and re-filled the tank, but were not familiar with Orenco Product or controls to understand that there is an audible alarm delay in the control panel. Company is probably NOT licensed to do onsite system inspections / service in Virginia! Nothing wrong with the control panel, everything functioning properly. Audible alarm delay was set to 180 minutes. - No other service conducted. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/24/2023 | Dec 30 1899 7:15AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/25/2023 | Alternative | RoutineScheduled | 05-125-010 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 12:00 AM
06/14/2023 | Alternative | Routine/Scheduled | S18-180-0089 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Jan 1 1900 12:00PM
05/19/2023 |  | Routine/Scheduled | 228-04-1220 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | Jan 1 1900 2:30PM
07/12/2023 | Alternative | Routine/Scheduled | 550-STS-6399 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 12:05PM
11/09/2023 | Alternative |  | 10-172-0024A Disc | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield |  |  | Bryan | Pope | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/28/2023 | Alternative | RoutineScheduled | 107-16-0126 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
04/19/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/01/2023 | Alternative | Reportable Incident | 061-STS-21156 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | EZ Treat Sandfilter | [6 empty] | Attached Growth Medium |  | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/29/2024 | 01:06 PM
02/11/2023 |  | RoutineScheduled | {FIPSCode}-STS-11298 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NO | Musty | Clear | 7.700000 | 6.300000 |  | 1.800000 |  | 02/13/2023 | Sample Chamber | 75.000000 |  |  | 4.300000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/23/2023 | 12:00 AM
06/15/2023 | Alternative | Reportable Incident | NYII-AYTJT3 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/15/2023 | Dec 30 1899 5:00PM
01/03/2023 |  |  | 02-197-077 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/03/2023 |  | 3.220000 |  |  | 1.200000 |  |  | Will be sent separately |  | BOD: 3.22 TSS: 1.20 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | 12:00 AM
03/03/2023 |  | Reportable Incident | 179-07-0213-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to clogged drip filter not allowing system to pump at the proper rate. cleaned filter. Pump tank needs to be pumped out due to sludge lrvels. Homeowner stated they were going to get the well water tested soon. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-486 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Recomend using sewer camera to verify where headers are located for the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
03/29/2023 | Alternative | RoutineScheduled | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | 7.530000 |  |  |  |  | 03/29/2023 | Pump Chamber | 18.000000 |  |  | 8.000000 | 61.000000 |  | Will be sent separately | Inspected | Bi-monthly inspection and routine sampling completed. All samples collected from and field tests done in the drip discharge tank. D.O. measured at 5.2 mg/L @ 12.3* C; settleable solids = nothing visible; turbidity not measured due to calibration error (new standards to be ordered); BOD = 18; TSS = 8 mg/L; N-N = 46.2 and TKN = 14.8. Effluent did not look as crystal clear as usual. This system routinely treats to 10/10. Will dig deeper into treatment process if effluent does not look better at next visit. In the past 26 days, the system pumped an average of 1,121.0 gals/day at 388.6 gals/cycle (avg.) for a total of 29,148 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping prior to 2024 inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/24/2023 |  | Pump-Out Only | 2013-143-0047 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Bionest |  | Pump | Gravity | Trenches | Not Applicable |  | SludgeScum Accumulation | SludgeScum Accumulation | YES | [16 empty] | Pumped Out | Pumped out trash chamber. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | 01:14 PM
12/12/2023 | Alternative | Routine/Scheduled | -STS-6907 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 12:30PM
03/01/2023 |  |  | 181-17-0073 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 2.000000 | 1200 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. Effluent filter checked and cleaned. No apparent leaks in system or drain field area. Control panels functioning properly. System did not need to be pumped. Lids were properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 08:20 PM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | 175-13-0489 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
08/23/2023 | Alternative | Reportable Incident |  | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Fuji |  | Pump | Gravity | Pad | Not Applicable | 1000.000000 |  | None | N/A | [17 empty] | Full install of treatment system initiated. Completion of installation will require system inspection by AOSE and Engineer of record. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/28/2023 | Dec 30 1899 10:00AM
09/22/2023 | Alternative | Routine/Scheduled | 228-15-0116 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | Dec 30 1899 10:51AM
11/02/2023 | Alternative | RoutineScheduled Component Maintenance | 177-19-0020-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend removing the tree that has fallen on the end of the drainfield and maintaining this area in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
04/20/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [7 empty] | 04/20/2023 |  | 19.000000 | [5 empty] | Will be sent separately | Inspected | no air vac access programmed panel properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
05/08/2023 |  | RoutineScheduled | 175-06-0230 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | J&G Septic Service |  | James | Kleindl | 3.000000 | 3750 | Delta whitewater n60 |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 07:15 PM
03/11/2023 |  | Reportable Incident | 175-10-0213 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [17 empty] | Alarm service call only: Found faulty UV-Light bulb. Replaced and cleaned sleeve/ Checked floats, pump and alarms - functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/24/2023 | Alternative | Routine/Scheduled | 151-00-337 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 6.000000 | 17000 | Puraflo |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 50.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 03:05 PM
01/24/2023 |  | RoutineScheduled | 175-16-0436 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Advantex spinners would not move when recirc pump was turned on. Pump intake was plugged with a lot of stringy sludge. Cleaning the recirc pump intake and the spinners restored normal operation. Septic tank is close to needing pumped and will be due for the 5-year pumping in January. Observed insulation damage to the wires for the field flush solenoid valve and the heater, possibly from mice. Repaired one connection. Owner looking into adding heated pipe tape in place of the original strip heater (very expensive). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
05/24/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 428 | Clearstream |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/08/2023 | 09:51 AM
01/02/2023 |  |  | 08-192-104 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/02/2023 |  | 2.240000 |  |  | 1.400000 |  |  | Will be sent separately |  | BOD: 2.24 TSS: 1.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2023 | 12:00 AM
04/18/2023 | Alternative | Initial Visit | 015-STS-337690 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [15 empty] | Envirocompliance has been closed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
01/09/2023 | Alternative | RoutineScheduled | SD-15-48 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"Control Operation" ,"Disinfection" ,"Distribution Pump Operation"] | ["Recirculation Pump" ,"Auxiliary Filter" ,"Control Operation" ,"Disinfection" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection and maintenance. Flushed out UV housing and replaced the UV lamp. Riser pipe was broken for ARV on the outside edge of mound and valve box lid was broken. Repaired pipe and installed new valve box and lid. Cleaned small amount of dirt from field flush valve. Discharge tank has a lot of sludge (considering it is a pump tank) and needs pumped out ASAP. Owner said he would make arrangements. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
11/20/2023 | Alternative | RoutineScheduled | 132-14-0141 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 2500 | Multi Flow |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","Effluent Screens","Attached Growth Medium"] | YES | Musty | Clear | [14 empty] | Inspected | Sludge Scum Accumulation - Septic 12", ATU 12", Pump Station 3" Treatment Socks Swapped out with clean units Pump Amperage - 11A | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 10:30 AM
06/23/2023 | Alternative | RoutineScheduled | 019-STS-29352 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Other conventional maintenance performed | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | LPD |  | Pump | Pressure | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [16 empty] | Inspected | Pump tank and alarm were operatrional. We found when running the effluent pump the discharge line was leaking in the walkway, we contacted the agent and Foutz for repairs right away and the line was repaired by Foutz after our visit. We located all 3 & 9 of the end caps on each side and 12 of the center caps in the middle on the drainfield for the Low pressure discharge. A flow test was not preformed nor a flush due to the line leaking. Foutz recently came out to flush the entire drainfield lines after our intiial visit and cleaned up brush and debris and located the center and end caps. We found them all visiable as designed. The septic tank has no above ground accsess and was not seen, Foutz was to return to pump the tank after our visit.. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/30/2023 | 09:30 AM
03/15/2023 | Alternative | Routine/Scheduled | 234-03-11324 | Chesapeake | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Discharge | Chlorination | 600.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basing - float sensors, pump and controls operating. Biofilter - Peatmoss ponding, looks like Mud - raked / tuned. Chlorinator - tablet feed serviced - supplemental air pump operating. Discharge point - clear of debris. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/16/2023 | Dec 30 1899 9:00AM
08/29/2023 | Alternative | Pump-Out Only |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [16 empty] | Pumped Out |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/01/2023 | 08:30 AM
01/12/2023 | Alternative | RoutineScheduled | 187-STS-37347 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Fuji Cen 7 | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Dispersal System Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 947 Pump Cycles, 70h 34m runtime. 0 Scum, 5" of sludge. Nothing in the pump tank. Cleaned blower filter. Checked drip field, looks good. return pressure @ 40psi. Everything in working order | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2023 | 12:30 PM
11/03/2023 | Alternative | RoutineScheduled | 07-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 8.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/20/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV Bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/02/2023 | Dec 30 1899 11:08AM
05/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pods are full of roots need to investigate and figure out how and what to do about roots | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
06/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Septic Tank | Septic Tank #2 | Pump | Pressure | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [7 empty] | 06/08/2023 | Sample Chamber | 60.000000 |  |  | 136.000000 |  |  | Attached to this report |  | Septic Tank #1-6"sludge 6"scum/ Septic Tank #2-4"sludge 0"scum/ EZ-Treat Septic & Recirculation Tank-3"sludge/ Pump Tank to Drainfield-2"sludge/ Pump Tank to LPD Trenches-2"sludge/ No pump outs needed at this time/ Recirc. pump intake cleaned/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pumps to Drainfield: Pump1-008667 ETM-0259917/ Pump2-008543 ETM-0259713/ Pumps to LPD Trenches: Pump1-731 ETM-31h 7m/ Pump2-694 ETM-37h 15m/ Peak-16/ High-17/ EZ-Treat Recirculation Pump Counts: 0187367 ETM-0830126 On-2.5m Off-10m/ No breakout or spongy areas on the LPD or Drainfield Trenches. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/18/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the disc filter. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV light bulb. The timer is set to 9 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/18/2023 | Dec 30 1899 3:45PM
09/01/2023 | Alternative | Routine/Scheduled | 02-172-0752AR | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & Spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 8:00AM
08/17/2023 | Alternative | RoutineScheduled | 06-160-0095 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | PURAFLO |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Septic | Discolored | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 AM
12/06/2023 | Alternative |  | 17-186-041 | Smyth | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/06/2023 |  | 2.940000 | [5 empty] | Will be sent separately |  | BOD: 2.94 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
12/26/2023 | Alternative | RoutineScheduled | 182-96-0485 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand filter |  |  | Pressure | Trenches | Not Applicable |  | ["None"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 2.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Recirculation Pump"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 11-2-23 WWTP Area: Needs other. Southeast corner of fence has bent post and bent support rods. Chain-link fence is intact. Septic tanks: Okay Flow EQ pump tank and lids: Okay no service needed. First lid needs to be replaced. AX Max Units: Spinners need cleaning come back Drip Field Walkover: Drip field walkover issues Pump 7 Meter reading: - 15509358.4 Pump 8 Meter Reading: - 12927 951.0 Return Meter Reading: - 1203048.44 11/14/2023 10:52:52 PM - Steven please check pump #5 - been getting alarms since 4pm on Thursday. Pressure gauge is in Makenzies office at JML for install on Max unit scritchfield 11/14 -Issue corrected Pump outs 11-5-23 4200 Advantage 11-9-23 4200 Advantage 11-15-23 4200 Advantage 11-22-23 4000 Advantage | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/16/2024 | 01:58 PM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-134 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Completed annual inspection and maintenance. Replaced broken riser on septic tank outlet. Dug up and discarded the concrete wedge lid at inlet end of septic tank. Added plastic riser and lid to grade. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/22/2023 | Alternative | Initial Visit | 199-STS-7018 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream, cleaned the disc filter, and cleaned the UV light bulb. Changed the filter in the aerator. Could not check the drainfield due to raining at the time of service. The timer is set to 7 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | Dec 30 1899 11:15AM
04/18/2023 |  | RoutineScheduled | 2118-06-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Discharge | Chlorination |  | ["Attached Growth Medium","Disinfection"] | ["Attached Growth Medium","Disinfection"] | NO |  |  | 6.100000 |  |  |  | Ecoli 1MPN/100mL | 04/18/2023 | Sample Chamber | 2.000000 |  |  | 26.000000 |  |  |  |  | Septic Tank-4"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Puraflo Peat turned in all 4 modules and peat in good condition/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-006737 ETM-0009944/ Installed new tablet feeders. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/05/2023 | Alternative |  | 07-184-5004 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/05/2023 |  |  |  |  | 11.200000 |  |  | Will be sent separately |  | BOD: BDL TSS: 11.2 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-231 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Water level in pump tank was lower than pump intake due to 2 bad floats (off and enabler) they were stock close, replaced both and added water to test gallons per minute. Sealed small leak on pump tank riser (J-box grommet). HL-20, ETM-0M PEAK-24, ETM-190H0M. Blower 2.96 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
02/28/2023 |  | Reportable Incident | 136-18-0196 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Control Operation | Control Operation | NO | [17 empty] | Alarm call over weekend - Owner noted control panel failed. Replaced aerator / pump control panel - system restored to proper operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/01/2023 | 10:30 AM
04/03/2023 | Alternative | Reportable Incident | SHUN-BCZQQ8 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the red light flashing - pump in tank seemed to be running constantly. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the relay and replaced the UV light bulb. The timer is set to 6 minutes every 3 hours. Did not take samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/03/2023 | Dec 30 1899 5:00PM
11/01/2023 | Alternative | RoutineScheduled | 107-09-0319 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Best 1 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Polylok lid to be replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced cracked filter | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
10/04/2023 | Alternative | RoutineScheduled | 166-02-317 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | peat check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-336 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
09/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 4"scum/ Microfast-4"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-2546 ETM-418h 59m Peak-16 ETM-170h 2m/High -15/ Watermeter-219,786.04/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/08/2023 |  | RoutineScheduled | 175-16-0343 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | UV |  | ["Recirculation Pump","Disinfection"] | ["Recirculation Pump","Disinfection"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ EZ Treat- 2"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Recirc pump intake cleaned, media in good condition/ Controls, pumps, floats and alarms functioning properly/ Counts: Drip Pump-3102 ETM-458h 17m/ Z1-3gpm/ Z2-4.3gpm/ Z3-4.3gpm/ Z4-4.3gpm/ EZ-Treat on-2.5m off-14m/ Drip dosing on-10m 14s off-2h/ Watermeter-0243178.3/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/07/2023 | Alternative |  | 085-STS-33010 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Carrington Pump & Irrigation | 1942001121 | John | Carrington | 2.000000 |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/16/2023 | Alternative | Reportable Incident | 234-13-425 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/16/2023 | Dec 30 1899 1:30PM
11/01/2023 | Alternative | Routine/Scheduled | 151-15-0110 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 05:02 PM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend replacing UV bulb. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance | 177-14-0236-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens"] | ["Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 175-13-0134 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/17/2023 | 10:52 AM
09/01/2023 | Alternative | RoutineScheduled Component Maintenance | SWT-05-354 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
10/09/2023 | Alternative | Routine/Scheduled | 14-174-0090 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/09/2023 | Dec 30 1899 11:27AM
09/07/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 7.600000 | [14 empty] | Pump not operational | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/09/2023 | 12:30 PM
09/30/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable | 200.000000 | ["Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [17 empty] | Replaced pump and floats tanks have medium corrosion | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/01/2023 | 12:00 PM
04/25/2023 |  | Routine/Scheduled | NYII-ATHMZU | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 12:20PM
06/17/2023 | Alternative | RoutineScheduled | 2095-04-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.500000 |  |  | 1.500000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/02/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/09/2023 | Alternative | Initial Visit | 075-STS-34545 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Pressure | Discharge | UV | 600.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Spray Irrigation/Dispersal - Initial visit. Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - recirc pump, spray grid, media drapes serviced. U.V. Disinfection - bulb and housing serviced - panel tolerances adjusted. Processing Tank - Discharge - float sensors, pump and controls operating. Spray Dispersal - heads inspected, pressure adjusted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | Dec 30 1899 7:15AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
09/05/2023 | Alternative | Routine/Scheduled | 08-160-0245 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 PM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
07/31/2023 | Alternative | RoutineScheduled | 09-177-1007 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 3.000000 |  | EcoPure | [6 empty] | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [8 empty] | 07/31/2023 | Pump Chamber | [6 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 12:00 AM
01/03/2023 | Alternative | Reportable Incident | SD-14-282 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm due to timer float switch only working intermittently. Replaced Connery brand float switch with Orenco brand. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
01/24/2023 |  | Routine/Scheduled | 175-STS-13994 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 12:39PM
01/05/2023 |  | RoutineScheduled | 14-100-0361 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 12:00 AM
08/21/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0091-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. Blower 3.0 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
10/19/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the alarm going off. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The septic tank needs additional risers on it to be properly inspected in the future. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/19/2023 | Dec 30 1899 2:15PM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 182-06-0439 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Ecoflo | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 11/13/2023 |  | 34.000000 | [5 empty] | Will be sent separately | Inspected | Replaced Media Filter | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | This inspection is required annually for VDH. please have new owner contact us at 540-860-8086 to update information and keep current rate | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
05/30/2023 |  | RoutineScheduled | 2090-04-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 06/15/2023 | 12:05 PM
11/10/2023 | Alternative | RoutineScheduled | 13-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 12 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/10/2023 | 12:00 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0212 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
03/13/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | Jan 1 1900 4:10AM
01/20/2023 | Alternative | RoutineScheduled | 133-STS-100802 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 01/20/2023 | [10 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/10/2023 | Alternative | RoutineScheduled | 17-100-0156 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Pressure | Mound | UV |  | [] | [] | [18 empty] | CLEANED HIGH PRESSURE FILTER. REPLACED VENT ON AQUASAFE TANK. EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 12:10 AM
09/01/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-71503 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - Alarm due to lack of Maintenance! Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Gravity feeds to community absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 07:30 AM
08/10/2023 | Alternative | RoutineScheduled | 001-STS-92971 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJI CLEAN CEN 5 |  | Pump | Gravity | Pad | UV | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | SLUDGE JUDGE 4" FROM BOTTOM REPLACED UV LIGHT UNIT | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/14/2023 | 12:30 PM
11/10/2023 | Alternative | RoutineScheduled | SP-05-279 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 1.000000 | 1500 | 0-2 | 0-1 | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Level Sensor Operation","SludgeScum Accumulation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 4.000000 | [11 empty] | Inspected | cleaned system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 10:00 AM
05/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/13/2023 | Alternative |  | 179-STS-90032 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
10/12/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 11:30AM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-333444 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 12/18/2023 |  | 79.000000 | [5 empty] | Will be sent separately | Inspected | Installed remanufactured blower and repaired air supply Unable to screw down middle lid due to egg shape of riser | This AOSS should now return to normal function after having provided the above state routine maintenance | 03/06/2024 | 10:42 AM
04/13/2023 |  | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 9:00AM
05/25/2023 |  | Routine/Scheduled | 2008-143-0175 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Hoot |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level - recommend pumpout and refill. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - sensor probe, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 01:45 PM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/21/2023 | Alternative | Follow-Up | 121-STS-13510 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Inspected | - exercised LPD valves and increased the flow rate from 2in in 2 min to 7in in 2 min, system flow rate now in satisfactory range at this time - this will be checked at next annual maintenance inspection visit in 2024 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled | 17-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 | [11 empty] | Musty | Cloudy | 6.000000 | 2.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
08/31/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/18/2023 |  | Routine/Scheduled | 2004-143-0250 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Best 1 |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routines Service. Trash tank - normal level Aeration Tank - normal level - mixing present compressor serviced. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 09:15 AM
03/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/28/2023 |  | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Advanced Septic |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Pumped primary septic tank and processing tank empty - serviced all components - refilled with fresh water for re-start. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 08:30 AM
01/24/2023 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 03:22 PM
03/27/2023 |  | RoutineScheduled | 108-01-0092 (LEGACY ALT. SYSTEM) | Bath | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2000 | Septic Tank Only | MicroFast | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | [17 empty] | The system did not need to be pumped. The blower and spin filters were cleaned. The controls were operating as designed. One of the two blowers were not operating at the time of inspection so a new starting capacitor was installed. The blower is now operating as designed. There were no visible leaks in the drip field. The drip field was operating as designed. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/03/2023 | 10:50 AM
04/24/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
11/06/2023 | Alternative | Routine/Scheduled | 08-120-0298A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/06/2023 | Dec 30 1899 2:29PM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/15/2023 | Alternative | Routine/Scheduled | 06-131-4118 | Floyd | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 10:45 AM
07/17/2023 | Alternative | RoutineScheduled | 107-03-0367 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. Effluent filter installed or maintained | Pending Review | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Initial Inspection for New Client, Septic tank zone had 6" in sludge, 16-18 in sludge on recirc side, 6" sludge in pump tank. RTU 1118983- Pulled and Cleaned RSV, Pulled/Cleaned Biofilter it was very dirty, Flushed and brushed spray manifold, Checked float switches and found bottom float on recirc side not responding. scheduled to return the next day for the trouble shooting and repair. 1992.3 hours on recirc pump 93,973 cycles, and 200.5 hours on dischrasge pump and 16,944 cycles in history. No recent Alarms in history. Superior septic had dealt with some alrams a few years ago in history. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/21/2023 | 09:30 AM
03/20/2023 |  | RoutineScheduled | SWP-04-93 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 8084.000000 | [] | [] |  |  |  | 7.310000 |  |  |  |  | 03/20/2023 |  | 22.000000 |  |  | 9.300000 | 11.410000 |  |  |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 02:30 PM
01/11/2023 |  | RoutineScheduled | 177-16-0157-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Disinfection"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Disinfection"] | NA | Sulphitic | Discolored | [7 empty] | 2.000000 |  | 1.000000 | 4.700000 |  |  | Will be sent separately | Inspected | We recommend pumping the septic tank and Advantex RT just prior to the house being reoccupied. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
01/23/2023 |  | RoutineScheduled | 177-STS-89493 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
06/30/2023 | Alternative | RoutineScheduled | 153-STS-20334 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Upon arrival system in alarm: Found EZ-Treat Recirculation Step 20 Pump was faulty. Replaced pump and tested, functioning as designed. Septic Tank-6"sludge 2"scum/ EZ-Treat Tank-2"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms now functioning properly/ Counts: Recirc. pump-0086738 ETM-0553149 On -3m Off-13m/ Drip Discharge Counts: 4252 ETM-713h 30m/ No breakout or spongy areas on the drip field and dosing correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/29/2023 | Alternative |  | 041-STS-260226 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3250 | 1250 | 1000 | Pump | Pressure | Discharge | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Pungent | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/29/2023 | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | Dec 30 1899 12:26PM
02/09/2023 | Alternative |  | 101-03-0639 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | John Rod | Temmink | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/11/2023 | Alternative | Routine/Scheduled | 16-120-0137R | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/11/2023 | Dec 30 1899 10:33AM
03/23/2023 |  | RoutineScheduled | 2005-143-0203 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | EcoFlo |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:00 AM
08/23/2023 | Alternative | Routine/Scheduled | 151-04-0008 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 4000 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | 10:23 AM
12/13/2023 | Alternative | RoutineScheduled | 2016-143-0184 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/09/2023 |  | RoutineScheduled | SWP-03-397 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media was ponding bad, augered ans was draining. Slime in media is starting to move into pump basing and distribution box. Treatment does not look to good recommend to have peat replaced. Recommend to replace outlet riser and lid on septic tank outlet with EZ-SET plastic riser and lid also to install access point in inlet side of septic tank. Will send proposal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
05/12/2023 | Alternative | RoutineScheduled | -STS-43145 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge levels-- 2-4" scum layer and 20" sludge in Septic tank- May Get pumped prior to our visit next year. Blower was been replaced by the owner 2 years ago, pump operational. Pump tank 6" sludge. Alarm float and pump run float tested good. Alarm sounded good. FLUSHED RETURN LINE VALVE AND FILTER FLUSH VALVE AND RE SET , WALKED UP TOP AND confirm the drip drainfield IS CUT. Found no leaks on the drainfield uptop the hill. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
12/05/2023 | Alternative | Initial Visit | 810-STS-4095 | Virginia Beach | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Contractor contacted us due to the panel not working properly. The panel is working properly. Pump tank floods when it rains, leaks around risers, and conduit for wires says owner. Alarm float at top of tank. Pump float did not have enough tether to work properly. Need to secure floats properly and seal risers and check tank for leaks | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/05/2023 | Dec 30 1899 12:00PM
04/19/2023 |  | RoutineScheduled | 04-118-0104 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump |  |  |  |  | [] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump","Effluent Screens","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | SP-04-356 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Installed new Advantex sheets & pumped Advantex Tank & Distribution Box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-25166 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation"] | NA | None | Clear | [5 empty] | 05/31/2023 | Pump Chamber | 33.000000 | [5 empty] | Will be sent separately | Inspected | On site for 180 day inspection and BOD sampling. Lab results listed as "<33 mg/L". Effluent looked clear, no signs of clogging in media. This was a random snapshot in time of the treatment process. Had discussion with tenant about use of cleaning products containing "quats". If effluent appears to be cloudy at next inspection, then some investigation will be justified. Both bottom float switches were stuck on which would allow pump cycles when water level was too low. Advised tenant to contact the installer asap for warranty repairs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
03/27/2023 | Alternative | Routine/Scheduled | 800-09-0171 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced pump, UV needs to be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/27/2023 | Dec 30 1899 9:00AM
01/13/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/29/2023 |  | RoutineScheduled | 177-STS-86799 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
03/09/2023 |  | RoutineScheduled | 101-17-0173 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled | 2003-143-0295 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 4.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/28/2023 | 12:00 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/02/2023 | Alternative |  | 17-100-0507 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [8 empty] | 05/02/2023 | Sample Tap | 6.000000 |  | 95.900000 | 5.000000 | 4.800000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
03/16/2023 |  | Reportable Incident | 2009-143-0110 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Hoot |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Repeated alarm events caused by sensor probe failure. Replaced Hoot Controller panel door, and replaced sensor probe. System left operational on departure. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/20/2023 | 07:00 AM
07/21/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0523 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Advantex sheets need replacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
03/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/29/2023 | Alternative |  | 051-STS-17598 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/29/2023 |  | 10.200000 |  |  | 14.000000 |  |  | Will be sent separately |  | BOD: 10.2 TSS: 14.0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled | 14-142-0251 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/15/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced contactor in control panel. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/11/2023 | Dec 30 1899 11:24AM
12/05/2023 | Alternative | Routine/Scheduled | 147-08-0141 | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal water level. No visible signs of structural defects. Inlet sewer line and outlet conveyance line as well as the sanitary tees are cast iron and are very corroded and deteriorated. No riser access on the inlet or outlet of the primary septic tank and both lids are leaking with water soil and root intrusion. No outlet effluent filter installed in the septic tank. Septic tank has over 12" of solids buildup and an indistinguishable amount of sludge(so much that it made it impossible to make an accurate sludge judge reading) Trash Tank Secondary Septic Tank(Orenco tank under first set of media sheets) Condition of above Component Notes for above Component Normal water level. No visible signs of structural defects. No signs of infiltration. Secondary septic tank has 12-14" of sludge which 33% of the tanks water column. Recirculation Tank Condition of above Component Notes for above Component Normal water level. No signs of infiltration. No visible structural defects. Recirc tank has 14" of sludge which is roughly 33% of total tank volume. Floats have aged past their life expectancy. Pulled and cleaned, floats, bio tube filter, and vault. RSV (Recirculating Splitter Valve) Condition of above Component Notes for above Component Normal water level. No visible structural defects. No signs of infiltration. RSV tank has 18" of sludge which is closer to 50% of total tank volume. RSV has lost a check valve boot and is no longer functioning like it is supposed to. Pulled and cleaned rsv Discharge/Pump Tank Condition of above Component Notes for above Component Normal water level. No visible signs of structural defects. Root, soil, water intrusion present around inlet. Pulled and cleaned pump screen and floats. Tank has 12" of sludge out of 14" of water. Pulled and cleaned floats and pump screen. Media Sheets Condition of above Component Notes for above Component Cleaned all sheets and laterals. All emitters functioning properly. Cleaned basin until only clear water returned to rsv tank. Control Panel Condition of above Component Notes for above Component All audible and visual alarms functioning properly, both contactors working properly, no signs of any problems with the control panel at this time, both pumps are pulling 11 to 11.5 A, which is within their historic operating range. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/13/2023 | Dec 30 1899 9:43AM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Clear stream needs pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/23/2023 |  | RoutineScheduled | VAG408232 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | [5 empty] | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | [18 empty] | no discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/23/2023 | 12:00 AM
03/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens"] | YES | Musty | Clear | [5 empty] | 03/16/2023 |  | 68.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Dec 30 1899 12:26PM
01/23/2023 |  | Routine/Scheduled | 136-14-0282 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump tank - float sensors, pump and controls operating. Biofilter - Peatmoss in good condition - Groundhog has dug several holes into the mound system and penetrated into the treatment module. - Peatmoss raked / turned - owner needs to hire pest control company to remove the varmint! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 08:00 AM
01/24/2023 | Alternative | RoutineScheduled | 162-17-0148 | Nelson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/28/2023 | 12:00 AM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/28/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | Dec 30 1899 10:00AM
10/25/2023 | Alternative | Routine/Scheduled | 157-06-0339 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tanks needs to be pumped out - about 3' of sludge in bottom. The pressure switch on the aerator is not hooked up. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/25/2023 | 03:15 PM
11/01/2023 | Alternative | Initial Visit | 093-STS-13783 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 6.000000 | [7 empty] | Owner called due to an orange light on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Fixed the grade on the pipe in the Clearstream. The timer is set to 3 minutes every 2 hours. Took BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 2:30PM
11/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
03/23/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | McKim Septic & Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | NA | [16 empty] | Pumped Out | Pumped out septic/ atu microfast | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/28/2023 | Dec 30 1899 3:00PM
10/09/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0205-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank, ATU and pump tank due to sludge accumulation in the tanks. We also recommend replacing the headworks box heater. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
12/07/2023 | Alternative | RoutineScheduled | SD-90-274 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.980000 |  |  | 1.000000 | [11 empty] | Not enough flow for a formal sample | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/28/2023 | 01:00 PM
11/24/2023 | Alternative | Routine/Scheduled | C05-180-0005 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [9 empty] | 17.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/24/2023 | Dec 30 1899 3:30PM
01/25/2023 |  | RoutineScheduled | SWT-97-422 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots on pump tank wedge lid. Gallons per minute are getting higher every year and no water is surfacing r coming back to septic will monitor next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
12/21/2023 | Alternative | RoutineScheduled | 06-197-A6 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/21/2023 | 12:00 AM
11/10/2023 | Alternative | Follow-Up | 153-STS-20506 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Aquarobic |  | Pump | Pressure | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Installed a new Aquarobic Blower in a new blower enclosure/ Installed a new junction box and new 230 volt contactor in the control box. Tested the blower, floats and system now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/26/2023 | Alternative |  | 179-19-0154-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
08/09/2023 | Alternative | Initial Visit |  | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | UV | 450.000000 | Disinfection | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. U.V. - Salcor - unit set in the ground - no riser protection - unit has failed - recommend full replace and install in protective riser housing. PUmp Tank - float sensors, pump and controls operating. DBox - plastic - intact - all laterals accepting effluent. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/15/2023 | 09:15 AM
09/15/2023 | Alternative | Follow-Up Component Maintenance | 179-06-0231-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | ["Dispersal System Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | NA | [15 empty] | Will be sent separately | Inspected | Septic tank pumped out by others. Degraded peat was removed by hand and new peat was installed.Peat was purchased from Drillers Services. Degraded peat was disposed at Spotsylvania Refuge. Inlet and outlet riser was dug up by homeowner and resealed. Dug up d-box cleaned and video inspected header lines and drainfield. Drainfield has been cut back by homeowner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance | SD-10-335 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. Average daily flow more than double recent months. In the past 10 days, the system pumped an average of 3,442.3 gals/day at 419.7 gals/dose (avg.) for a total of 34,423 gallons. Grass in dripfield needs cut. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
09/28/2023 | Alternative | Routine/Scheduled | 800-STS-14856 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Recirculation: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Not due for pump out. Recirculation pump has met life expectancy. Recirculation pump plumbing has met life expectancy. Recirculation floats have met life expectancy. -RSV: Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. -Discharge/Pump Tank: Water level high upon arrival due to leaking toilet. Water level normal on departure. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Discharge pump has met life expectancy. Discharge pump plumbing has met life expectancy. Discharge floats have met life expectancy. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 10:09AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0407 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
10/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Micro fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 10/31/2023 | Sample Chamber | 21.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0309-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  |  | Trenches | Not Applicable |  | ["Septic Tank Baffles","Dispersal System Operation"] | ["Septic Tank Baffles","Dispersal System Operation"] | [18 empty] | pump line repaired | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | 12:00 AM
08/25/2023 | Alternative | Initial Visit Component Maintenance | 137-STS-26948 | Orange | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Control Operation"] | ["Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Repair system installed to replace a failed drip system. Service provider has agreed to post the discharge sign. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 09/01/2023 | 05:07 AM
10/02/2023 | Alternative | Routine/Scheduled | 151-04-423 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 04:21 PM
06/01/2023 | Alternative | RoutineScheduled | 153-STS-20458 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Prince William | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Setic | Fast | Pump | Pressure | Drip | UV |  | [] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","BlowerCompressorAerator Operation","Control Operation"] | NA | [17 empty] | 12" of sludge and 1" of scum 48" overall liquid depth. Field dry. Alarm was unhooked. I hooked it back up. Alarms are working. Pumps working. 760 pump events, 73 hrs, 39 min. Took BOD and Fecal Coliform sample. Results on both came back out of the limits. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/09/2023 | 10:30 AM
10/03/2023 | Alternative |  | 154-10-0207 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
11/30/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0220 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | EcoPod | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
01/05/2023 |  | Routine/Scheduled | 228-16-0289 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 9:50AM
02/01/2023 |  | Follow-Up | 800-STS-13172 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 6.000000 |  | 1.000000 | [5 empty] | Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | Jan 1 1900 12:00PM
10/16/2023 | Alternative | Pump-Out Only | 03-160-0298 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | - Advanced Environmental maintenance provider, refer to his reports | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 11:17 AM
08/09/2023 | Alternative | Routine/Scheduled | NYII-B9RMWK | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 11:50AM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0238-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Gravity | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend pumping and cleaning the pump tank. It would be advisable to pump the Advantex tank at the same time. We also recommend replacing the lower air release housing and lid and the Advantex module vent cup. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
02/03/2023 |  | Routine/Scheduled | 234-17-0084 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | Jan 1 1900 11:05AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [15 empty] | Will be sent separately | Inspected | Effluent Filter is broken making it unserviceable and needs to be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | 02:21 PM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0003 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | 9/7 Discovered several problems during the annual inspection. The zone return solenoid stuck on during testing of flush rates, replaced it. The bottom float switch (R.O.) was stuck on, and zone 1 check valve was stuck open. 9/8 Returned to complete repairs. Replaced the bottom float switch. Noticed that the end of the float cord for the inside alarm had a bunch of tape on it. Someone had added a 16" extension of float cord by twisting the copper strands together and "sealed it" with black tape. Wires were starting to corrode. Removed the extension and wired the float directly to the incoming power in the junction box. First test of drip rate for zone 2 was high at 7.7 gpm. Replaced check valve for zone 1 as it was stuck open. Rate dropped to 4.5 gpm on second test (same as last year). No spongy spots on either drip mound. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
02/07/2023 |  | RoutineScheduled | 179-STS-89494 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Septic tank was pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/09/2023 | Alternative | Follow-Up Component Maintenance | SWP-04-471 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Homeowner had tree company remove trees. Grinded stumps. Replaced header lines as necessary. Jet cleaned lines as necessary. Seed and strawed construction area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0441 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
12/15/2023 | Alternative | RoutineScheduled |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Control Operation","SludgeScum Accumulation","Effluent Screens"] | YES | Musty | Cloudy | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | Dec 30 1899 9:00AM
09/01/2023 | Alternative |  | 132-14-0052 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Bryan | Jones | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/13/2023 |  | Routine/Scheduled | 133 07 0091 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 11:15 AM
04/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/26/2023 | Alternative | Routine/Scheduled | 093-12-0035 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. BioFilter - peatmoss in good condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | Dec 30 1899 12:00PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/07/2023 | Alternative | RoutineScheduled | SD-13-290 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Control Operation" ,"Disinfection" ,"Auxiliary Filter" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Disinfection" ,"Auxiliary Filter" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Bottom float was stuck on in recirc tank. Vacuumed out water from splice box and replaced that float's wire nuts, proper operation restored. Rinsed out uv housing, cleaned sleeve, and replaced the uv lamp. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
10/06/2023 | Alternative | RoutineScheduled | 2013-143-0157 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/13/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1500 | Auquarobic |  | Pump | Pressure | Drip | Not Applicable | 100.000000 | ["Distribution Pump Operation","Effluent Screens"] | ["Control Operation","BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens"] | YES | Musty | Cloudy | [15 empty] | The entire system is in working order. it was reccommended to have the system pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 11:00 AM
09/29/2023 | Alternative | RoutineScheduled | 06-177-1298 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 2.000000 | 300 | 3 Puraflo Pads |  | Pump | Pressure | Pad | Not Applicable | 300.000000 | ["None","Other"] | ["SludgeScum Accumulation","Effluent Screens","Other"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/29/2023 | 02:30 PM
07/27/2023 | Alternative | RoutineScheduled | 07-142-0260 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/09/2023 |  | RoutineScheduled | 108-05-0023 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | RetroFast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | 12:20 PM
02/03/2023 |  | Routine/Scheduled | 095-STS-6848 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [16 empty] | No Power, Turn on septic/sewer breaker in house panel. The light will come on when you turn the power on. Give the tank a couple of days to work itself down. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | Jan 1 1900 9:00AM
04/08/2023 |  |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/22/2023 | 12:00 AM
03/25/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. 12" of solids in discharge tank, very "fluffy". Flushed treatment unit spray manifold. Cleaned recirculation pump basket filter. Repositioned recirculation pump low float, slightly too low originally. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 07:03 PM
07/22/2023 | Alternative | RoutineScheduled |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | ATU | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 08:35 AM
12/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 0"scum/ Microfast ATU-2"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower is working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-1091 ETM-167h 6m/ Peak-13 ETM-66h 30m/ High-18/ Watermeter-0057412/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic / Ecopod ATU Treatment Tank | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 3"scum/ Ecopod-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-10356 ETM-291h 16m/ Pump2-10464 ETM-287h 39m / On-4m 48s Off-7h 55m/ Peak-6615 High-154/ No breakout or spongy areas on the LPD Pad Site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 3:10PM
10/25/2023 | Alternative |  | ST-05-32 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/22/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | Dec 30 1899 9:55AM
07/17/2023 | Alternative | Reportable Incident | 136-17-0123 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The timer is set to 3 minutes every 1 hour. Did not take 5 year labs due to the aerator not working on arrival. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | 10:00 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0048 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
03/15/2023 |  |  | 087-STS-6193 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Purasys | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
12/14/2023 | Alternative | Follow-Up | 08-197-A13 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  |  |  | Gravity | Gravity |  | Chlorination | [21 empty] | Tablets now installed | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 12/15/2023 | 12:00 AM
02/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | All 3 tanks need pumped out. Their are alot of wipes in the septic tank. Also both the surge box and d-box are badly broken and will need replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/10/2023 |  |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/22/2023 |  | RoutineScheduled | 08-183-100 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Fast |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/22/2023 | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-14137 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/05/2023 | Alternative | Routine/Scheduled | 157-08-0322 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | 10:45 AM
05/11/2023 |  | RoutineScheduled | 133 10 0277 | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic zone 1" scum 6-8" sludge- discharge zone 7" sludge, Punp tank 3-4"sludge -Effluent filter was cleaned- very dirty, good even spray after servicing brushing and flushinf sprayer head. We sprayed off media, Checked FLoats and found bad bottom or on off float for recirc pump, replaced it and system returned to normal operation. alarm is good. Ran system in test mode. sprayed ants in control box. All is functional; flushed the pump tank. spray improved. Recir pump 1560 hours and 648 cycles and discharge pump 2746 hours and 19637 cycles. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | 09:30 AM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 12:48 PM
06/09/2023 | Alternative | Routine/Scheduled | 166-07-0477 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Biofilter - peatmoss in good condition - raked / turned. Pump Basin - float sensors, pump and controls operating - replaced HLA float sensor. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 06:45 AM
12/08/2023 | Alternative | Routine/Scheduled | 133 06 0342 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | 11:45 AM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | 061-15-393 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Effluent appeard a bit murky, not as crystal clear as in past 3 years. Owner said they were having some issues with their water treatment system. Getting that straightened out may restore proper treatment in the Microfast tank. But she is also advised to consider discontinue using scent beads and liquid fabric softener as many of them contain quaternary ammonia (quats) which have a devastating effect on the septic treatment. The 6" inspection port lid was a little difficult to find due to tall grass/weeds and the drainfield was difficult to inspect because of the tall grass. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
01/13/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.700000 |  |  |  |  | 01/13/2023 |  | 13.000000 |  |  | 7.200000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Drain field has surfacing wet spots that need investigating. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
06/16/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | UV bulb and ballast were replaced. The system should return to proper function. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/30/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 9:25AM
12/26/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
10/24/2023 | Alternative | Routine/Scheduled | 196-06-415 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing |  |  | Puraflo |  |  |  | Drip |  |  |  |  | N/A | [16 empty] | Pumped Out | Annual Maintenance: -Septic Tank: Normal level 1 in of sludge and less than 1 in of solids Pulled and cleaned filter Riser leaking -Discharge/Pump Tank 1 Primary discharge: Notes for above Component Normal level Less than 1 in of suspended solids Tested floats and pump all working as should All plumbing intact and pump moving water properly Riser is leaking -Discharge/Pump Tank 2 Secondary discharge: High level when we arrived on site due to pump not functioning Floats are functioning properly however they are aged Riser is leaking -Peat Moss: 3 peat modules all intact 1st peat module racked out in decent condition 2nd peat module racked out however peat is spent and broken down 3rd peat module racked out and in good condition -Control Panel 1 Primary discharge panel: 120 volts coming in All visual and audible alarms functioning properly Pump pulled 13.7 amps All components working properly however panel is aged -Control Panel 2 Secondary discharge panel: 120 volts coming in All visual and audible alarm functioning properly All components work however panel is aged -Drip Field: No signs of surfacing Repairs (10/31): -Installation of 24" Riser on the primary discharge Tank -Installation of 24" Riser on the secondary discharge Tank-Installation of 24" Riser on the Septic Tank -Installation of a Zoeller Pump includes: - Removal & disposal of spent Pump - Manufacturer Warranty -Installation of a Plumbing Kit -Installation of a Plumbing Kit -Installation of a Goulds Pump includes: - Removal & disposal of spent Pump - Manufacturer Warranty -Installation of 6 Floats -Conduit & Wiring between 20' & 30 Pump Out (10/31): | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | 04:08 PM
01/25/2023 |  | Reportable Incident | 264-18-245 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the alarm and red light - installed an aerator rebuild kit. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream, cleaned the disc filter, and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs additional risers on it to be properly inspected in the future. There is visible wetness on the drainfield - most likely from rain - once it dries need to keep an eye on it. The timer is set to 8 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/25/2023 | Jan 1 1900 9:45AM
01/16/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.500000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 12:15 AM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/19/2023 | Alternative | RoutineScheduled | 154-05-1040 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2000 | Puraflow |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter","Control Operation"] |  | Septic | Clear | [14 empty] | Inspected | Sludge/Scum Accumulations - Septic 10", Pump Station 4" Timer Replaced in Control Panel - System in High Water Alarm During Inspection Peat Moss Dry | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/19/2023 | 10:00 AM
06/16/2023 | Alternative | Initial Visit | 015-STS-337065 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [15 empty] | Local lab unavailable | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
03/08/2023 |  | Routine/Scheduled | 199-17-0009 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Trash Tank - recommend pumpout. Aeration Tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. PUmp Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/09/2023 | Jan 1 1900 7:30AM
08/14/2023 | Alternative | RoutineScheduled | 027-STS-18381 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/14/2023 | 12:00 AM
11/27/2023 | Alternative | RoutineScheduled | 115-14-0300 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank | Advantex AX20 | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge level 1-2" scum and 10" Sludge in Septic tank zone. 5" Sludge in Recirc tank, Clear Effluent on top. Owners added mulch this year to cover the system and looks good, Biofilter was very dirty and almost fully clogged, we cleaned and flushed the system. Pump is functional, alarm functional, Brushed Manifold, Cleaned RSV and Ran is test mode. System is fully operational at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/28/2023 | 05:30 PM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-18-0464-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Junction box on recirc tank was hit by mower and lid came off causing water to get in box, vacuumed water and put lid back on. RECIRC: HL 5, LL 147, OVERRIDE 98. DISCHARGE: HL 7, LL 14, OVERRIDE 5. 24 psi. "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
06/09/2023 | Alternative | Routine/Scheduled | 157-11-0006 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the mesh screen in the spinfilter. Changed the diffuser in the Clearstream and changed the filter in the aerator. Added an override float. The timer is set to 6 minutes 15 seconds every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/09/2023 | 11:45 AM
02/15/2023 |  | RoutineScheduled | 101-06-0409 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Advantex AX/RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter","Control Operation"] | NA | [16 empty] | Inspected | Septic Sludge/Scum Accumulation - 12" Treatment Sludge/Scum Accumulation - 6" Pump Station Sludge/Scum Accumulation - 2" Recirculation Pump - 12.25amps, Effluent Pump - 12.89amps Wiring in Control Panel Tightened, wires not secure in terminals | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 01:30 PM
10/13/2023 | Alternative | RoutineScheduled | 019-STS-29495 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aquasafe |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [16 empty] | Inspected | New Installation Start up Inspection -Treatment tank is filled with water and aerating. Alarm is on and functional when tested. Septic tank is new and not yet filled with water. Effluent filter is new and clean and not yet in the water. Drainfield is to the right side diagonally from the system towards the road. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 09:30 AM
06/13/2023 | Alternative | Routine/Scheduled | 234-17-457 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the UV light bulb. Could not locate vacuum breakers - no valves boxes. The timer is set to 6 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | Dec 30 1899 10:00AM
05/24/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Whitewater |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic Tank 1-2" scum, 6-8" sludge, Treatment unit 2-3" scum and 6" sludge trace, Pump Tank 4-6" Sludge. Discharge Pipe in treatment tank was corrected by owner and is opperatioanl at this time..Owner cleans air filter. Good running on dosing pipe. Drip filter cleaned. Drip drainfield looks dry but needs a cutting yearly or biannually to prevent trees. Pressure bell Level indicator on pump panel good reading | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0075-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Control Operation" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Both wedge lids have small roots in tanks, customer said he had a different company dug up and sealed lids. Pods ponding half way due to roots clogging drain line, removed some of the roots. D-box was full of roots removed most of them but line # 2 still have some, recommend to replace dbox with monster box to be able to inspect every year and treated as needed. Recommend to snake camera drain line between dbox and pods to see what's stopping water from draining correctly. Recommend to auger peat after clearing drain line. Will send proposal for all that work. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
06/25/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-11802 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | ISF | Gravity | Pressure | Discharge | Chlorination |  | [] | [] | YES | Musty | Cloudy | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/24/2023 | 08:05 AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-86773 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Dark Brown | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
02/01/2023 |  | RoutineScheduled | 175-18-0010 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Needs new water meter. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/13/2023 | 08:47 AM
03/27/2023 |  |  | 2016-143-0146 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EZ Treat | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Pad | Not Applicable | 750.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | Dec 30 1899 3:20PM
06/15/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
09/27/2023 | Alternative | Routine/Scheduled | 17-120-0158AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 |  |  | Pump | Pressure | Pad | Not Applicable | 150.000000 | ["Effluent Screens","Level Sensor Operation"] | ["Effluent Screens","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | Dec 30 1899 10:11AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/01/2023 | Alternative | Reportable Incident | 154-17-0123 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | ADVANTEX AX/RT |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","Distribution Pump Operation","Effluent Screens"] | YES | Pungent | Clear | [14 empty] | Inspected | CALLED FOR HIGH WATER ALARM - BREAKER TRIP FOR RECIRCULATION PUMP - HEAVY SLUDGE BUILDUP IN TREATMENT TANK FILTER SLUDGE/SCUM ACCUMULATION - SEPTIC 4", TREATMENT TANK 2", PUMP STATION >1" DRIP LINES FLUSHED FOR 20MINS | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/01/2023 | 12:00 PM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | drip time zone 1 8:16 43 gal dose zone 2 7:38 29 gal dose | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/01/2024 | 06:53 PM
09/25/2023 | Alternative | Routine/Scheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1275 | Microfast |  | Pump | Pressure | Drip |  | 750.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/05/2023 | 02:01 PM
05/26/2023 |  | RoutineScheduled | 15-163-0088 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Ecopod |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/26/2023 | 12:00 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/27/2023 |  | RoutineScheduled | 08-163-00448 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 500 | Advantex |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [6 empty] | Recommend pumping in 2 to 3 years | [9 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Jan 1 1900 2:45PM
03/13/2023 |  | RoutineScheduled |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock-Rapidan | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/21/2023 |  | Initial Visit | 1999-143-0065 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | AOSS - Initial Visit by Millers Services. Primary septic tank - normal level - appears to have recently been pumped. Pump Tank - float sensors, pump and controls operating. - extremely dated! BioFilters - 4 modules - peatmoss spent in all Modules and requires replacing. Sample port has 18' of standing effluent - | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/24/2023 | 09:45 AM
01/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Replaced 3 distribution box lids. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
03/23/2023 |  | Routine/Scheduled | 10-142-0081 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level - recommend pump out. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Jan 1 1900 6:45AM
07/26/2023 | Alternative |  | 11-197-056 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 |  | 4.510000 |  |  | 2.300000 |  |  | Will be sent separately |  | BOD: 4.51 TSS: 2.30 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
01/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic & Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Other"] | [8 empty] | 01/30/2023 | Pump Chamber | 25.000000 |  |  | 98.200000 |  |  | Will be sent separately |  | BOD and TSS sample taken | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Dec 30 1899 3:50PM
11/15/2023 | Alternative | RoutineScheduled | 031-STS-25809 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Septic Tank | Norweco | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | 1 yr inspection & regulatory sampling - Old septic tank - Norweco Septic zone 6 " sludge- Aeration zone- aerator working good aeration- No smells- Discharge tank 24" sludge trace (light)- Pump tank 12" sludge, Cleaned Biofilter- both parts, medium dirty- Some Lids screws have failed due to inadequate design from factory - Lids are secure- SMall tree growing at control panels on house need to be cut/removed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
11/20/2023 | Alternative | RoutineScheduled | 01-192-354 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/20/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled | 153-STS-20376 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
10/01/2023 | Alternative | Routine/Scheduled | 041-STS-261101 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/01/2023 | Dec 30 1899 10:30AM
02/23/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | Dec 30 1899 12:46PM
03/22/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Advantex sheets need cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-391 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Owner said that Microfast had alarmed several times recently for short duration. Panel has done this in the past. Turned down the adjustment screw on the pressure switch 1 turn. No problems found with atu, blower replaced in 2021 and running well. The Microfast panel is old/original - recommend replace as well as the pressure treated post that it's attached to. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408270 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Chlorination |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
12/13/2023 | Alternative | Routine/Scheduled | 085-STS-31471 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Checked and confirmed spray pattern is good Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 9:41AM
10/04/2023 | Alternative | RoutineScheduled | 03-197-235 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 12:00 AM
01/19/2023 |  | RoutineScheduled | 033-STS-90111 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
02/16/2023 |  | RoutineScheduled | 175-15-0218 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity |  | UV |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | 7.200000 | 20.800000 | [11 empty] | Will be sent separately | Inspected | Breaker turned off, system was not cycling at Inspection. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 03/01/2023 | 02:21 PM
06/14/2023 | Alternative | Routine/Scheduled | 234-15-167 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 11:50AM
01/20/2023 | Alternative | Initial Visit | 159-11-113 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 | 1000 | Bio-Microbics Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Other","SludgeScum Accumulation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation","Other"] | NA | None | Clear | [14 empty] | Pumped Out | Initial Visit was 1-8-2023, Troubleshoot AOSS for client that stated they wanted a second opinion. Provided the following work on 1-20-2023: Pump septic tank and treatment tank. Replace aerator. Install new control panel for pump chamber. Install new effluent pump. Install new float system in pump chamber. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/20/2023 | 04:00 PM
05/10/2023 | Alternative | Initial Visit | 159-11-0080 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 0.000000 | 12000 | None | None | Pump | Pressure | Drip | UV | 12000.000000 |  | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - community Absorption Field - Initial Visit. Primary pump tank - 12000 gallon - high level on arrival - Control panel found OFF - re-activated and found timer unit not functioning properly. UV System found to be NOT installed properly - No power to unit - No bulb s in unit. No service conducted on individual lots as required by permit and operations manual. Headworks serviced. K-Rain valves appear to be intact. Drip Filed has damaged tubing resulting in surfacing issues. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/25/2023 | 08:30 AM
12/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 12/11/2023 | Pump Chamber |  |  | 2.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/26/2023 |  | RoutineScheduled | 163-STS-338158 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | 0.5 FAST |  | Gravity | Gravity | Mound | Not Applicable |  | ["None"] | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 01:00 PM
07/12/2023 | Alternative |  | 107-12-0203 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 177-10-0129-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
12/26/2023 | Alternative |  | 127-STS-33607 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Carrington Pump & Irrigation | 1942001121 | John | Carrington | 2.000000 |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
12/01/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
03/15/2023 |  | RoutineScheduled | SP-04-142 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
01/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/05/2023 | 11:59 AM
10/12/2023 | Alternative | Routine/Scheduled | 136 03 655 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 6 in of sludge 1 in of solids Pulled and cleaned filter Filter housing intact and filter properly working No signs of infiltration -Discharge/Pump Tank Pump chamber: Normal level Tested all floats and pump all working as should Plumbing intact and pump properly moving water Pump chamber is cracked in multiple places -Peat Moss: Tipping bucket and dispersal trays are intact and working properly Peat is spent holding water, and roots intruding heavily Peat module intact with no cracks or damage -Control Panel: 120 volts coming in All visual and audible alarms properly working however the alarm light housing in broken Pump pulled 7.3 amps -Drain Field: Inspection port not holding any water. No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 04:24 PM
05/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Prince William | EcoVirginia LLC | 1942001235 | William | Poindexter | 2.000000 |  | Advantex |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter"] | ["Attached Growth Medium","Auxiliary Filter"] | YES | None | Clear | [15 empty] | 287.11Hr / 22605 cy | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
08/05/2023 | Alternative | RoutineScheduled | 2126-09-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | UV | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.400000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/23/2023 | 01:49 PM
04/11/2023 |  | RoutineScheduled | 175-90-0082 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/17/2023 | 12:44 PM
10/04/2023 | Alternative | Routine/Scheduled | 053-STS-10327 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | Dec 30 1899 11:54AM
01/17/2023 |  |  | 033-18-0118-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
01/05/2023 |  | Initial Visit | 15-174-0221 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Aqua Klear |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - Unknown when sampling has occurred. Trash Tank - normal level - recommend pumpout. Aeration Tank - normal level - recommend pumpout - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 7:15AM
01/10/2023 |  | RoutineScheduled | 03-197-034 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
08/01/2023 | Alternative | Reportable Incident |  | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | BlowerCompressorAerator Operation | N/A | [17 empty] | System reported alarming over weekend - did not want weekend emergency call. Found compressor failed - replaced with new High Blow 60/80. System restored to proper operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/02/2023 | 07:45 AM
09/18/2023 | Alternative | RoutineScheduled | 182-98-0337 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Septic/Fast to be pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/18/2023 | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled | 175-87-0360 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Demand dose control panel, pump, floats and alarm are functioning properly/ No counts or etm readings on the control box/ No breakout or spongy areas on the LPD Trench area and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/02/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 0" of solids in recirculation portion of treatment unit. 12" of solids in discharge portion of treatment unit. Excellent treatment quality. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 07:03 PM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-08-0419 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens" ,"Level Sensor Operation"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
10/02/2023 | Alternative | Reportable Incident | 07-172-0268A | Powhatan | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 1000 | Eco-Flow |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Distribution Pump Operation"] | NA | Musty | Clear | [15 empty] | Faulty Pump and Float replaced Peat Moss heavily saturated and ponding in Pod - needs replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/02/2023 | Dec 30 1899 5:30PM
02/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/17/2023 | Dec 30 1899 10:44AM
10/19/2023 | Alternative | RoutineScheduled | 121-STS-12748 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 |  | Aquasafe |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [7 empty] | 10/19/2023 | Sample Tap | [6 empty] | Will be sent separately | Inspected | - upon arrival alarm system was on silent, adjusted air line and alarm sounded - everything appears functional at this time, more work may be needed if problems occur | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 12:00 AM
12/15/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:30 AM
06/07/2023 | Alternative | Initial Visit | 151-03-471 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Primary septic tank - high level - effluent screen serviced. Pump Basin - high level - float sensors stuck - vault is leaking and bulging noted. Biofilter - fiberglass appears intact - peatmoss spent, compacted, root bound. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 10:45 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/13/2023 | Alternative | RoutineScheduled | 107-02-0270 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.190000 |  |  |  |  | 12/13/2023 |  | 13.000000 |  |  | 16.900000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | 01:45 PM
08/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | NA | [17 empty] | Septic Tank-12"sludge 6"scum/ Microfast-16"sludge/ Pump Tank-1"sludge/ Septic- Microfast Tank requires pump out and media sprayed/ Blower is not working and requires replacement/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-824 ETM-66h 7m/ Pump2-809 ETM-65h 0m/ Peak-8/ High-9/ No breakout or spongy areas on the LPD Pad site and dosing properly. Returned on 8/11/2023 and replaced the .75 Microfast Blower/ Tested and working properly/ Septic-Microfast Tank has been pumped and media sprayed down. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/10/2023 |  | RoutineScheduled |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 01/10/2023 | Sample Chamber | 8.000000 | [5 empty] | Attached to this report |  | Septic-4"sludge 2"scum/ Microfast-4"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned/ Microfast blower controls and alarm functioning properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/25/2023 |  | Routine/Scheduled | 06-142-0084 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable | 600.000000 | ["Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Owner reported system was alarming the day after being pumped out. System was checked on 5/30/23. Both the recirculation and discharge pump systems had high liquid levels. Everything was working correctly. A lot of water may have been used or pump contactor may be faulty. System is now monitored with remote telemetry. There was a lot grease in the tank. A grease trap is recommended. System was refilled with approximately 1000 gallons of water after it was pumped out. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/31/2023 | Jan 1 1900 12:45PM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20469 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
04/29/2023 |  | RoutineScheduled | 067-STS-38685 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | Modified Extended Aeration |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | YES | [17 empty] | Total flow to drain fields April 2023 -172,889 gallons. Average 6,174 gallons per day. All aspects of the system are operational. Wasting of settled mixed liquor from the clarifier to the digester and decanting of supernatant from digester are occurring regularly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 07:03 PM
06/30/2023 | Alternative | RoutineScheduled | SD-14-320 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 0"scum/ Microfast-2"sludge 0"scum/ No pump out needed at this time but may be necessary next year/ Blower air filter cleaned and blower functioning properly/ Controls and alarm functioning properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/13/2023 |  | RoutineScheduled | 179-15-0279-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Recirc pump and biotube filter look dark black as if bacteria is dead (maybe antibiotics) but treatment is not bad. will check next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
08/31/2023 | Alternative | RoutineScheduled | 10-183-016 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/31/2023 | 12:00 AM
04/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Loudoun Environmental Treatment | 1942001460 | Raymond | Kirkpatrick | 3.000000 | 1500,1500,1250 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | NO | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 2:00PM
03/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection on a conventional pump septic system. The septic control panel is an interior demand dose. There is 1 clean out near the house that we camera snaked the sewer line from. It was clear. The septic tank has a plastic riser on the outlet side of the tank. The tank was pumped out and the filter was cleaned. The state requires that every 5 years all conventional septic tanks must be pumped out and filed with the state and county. Also the filter manufacture recommends the filter be cleaned every 6 months to prevent a back up. The pump tank, riser, electric box, floats, pump and force main were inspected. All were in working condition. I would recommend at some point that the 3 floats be replaced. The cords are very stiff and the weights on them have rust build up on them. But they are working at this time. The plastic splitter and both plastic d-boxes were dug up they were about 4" under the ground. All 8 header lines were camera snaked and were clear. The drain field was probed. At time of inspection all components were in working condition. This inspection does not guarantee the life of any component. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/21/2023 | Alternative | Routine/Scheduled |  | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. BioFilter - peatmoss in good condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 06:30 AM
10/05/2023 | Alternative | RoutineScheduled | 12-184-060 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ATL |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Dispersal System Operation","SludgeScum Accumulation"] | ["Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 12:00 AM
11/15/2023 | Alternative | RoutineScheduled | 07-184-5011 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/15/2023 | 12:00 AM
05/11/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic tank 1: scum and 26" sludge, Recirculation zone no scum and 14" sludge and discharge zone no scum and 14-16" sludge- May want to pump in a year. Cleaned BioFilter, RSV Spray Manifold. Tested both Pumps, ok, Alarm ok, Alarm History 7-6-22 highlevel. Bottom float on recirc appears to be going bad and we should schedule a replacement visit before it goes bad and causes alarms. Float switches test good but bottom recirc slow to respond. 2 PVC ball valves on header going bad and need replacement due to age-2,921.7 hours recirc pump run time and 63,897 cycles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
08/07/2023 | Alternative | Reportable Incident | 234-17-0299 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/07/2023 | Dec 30 1899 7:15AM
07/06/2023 | Alternative | RoutineScheduled | 001-STS-92361 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | CHICKEN CITY ROAD |  | Pump | Pressure | Mound | UV | 450.000000 | [] | [] | [18 empty] | REPLACED AIR COMPRESSOR HOUSING-SLUDGE JUDGE 4" FROM BOTTOM 1" FROM TOP EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 10:15 AM
04/27/2023 |  | RoutineScheduled | 015-STS-334127 | Augusta | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | grass to close to back of media filter wipes Pressure gauge bad | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/21/2023 | 03:35 PM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 107-03-0305 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 11/08/2023 |  | 61.000000 | [5 empty] | Will be sent separately | Inspected | Media is ponding and lab sample abnormal. Would recommend replacing media due to this | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
12/04/2023 | Alternative | Routine/Scheduled | 147-11-3062 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Changed the filter in the aerator and changed the mesh screen in the spinfilter. Replaced the UV light bulb. The Clearstream tank needs to be pumped and cleaned and also the septic tank. The timer is set to 8 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | Dec 30 1899 1:20PM
01/04/2023 |  |  | 2006-143-0353 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
07/10/2023 | Alternative | Reportable Incident | 147-13-0038 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 | ["Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | System in Alarm - discharge pump failed, float sensor failed. Trash Tank - normal level Aeration tank -normal level - mixing present - compressor serviced. Pump Tank - pump ON float sensor failed - replaced - discharge pump pulling high amperes and tripping breaker - replaced P20 HHT with new. Control panel operating. U.V. bulb and housing serviced. Drip Field - headworks serviced. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/11/2023 | Dec 30 1899 7:15AM
06/05/2023 |  | RoutineScheduled | 07-163-0042 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Effluent Screens","Level Sensor Operation","Control Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
12/18/2023 | Alternative | RoutineScheduled | 14-160-0046 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | [9 empty] | [] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation"] | NA | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20283 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | AP80 compressor needs replaced/or rebuilt. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/06/2023 | 09:34 AM
08/07/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1200 |  |  | Pump | Pressure | Trenches |  | 600.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:13 PM
04/24/2023 |  | RoutineScheduled | 15-120-0498A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","BlowerCompressorAerator Operation","Control Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled | 093-14-0153 | Isle of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | JEFulbright Septic, LLC | 1942001131 | Jason | Fulbright | 1.000000 | 3000 | Aerobic Treatment Unit |  | Pump | Gravity | Trenches | Not Applicable | 1000.000000 | [] | [] | NA | Musty | Clear | 6.900000 | 3.000000 |  |  |  | 12/13/2023 | Pump Chamber | 32.000000 |  |  | 29.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | Dec 30 1899 3:30PM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 182-15-0208 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 10/10/2023 |  | 30.000000 | [5 empty] | Will be sent separately | Inspected | Lab normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
03/21/2023 |  | RoutineScheduled | 177-06-0260-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
09/22/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | Dec 30 1899 10:25AM
08/18/2023 | Alternative | Routine/Scheduled |  | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss root bound & ponding - poor condition - raked best able. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 10:30 AM
04/18/2023 | Alternative | Follow-Up | 800-STS-14575 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 11.000000 |  | 3.000000 | [5 empty] | Took BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | Dec 30 1899 11:00AM
07/20/2023 | Alternative | RoutineScheduled | 136-18-0133 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 |  | Clearstream 600dc3 |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["None"] | ["None"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 12:00 AM
12/29/2023 | Alternative |  | 17-100-0507 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
02/11/2023 |  | RoutineScheduled | 175-19-0229 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Advantex |  | Pump | Gravity | Discharge | UV | 500.000000 | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.500000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/15/2023 | 12:00 AM
04/11/2023 |  | RoutineScheduled | 113-03-190 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | The air pump has stopped working. A replacement has been ordered. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
05/31/2023 |  | RoutineScheduled | 179-13-0132-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
01/13/2023 |  | Routine/Scheduled | S 093-19-0058 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | EZ Treat Sandfilter |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - effluent screen serviced - 90% clogged. Processing Tank - recirc pump and RSV serviced. Treatment Module - media bags & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 11:00AM
11/04/2023 | Alternative | Initial Visit | 147-11-0052 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 | 1000 | Norweco |  | Pump | Pressure | Drip | UV |  | ["SludgeScum Accumulation","Effluent Screens","Disinfection"] | ["Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [14 empty] | Pumped Out | Performed annual maintenance inspection. Verified septic tank had been pumped by Jerry Septic Tank Service. Replaced UV lamp. Cleaned intermediate screen. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/04/2023 | 12:00 AM
04/04/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | a new air blower and blower control panel was installed. septic system is in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
02/05/2023 |  | Routine/Scheduled | 041-STS-261408 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | [16 empty] | Turn septic breaker on in the house. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/05/2023 | Jan 1 1900 11:30AM
01/05/2023 |  | Routine/Scheduled | 228-05-0109 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 1:35PM
10/15/2023 | Alternative | Routine/Scheduled | 17-142-0233 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump |  |  | Not Applicable | 500.000000 | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Septic Tank Pumped out 11/03/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | Dec 30 1899 10:51AM
07/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 07/24/2023 | Sample Chamber | 24.000000 | [5 empty] | Attached to this report |  | Septic Tank-3"sludge 2"scum/ Microfast ATU-0"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-229 ETM-8h 14m/ Pump2-221 ETM-7h 59m/ Peak-22/ High-23/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled | 109-15-0366 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | NA | [16 empty] | Inspected | Called due to intermitent alarm. Checked all all 6 floats are operational, cleaned pump clog around the pump inlet screen. Increased run time 0.1 min or 6 seconds. No recent alarm in history, date is corrupted- and system is running back in start up mode. found leak in return line in tank which is being scheduled for repair by owner. 1 in ball valve is needed to be replaced and return line has settled outside the tank causing a stress crack to develop inside the treatment unit below the exhisting ball valve.. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/30/2023 | 09:30 AM
12/06/2023 | Alternative | RoutineScheduled | 153-STS-20284 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank-3"sludge 0"scum/ No pump out needed at this time/ Repaired broken pump line pipe inside the tank/ Controls, pump, floats and alarms are now functioning properly/ Counts: Pump-2142 ETM-24h 46m/ High cnts-27/ Puraflo peat turned and in good condition at this time/ No breakout or spongy areas at the pad site and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/26/2023 | Alternative |  | 95-186-095 | Smyth | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/26/2023 |  | 7.570000 |  |  | 6.800000 |  |  | Will be sent separately |  | BOD: 7.57 TSS: 6.80 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/26/2023 | 12:00 AM
01/18/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | New Kent | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 3.000000 | 3000 | Multiflo FTB |  | Pump | Gravity | Trenches | Not Applicable | 1800.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service System A - Septic tank normal level - aeration tank - mixing present - compressor serviced - pump tank float sensors, pump and controls operating. System B - Septic tank normal level - aeration tank - mixing present - compressor serviced - pump tank float sensors, pump and controls operating. System C - Septic tank normal level - aeration tank - mixing present - compressor serviced - pump tank float sensors, pump and controls operating. Absorption fields all have areas of surfacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/19/2023 | 07:30 AM
03/08/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
10/23/2023 | Alternative | Pump-Out Only |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 9:30AM
09/13/2023 | Alternative | RoutineScheduled | 2001-143-0062 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Clearstream |  | Gravity | Gravity | Discharge | Chlorination |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Auxiliary Filter","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/13/2023 | 12:00 AM
10/23/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/23/2023 | Dec 30 1899 9:45AM
11/30/2023 | Alternative | RoutineScheduled | 196.03.581 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | checked peat, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/11/2023 | Alternative | Routine/Scheduled |  | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Pressure | Discharge | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Spray Dispersal Primary septic tank - normal level - effluent screen serviced. Processing Tank - Recirc - recirc pump, spray grid, media drapes serviced. Processing Tank - U.V. - bulb and housing serviced. Processing Tank - discharge - float sensors, pump and controls operating. Spray - 2 heads | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | Dec 30 1899 6:00AM
02/02/2023 | Alternative | RoutineScheduled | 166-06-098 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/28/2023 |  | RoutineScheduled | 2048-97-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | SBR |  | Pump | Gravity | Discharge | UV | 500.000000 | [] | [] | [19 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Tree that was next to the distribution boxes in the past has been cut down. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
02/07/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Gravity | Trenches |  |  | ["Attached Growth Medium","Septic Tank Baffles","Dispersal System Operation"] | ["Attached Growth Medium","Septic Tank Baffles","Dispersal System Operation"] | [18 empty] | Removed roots from dbox. Peat could stand to be topped off. Concrete lids deteriorating (recommend replacing with plastic lids) | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/07/2023 | 12:00 AM
11/17/2023 | Alternative | RoutineScheduled | 05-197-179 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Recirculation Pump","Effluent Screens","Level Sensor Operation","Dispersal System Operation","Control Operation","Auxiliary Filter","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 182-13-0067 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Blower panel alarm not functioning | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/13/2023 | 01:07 PM
12/14/2023 | Alternative | RoutineScheduled | 88-184-169 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | [29 empty] | Property is vacant and system is not in use. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/20/2023 | Alternative | RoutineScheduled | 154-16-0131 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 12:00 AM
05/10/2023 |  | Routine/Scheduled | 14-118-0034 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Flushed manifold. Cleaned filter. System appears to be operating normally. No overrides last 30 days. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Jan 1 1900 8:44AM
07/11/2023 | Alternative | RoutineScheduled | 125-STS-32067 | Nelson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Gravity | Discharge | UV | 450.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES |  |  | 7.200000 | 8.300000 |  |  |  | 07/11/2023 |  | 4.000000 |  | 2.000000 | 2.800000 |  |  | Will be sent separately |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 12:00 AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-87971 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. System barely out of alarm due to partially clogged pump intake and manifold, cleaned both and spoke to customer about garbage disposal usage (advised not to use it). Junction box for recirc was full of water, vacuumed water out and cleaned wires. system should go back to normal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/06/2023 |  | RoutineScheduled | 14-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/06/2023 | 12:00 AM
05/02/2023 |  |  | 133 06 0436 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [5 empty] | 05/03/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 01:30 PM
12/21/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2024 | 12:00 AM
08/07/2023 | Alternative | Reportable Incident Component Maintenance | 179-12-0236-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed on and off float in discharge side of rt unit, replaced both floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
09/19/2023 | Alternative | RoutineScheduled | 195-STS-27344 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/19/2023 | 12:00 AM
03/07/2023 |  | RoutineScheduled | 02-125-087 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 099-11-0042-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
12/20/2023 | Alternative | Routine/Scheduled | 1996-143-0262 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. No tee on inlet line. Outlet tee appears to be intact. No riser access. Not due for pump out Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Discharge pump has exceeded life expectancy. Discharge floats have exceeded life expectancy. Noted root infiltration along mid seam of tank. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Drip Field Condition of above Component Notes for above Component Flushed and cleaned disk filters. Checked and confirmed automatic headworks is functioning properly. Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 08:37 AM
02/22/2023 |  | Routine/Scheduled | 800-07-0096 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 11:15AM
03/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/21/2023 | 11:27 AM
02/09/2023 |  | Routine/Scheduled | 14-120-0280A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. PRimary septic tank - plastic and shows indications of deformation! - Effluent screen serviced. Processing Tank - recirc - recirc pump, media drapes & spray grid serviced. Processing tank - discharge - float sensors, pump and controls operating. Dbox - Intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | Jan 1 1900 7:00AM
06/26/2023 | Alternative | RoutineScheduled | 175-11-0227 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Other"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-10"sludge 2"scum/ .50 Microfast ATU-11"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time but may need pump out within the next 1-2 years/ Blower air filter cleaned and blower working correctly/ Controls, pump/ floats and alarms functioning properly/ Counts: Pump-002923 ETM-0019740/ Inlet riser of the septic tank is damaged allowing surface water infiltration and requires replacement/ No breakout or spongy areas on the drainfield. On 8/11/2023 Owner stated they have taken care of the riser issue. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/22/2023 | Alternative | Reportable Incident | 109-06-0117 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank Pumped | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Roots are blocking the gravity drain of the system from the D box and it will not flow. The control panel post is rotted at the ground. The system is operational but has severe blockage,. Contacted Foutz for an emergency pump out the next Day. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/30/2023 | 09:30 AM
05/13/2023 | Alternative | RoutineScheduled | 133 12 0238 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. 0" of solids in recirculation portion of treatment unit. 4" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 07:03 PM
08/30/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | JUST A NOTE NOT DEFIENCY need to keep bushes trimmed back were ecopod tank is. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
09/08/2023 | Alternative | Routine/Scheduled | 136-11-0294 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Pumped out the septic tank and pump the trash from the bottom of the Clearstream tank. The timer is set to 2 minutes every 3 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 10:30 AM
01/18/2023 |  | RoutineScheduled | 107-16-0279 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | NA | Musty | Clear | [15 empty] | House to panel wiring was shorted underground. Replaced shorted wiring. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/08/2023 | 12:00 AM
03/15/2023 |  | Routine/Scheduled | 234-16-111 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/15/2023 | Jan 1 1900 12:25PM
07/05/2023 | Alternative |  | SR-05-339 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled | 033-10-0022-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | checked sludge, cleaned filters, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic/atu tank needs pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/03/2023 |  | RoutineScheduled | {FIPSCode}-STS-1511 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | JEF Septic LLC | 1942001131 | Jason | Fulbright | 1.000000 | 500 | Norweco |  | Pump | Gravity | Pad | Not Applicable | 300.000000 | [] | [] | NA | Musty | Cloudy | 7.150000 | 3.250000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 10:00AM
10/13/2023 | Alternative | Follow-Up Component Maintenance | SD-13-115 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Gravity | Gravity |  | UV |  |  |  | NA | [9 empty] | 2.000000 |  | 2.000000 | 15.100000 |  |  | Will be sent separately | Inspected | SAMPLE RESULTS ONLY Dissolved Oxygen 9.36 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
02/21/2023 |  | Initial Visit | 18-120-0432A | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - Unknown service provider - FOIA filed for permit documents. Primary septic tank - normal level - leakage noted at riser interface. Aeration Tank - normal level - mixing present - compressor serviced. Salcor UV - discontinued - control head has failed - requires replacing. PUmp Tank - float sensors, pump and controls operating. DBox - intact - minor root infiltration removed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/22/2023 | Jan 1 1900 9:45AM
02/15/2023 | Alternative | Pump-Out Only | 12-160-0071 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | [8 empty] | [] | [] | [17 empty] | Pumped Out | - pumped/cleaned both tanks - installed/replaced Tuff-tite lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled | 2017-143-0169 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/16/2023 | Alternative | RoutineScheduled | 2004-143-0042 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Effluent Screens","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/24/2023 | Alternative | RoutineScheduled | 101-06-0369 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Old Dominion Engineering | 1942001085 | Michael | Craun | [9 empty] | ["None"] | [] |  | None | Clear | 5.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 10:15 AM
03/12/2023 |  | RoutineScheduled | SD-04-164 | Madison | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Puraflo | Gravity | Pressure | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/17/2023 | 08:30 AM
12/07/2023 | Alternative | Routine/Scheduled | 087-STS-6588 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/07/2023 | 03:03 PM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-90 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
12/12/2023 | Alternative | Routine/Scheduled | 085-STS-32915 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Checked and confirmed spray pattern is good Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 12:55PM
02/28/2023 |  | RoutineScheduled | 177-10-0054-ST | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend replacing the regenerative blower & the Tuf-Tite sample box lid. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/21/2023 |  | RoutineScheduled | 003-STS-32376 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/23/2023 | 12:00 AM
11/11/2023 | Alternative | RoutineScheduled | 2086-04-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.400000 |  |  | 1.600000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/13/2023 | 12:00 AM
10/06/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
06/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Pad | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | 12:00 AM
03/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | do not flush wipes into system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
08/02/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Routine Service Primary septic tank =- normal level - Recommend pumpout. Aeration tank - normal level - mixing present - compressor diaphragms found failed - rebuilt on property - returned to service. - recommend pumpout and refill 08/07/2023 - Pumped septic tank empty, pumped aeration tank empty and refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 07:30 AM
04/11/2023 | Alternative | RoutineScheduled | -STS-13566 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | King's Alternative Septic | 1942001094 | David | King | 2.000000 | 1000 | Delta DF 50 Whitewater |  | Pump | Gravity | Trenches | Not Applicable | 200.000000 | ["None"] | ["None"] | NA | [17 empty] | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/28/2023 | 12:00 AM
06/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [17 empty] | Septic Tank-4"sludge 12"scum/ Microfast ATU-2" sludge 0"scum/ Pump Tank-0"sludge 0"scum/ Pump out of the Septic-Microfast Tank required due to heavy scum layer/ Blower air filter cleaned and blower working correctly/ Replaced faulty off float during inspection/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-348 ETM-21h 12m/ Pump2-342 ETM-21h 7m/ Peak-7/ High-6/No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/07/2023 | Alternative | Initial Visit |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Va Septic LLC | 1942001734 | Richard | Morrison | 1.000000 | 1500 | FujiClean Cen7 |  | Gravity | Gravity | Trenches | UV |  | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 12:00 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | Dec 30 1899 11:24AM
04/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-89488 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Attached Growth Medium" ,"Recirculation Pump"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
10/27/2023 | Alternative | Follow-Up Component Maintenance | {FIPSCode}-STS-10379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed mid-seam joints on both sand filter tanks to prevent roots from growing into tanks. Resealed inlet/outlet pipes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
04/26/2023 |  | Routine/Scheduled | NYII-BCPSAX | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 1:55PM
12/28/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | UV |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replace (2) N98/115v effluent pumps, (4) control floats & contactor for control panel. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/13/2024 | Dec 30 1899 11:49AM
01/23/2023 |  | RoutineScheduled | 101-03-0581 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast |  | Gravity | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
07/28/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-91616 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
12/13/2023 | Alternative | RoutineScheduled | 041-STS-257936 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/13/2023 | Alternative | RoutineScheduled | VAG401203 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | NA | Musty | Clear | [15 empty] | no discharge during visit tablets in feeders | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
10/30/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Multiflo FTB |  | Pump | Gravity | Trenches |  | 450.000000 | Level Sensor Operation | Level Sensor Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/16/2023 | 12:11 PM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0218 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Septic | Cloudy | 7.100000 | 1.200000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 11/15/2023 | 02:02 PM
04/21/2023 | Alternative | RoutineScheduled | 137-STS-21806 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
07/03/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Orenco Advantex |  | Pump | Pressure | Drip |  | 600.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/07/2023 | 10:15 AM
11/22/2023 | Alternative | Follow-Up | 159-09-0024 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced blower due to failing bearing. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/06/2023 |  |  | 2006-143-0369 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Biomicrobics Microfast |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Auxiliary Filter","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 12:00 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/13/2023 | Alternative | RoutineScheduled | 108-18-0007 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The recirculating and discharge pumps were both pulled and cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 10:25 PM
01/06/2023 |  | RoutineScheduled | 132-06-0275 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
03/20/2023 |  | RoutineScheduled | SWP-04-205 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Pump is old but still pumping strongly. Will need to modify piping when it fails to make it more accessible. Lid for pump tank has some heavy cracks, but so far has stayed in one piece. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
06/21/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | follow up to determine infiltration | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
11/21/2023 | Alternative | Routine/Scheduled | 16-172-0413A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Not due for pump out. -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Checked and confirmed UV is functioning properly. Flushed and cleaned UV system. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly -Drip Field: Flushed and cleaned disk filter. Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | Dec 30 1899 3:48PM
06/20/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | UV Bulb replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/24/2023 | Alternative | Routine/Scheduled | 13-163-0023 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | Dec 30 1899 7:30AM
04/18/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | filter clog cleaned septic tank pumped | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
04/07/2023 |  | RoutineScheduled | 177-STS-87861 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 4.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment looks good. Hopefully this will be the case when business picks up next month. An employee had mentioned a few people complaining of septic odor near the bar downstairs. Recommended a pump-out of the grease trap and primary septic tank. Pumper to check lid gaskets and tees at that time. No odor smelled today and no external indications of clogging between the tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The header line appears to be nitrified and probed out slightly wet. Recommend uncovering distribution box and checking header line connections. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/12/2023 | Alternative | RoutineScheduled | 103-STS-99678 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 3.000000 |  | Biomicrobics MicroFAST | Whitewater ATU | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
10/20/2023 | Alternative | Pump-Out Only | 157-03-185 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Arrived at the septic tank pumped 1000 gallons lite solids extremely heavy sludge. No visible issues at this time. Service agreement had been done on the system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 01:29 PM
04/05/2023 |  | RoutineScheduled | 033-STS-91614 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Satellite cable was installed in the drainfield area. Currently there is no effluent coming to the ground surface. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Drip |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic system, 2 " Scum and 6-7" slduge in Septic tank, Pump tank 4-5" sludge, no scum. Alarm Test Good - Floats test Good - Pump count 558 vs 143 Peak count 33 vs 32, Pump time 39hr 4 min vs 18hr 19 min peak time same @27 min | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 05:30 PM
02/20/2023 |  | Routine/Scheduled | 08-163-0074 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped processing tank empty - serviced and refilled with fresh water for restart. Installed new access riser and plumbing in pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 8:00AM
10/18/2023 | Alternative | RoutineScheduled | 133-STS-96435 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced faulty uv ballast, system check - okay | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | ecopod and pump tank need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
04/25/2023 |  | RoutineScheduled | 2002-93-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  |  |  | NA | Musty | Clear | 7.900000 | 8.200000 |  |  |  | 04/25/2023 |  | 37.000000 |  |  | 7.000000 |  |  | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 05/15/2023 | 12:48 PM
04/25/2023 |  |  | 13-142-0100 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | CLearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
05/04/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 12:00 AM
02/08/2023 | Alternative | RoutineScheduled | 166-18-133 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Aquasafe |  | Pump | Pressure | Pad | UV |  | ["Auxiliary Filter","Other"] | ["Auxiliary Filter","Other"] | [18 empty] | UV light bulb replaced and Spin filter missing replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 12:00 AM
12/14/2023 | Alternative | RoutineScheduled | 09-113-236 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/14/2023 | 12:00 AM
05/09/2023 |  | Routine/Scheduled | 234-17-304 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [14 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | Jan 1 1900 9:00AM
03/28/2023 |  | RoutineScheduled |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 03/28/2023 | Sample Chamber | 51.000000 |  |  | 60.000000 | 88.000000 |  | Attached to this report |  | Septic Tank-8"sludge 4"scum/ Microfast-4"sludge/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarm functioning properly/ Counts: Pump1-14097 ETM-243h 33m/ Pump2-13976 ETM-241h 4m/ Peak-48/ High-55/ Pump/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/09/2023 |  | RoutineScheduled | 175-01-0280 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Advantex needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
01/26/2023 |  | RoutineScheduled | 04-192-109 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 8 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/26/2023 | 12:00 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend adding ball valves. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/14/2023 |  |  | 179-14-0307-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | EcoPod | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | 182-98-0112 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 12:00 AM
01/13/2023 |  | Routine/Scheduled | 07-137-0062 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss in fair condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 12:30PM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Strongly recommend pumping Norweco tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/20/2023 | Alternative | RoutineScheduled | VAG408135 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | Chlorination |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["Distribution Pump Operation","BlowerCompressorAerator Operation","Auxiliary Filter"] | [18 empty] | blower wire to be scheduled for repair | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled | 167-STS-17733 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Mound | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | 12:00 AM
08/28/2023 | Alternative | RoutineScheduled | 16-183-183 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/28/2023 | 12:00 AM
03/20/2023 |  | Routine/Scheduled | 234-13-334 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | Jan 1 1900 3:30PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Upper right lines might be receiving more effluent than the rest. Recommended to homeowner to contact DSS regarding the possibility of balancing and/or flushing the lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/03/2023 |  | Routine/Scheduled | 228-12-0024 | Virginia Beach | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV isn't working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/03/2023 | Jan 1 1900 10:15AM
04/13/2023 |  | RoutineScheduled | 09-192-011 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/13/2023 | 12:00 AM
07/12/2023 | Alternative | Pump-Out Only | 199-05-0124 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Chesapeake Bay Pump Out - pumpout of primary septic tank only as recommended from last service visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | Dec 30 1899 6:30AM
01/17/2023 | Alternative | Routine/Scheduled | 151-17-0042 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | 06:49 PM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/17/2023 |  | Routine/Scheduled | NYII-ATHN4M | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Jan 1 1900 1:10PM
01/30/2023 |  | RoutineScheduled | 14-183-038 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 12:00 AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/09/2023 | Alternative | RoutineScheduled | 14-142-0120 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | MicroFAST |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
07/14/2023 | Alternative | RoutineScheduled | SP-02-616 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-2 | 0-0 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 4.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 02:00 PM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:17 PM
07/14/2023 | Alternative | Routine/Scheduled | 136-05-0240 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - flooded - no indications of surfacing in absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 09:15 AM
01/10/2023 |  | Routine/Scheduled | 05-120-0050A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes bridging & clogged - recommend replacing - spray grid serviced. PUmp Tank - float sensors, pump and controls operating. DBox - not located. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2023 | Jan 1 1900 12:30PM
04/06/2023 |  | Routine/Scheduled |  | Chesterfield | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Discharge | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. U.V. - bulbs and housing serviced. Pump Tank - float sensors, pump and controls operating. Discharge point - free flowing, free of debris - signage present. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/10/2023 | Jan 1 1900 7:15AM
10/10/2023 | Alternative | RoutineScheduled | 085-STS-34464 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/27/2023 |  | RoutineScheduled | 179-12-0191-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-23024 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn |  |  | Whitewater ATU | Whitewater ATU | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation"] | NO | None | Clear | [5 empty] | 09/27/2023 | Pump Chamber | 9.000000 |  |  | 3.000000 | 18.000000 |  | Will be sent separately | Inspected | Surfacing Effluent Zone 1b buried line leaking repaired All other routine services complete MW 1 TN 2.5 MW 2 TN 2.4 MW 3 TN 3.6 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
12/04/2023 | Alternative | RoutineScheduled | 107-06-0716 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | 12:00 AM
02/02/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.550000 |  |  |  |  | 02/02/2023 |  | 2.000000 |  |  | 29.000000 |  |  |  |  | Advised client to have system pumped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:00 AM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Needs compressor replaced. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
07/12/2023 | Alternative | RoutineScheduled | 107-09-0308 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
04/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/17/2023 | 12:44 PM
10/26/2023 | Alternative | RoutineScheduled | 159-08-167 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 | Clearstream |  | Gravity | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/21/2023 | Alternative | Routine/Scheduled | 151-11-0116 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/21/2023 | 04:04 PM
07/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/06/2023 | Dec 30 1899 4:00PM
11/13/2023 | Alternative | Routine/Scheduled | 157-05-229 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 1" of solids with 4" of sludge Pulled and cleaned filter -Discharge/Pump Tank: Pump and floats functioning properly -Peat Moss: Tipping bucket and trays functioning properly Peat has some ponding but nothing major Raked out peat -Control Panel: Panel is functioning properly Visual and audible alarms working Discharge pump pulling 9.47amps -Distribution Box: Concrete dbox just below grade in the front yard Did not want to dig it up because of the new grass Dbox looked great during Kaines REI last year -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 08:44 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping treatment unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/22/2023 | Alternative | RoutineScheduled | SD-12-455 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 |  | septic |  | Pump | Pressure | Mound |  |  | [] | ["Control Operation","SludgeScum Accumulation"] | [18 empty] | 1" Of scum and 12" of sludge recommend pumping with in the year. Everything looks good and dry. Alarm is operational. 201h 5 min of run time 18279 doses | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:30 PM
11/09/2023 | Alternative |  | 07-197-A2 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/09/2023 |  | 9.520000 |  |  | 17.200000 |  |  | Will be sent separately |  | BOD: 9.52 TSS: 17.2 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 12:00 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend evaluation of the distribution boxes. Trees on neighboring lot could potentially cause damage to the system (Force main, Distribution Boxes, Headers, Lines). The septic tank is listed as a plastic tank but was replaced in 2014 with concrete tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. In the past 20 days, system has pumped an average of 1100.9 gals/day at 278.7 gals/dose (avg.) for a total of 22,019 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/29/2023 |  | Routine/Scheduled | 02-120-0826A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes are ponding heavy biomat - recommend replacing with new. DBox - deep bury - did not excavate. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | Jan 1 1900 7:45AM
09/08/2023 | Alternative | Routine/Scheduled | 16-174-0218 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/08/2023 | Dec 30 1899 8:43AM
07/19/2023 | Alternative | RoutineScheduled | 11-100-0140 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump | Pressure | Pad |  | 600.000000 | [] | [] | YES | [16 empty] | Pumped Out | TANK RECENTLY PUMPED. UV LIGHT UNIT REPLACED. EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 11:15 AM
01/03/2023 |  | RoutineScheduled | 05-100-0828 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 2.000000 | 1000 | Ecoflo |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | Everything working properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 11:00 AM
08/05/2023 | Alternative | Reportable Incident |  | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NO | [17 empty] | System alarming - found drip disc filter heavily clogged - last service conducted 6 months ago (February) - recommend service frequency be increased to a 6 month interval. Serviced drip disc filter / headworks - system may take as long as 48 hours to return to normal - recommend follow-up visit for Monday. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 11:00 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
07/26/2023 | Alternative | RoutineScheduled | 18-160-0132 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | Whitewater | [6 empty] | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [9 empty] | Sample Tap | [6 empty] | Will be sent separately | Inspected | - recommend pretreatment tank be pumped/cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/14/2023 | 12:00 AM
06/27/2023 | Alternative | Reportable Incident | 18-118-0054 | Charles City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 300.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | None | N/A | [17 empty] | Working on adjoining property - reportedly maintained by Stamie Lyttle Company. Compressor failed - no mixing present. Major wet area below absorption field with running water? Effluent? ... no odor, no indications of Nitrogen loading, no black discoloration - possible Spring? - unknown - Owner advised to contact the service provider for full evaluation. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/05/2023 | Dec 30 1899 7:00AM
02/15/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Distribution Pump Operation","Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | reset pump in pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20367 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
05/24/2023 |  | RoutineScheduled | 177-18-0217-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Pressure | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/28/2023 | 12:00 AM
06/30/2023 | Alternative | Routine/Scheduled | 234-15-419 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 10:59AM
04/26/2023 |  | Pump-Out Only |  | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 4.000000 | 9000 | None | None | Pump | Pressure | Trenches | Not Applicable | 4000.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped septic tanks for storage ... Site visit scheduled for Friday to discuss making full repairs to distribution system. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/27/2023 | Jan 1 1900 7:00AM
08/08/2023 | Alternative | RoutineScheduled | 13-184-004 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Presby |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 12:00 AM
01/24/2023 |  | Pump-Out Only | 2018-143-0037 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | SludgeScum Accumulation | SludgeScum Accumulation | YES | [16 empty] | Pumped Out | Septic tank pumped out and filter cleaned. Fixed air vent on Advantex AX20RT. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | 01:11 PM
11/10/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | Dec 30 1899 11:05AM
08/22/2023 | Alternative | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - System Commissioning / Start-up Trash Tank - filled while on property. Aeration Tank - filled with fresh water for start-up - compressor operating - mixing present. Pump Tank - float sensors, pump and controls operating. - drawdowns conducted - timed dosing adjusted. Drip Headworks - automatic - both zones operating. Drip Field - remote - confirmed that both zones obtaining effluent - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 07:15 AM
06/01/2023 | Alternative | Reportable Incident | 103-STS-102467 | Lancaster | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Three Rivers | Wayde P Adams T / A Complete Household M | 1942001076 | Wayde | Adams | 1.000000 | 1200 gal | 1 |  | Pump | Gravity | Pad | Not Applicable | 350.000000 | ["BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","None"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","None","Distribution Pump Operation","Recirculation Pump"] | NA | None | Clear | [14 empty] | Inspected | System has been reconnected and is working properly | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/06/2023 | 12:05 PM
01/30/2023 |  | Routine/Scheduled | 093-STS-14976 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 1000 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | Jan 1 1900 9:00AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Peat fiber is badly broken down and 3 of the pods are holding effluent. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
02/23/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Settling was observed in the sample chamber box. Need to dig up and reset inlet and outlet pipes of sample box before issue progresses any further. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/13/2024 | Dec 30 1899 5:34PM
11/20/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | Dec 30 1899 2:25PM
11/09/2023 | Alternative | RoutineScheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 750 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Effluent Screens","Level Sensor Operation","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation"] | YES | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | Dec 30 1899 11:00AM
07/20/2023 | Alternative | RoutineScheduled | 003-STS-30112 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 3.000000 |  | Aqua Safe |  | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | YES | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 05:20 PM
08/14/2023 | Alternative | Routine/Scheduled | 2018-143-0093 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/14/2023 | 09:49 AM
02/13/2023 |  | Follow-Up | 177-17-0061-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pumpout. Inspected tank and reassembled components in recirc tank. Tank was refilled back to proper levels with a water truck. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
12/08/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 11:10AM
04/25/2023 |  | RoutineScheduled | 179-16-0380-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | None | Clear | [5 empty] | 04/25/2023 |  | 22.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection.18 psi. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/10/2023 | 05:56 AM
09/20/2023 | Alternative | Reportable Incident | C 800-16-0181 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/20/2023 | Dec 30 1899 10:00AM
03/31/2023 |  |  | 2005-143-0242 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance | 033-07-0072-SR | Caroline | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We replaced a defective bottom float. We recommend scraping the Advantex sheets & pumping the tank afterwards. We also recommend that when the new drainfield is installed, that all pipes and risers on the Advantex tank be resealed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
07/31/2023 | Alternative | Initial Visit | 101-STS-95955 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 13.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1.5 minutes every 2 hours. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 02:30 PM
07/06/2023 | Alternative | Routine/Scheduled | 199-08-0048 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Routine Service. Pumped processing tank empty and serviced as recommended during last service visit. RSV, recirc pump and effluent screen serviced. Replaced float sensors in processing Tank Replaced float sensors in pump tank Refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 7:15AM
08/07/2023 | Alternative | RoutineScheduled | 13-100-0225 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1000 | Septic Tank | Delta Envir. DF | Gravity | Pressure | Pad | UV | 300.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 02:45 PM
03/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1250 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/27/2023 | Alternative | RoutineScheduled | 182-15-0182 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
01/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | NOT A DEFICIENCY JUST A NOTE yard is very wet | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/21/2023 | Alternative | Follow-Up | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 2.000000 | 4200 | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation"] | ["Dispersal System Operation" ,"Recirculation Pump"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 4-14-23 Advantage pumped 1 load 4200 gallons 4-17-23 PEC with FQHD, FQCO & VDH Engineers 4-20-2023 Steve with AQWA reduce run time in RT from 1.5 to 1.4 min increase rest time from 3.8 to 4 min. to help correct repeat low level alarms in RT. 4-21-23 Weekly check nom issues , dosing rates checked adjusted dosing cycles and turned 5 & 6 back off 4-21-23 Confirmed May 10th for soil field review with FQHD and VDH Areas not limed, SES and Southern states out of lime | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/02/2023 | 07:08 AM
03/30/2023 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Microfast blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
10/16/2023 | Alternative |  | 132-07-0050 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Hung | Cao | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 75.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 03:37 PM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
06/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 4"scum/ Microfast-4"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Blower controls and alarm functioning properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/18/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 10/18/2023 |  | 4.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | Dec 30 1899 1:00PM
10/30/2023 | Alternative | RoutineScheduled | 159-06-0359 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/24/2023 |  | RoutineScheduled | 11-183-190 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/24/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0438 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs new UV Unit. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/30/2023 | 10:30 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | Dec 30 1899 9:34AM
06/01/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1543 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Jan 1 1900 11:30AM
09/21/2023 | Alternative | RoutineScheduled | 027-STS-15545 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/21/2023 | 12:00 AM
11/03/2023 | Alternative | RoutineScheduled | 11-142-0070 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 2.000000 | 2500 | Norweco |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Auxiliary Filter","Effluent Screens"] | ["Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation","Auxiliary Filter","Effluent Screens"] | YES | Musty | Clear |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/21/2023 | Dec 30 1899 10:50PM
10/03/2023 | Alternative | Follow-Up Component Maintenance | 177-06-0533-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed inlet and outlet pipes on septic tank and pump tank. Installed 18? riser on septic tank wedge lid in order to waterproof and provide future access. Resealed septic tank and pump tank risers. Resealed pump tank wedge lid. Repaired leaking force main near tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
11/20/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/20/2023 | Dec 30 1899 11:00AM
10/02/2023 | Alternative | Routine/Scheduled | 087-STS-6617 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/02/2023 | 02:43 PM
08/14/2023 | Alternative | Routine/Scheduled | 13-120-0350A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Multiflo FTB |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Trash tank was pumped August 28, 2023 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/14/2023 | Dec 30 1899 2:00PM
08/08/2023 | Alternative | Routine/Scheduled | 05-118-0060 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/08/2023 | Dec 30 1899 1:42PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 047-16-250 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Recirculation Pump"] | ["Disinfection" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
10/19/2023 | Alternative | Routine/Scheduled | 13-120-0022A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/19/2023 | Dec 30 1899 11:07AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0781 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Whitewater ATU | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 10:33 AM
12/22/2023 | Alternative | Reportable Incident | 093-STS-14886 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream (it was stopped up). Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/22/2023 | Dec 30 1899 2:00PM
04/03/2023 |  | RoutineScheduled | 132-19-0076 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
11/27/2023 | Alternative |  | 177-06-0128-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/15/2023 | Alternative |  | 001-STS-92314 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | See Attachment | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
12/04/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | Dec 30 1899 1:00PM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-156 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Replaced failed cycle counter (locked up) in control panel. Peat moss still looks like new. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
01/16/2023 | Alternative | RoutineScheduled | 115-15-0020 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-2-4" scum layer and 8" Sludge in Septic tank. 6" Sludge trace in Recirc tank, 10" sludge trace on Discharge zone. System was pumped a year ago. Media looked and smelled normal, spray pattern was good, usual amount of growth. Cleaned eflfuent filter minimally dirty. All Floats switched tested good. Pumps both opperate. Septic tank sludge has a whiteish color duer to previous tennents using too much bleach or toilet chemcials, reccmoned to use minimal chemicals to future renters. Does not need pumping this year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 05:30 PM
03/08/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | lots of cleaners and soaps | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
01/18/2023 |  | RoutineScheduled | 133 17 0208 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Gravity | Gravity | Mound | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 12:00 AM
04/20/2023 |  | Reportable Incident | 179-STS-91652 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Pressure | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for wet spot in dripfield due to ARV getting hit. Appeared to be a lawn mower. Replaced ARV and irrigation box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
06/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/20/2023 | Alternative | RoutineScheduled | 07-113-164 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 - Blue Crystal tablets installed 4 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/20/2023 | 12:00 AM
07/19/2023 | Alternative | Routine/Scheduled | 234-08 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 9:55AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed. There was some nitrification down hill on the header lines. The box was uncovered and appeared to be functioning as designed. Recommended to contact the installer and monitor the area and advise of any changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/31/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3118 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | Jan 1 1900 2:45PM
08/07/2023 | Alternative | Routine/Scheduled | 800-12-0232 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 12:10PM
04/03/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 04/03/2023 |  | 4.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
10/06/2023 | Alternative | Initial Visit Component Maintenance | 033-08-0014-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump Tank was very milky. Builder told installer this was drywall dust and not paint. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
05/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lid on septic tank needs replaced broken. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Cleaned air pre-filter as a matter of preventative maintenance. Observed whine and bearing noise from blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
01/12/2023 |  | RoutineScheduled | 124-STS-2379 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton |  |  | Advantex AXRT |  | Pump | Pressure |  |  |  | [] | ["Attached Growth Medium","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","Auxiliary Filter"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2023 | 12:00 AM
08/14/2023 | Alternative | RoutineScheduled | 179-STS-91626 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 11883.000000 | [] | [] |  |  |  | 7.270000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:35 PM
11/08/2023 | Alternative | Reportable Incident | 800-07-0126 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Upon arrival, I found the control panel indicating recirculation in high level. Checked and confirmed recirculation pump is functioning properly. Checked media module and found that over 80% of the dispersal grid was clogged. I flushed and cleaned laterals and confirmed spray height is good. I noted signs that effluent screen was clogged. Flushed and cleaned effluent screen. Cleaned recirculation pump. Pumped system to normal level. Noted possible wet spot in yard that homeowner mentioned but unable to thoroughly evaluate due to lighting conditions. Informed homeowner we will follow up on the wet spot during routine service. Homeowner mentioned he moved into the house in '19 and does not have much knowledge of his septic system. I informed him about regulations requiring annual service and lab sampling every five years. System appeared to be functioning properly upon departure. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 1:21PM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/19/2023 |  | Reportable Incident | 2009-143-0135 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip | UV | 250.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | N/A | [17 empty] | System alarming. Blower was turned off and the pump tank effluent level was very high. The blower should never be turned off. The tanks most likely have leaks and they are located in a low area. The leaks in the tanks need to be sealed. Soil needs to be added above the tanks and then graded so water does not stand above the tanks. Down spouts need to be diverted away from the location of the tanks. The discharge pump can not keep up with the extra water from the apparent leaks. The next routine visit is scheduled for or around 11/01/2023 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/22/2023 | 08:10 AM
06/07/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0014-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted previously, large trees growing on the drainfield should be removed to prevent root intrusions in the drainfield lines. The tree growing between the modules 3 & 4 has been removed, but the modules are not level. Owner called with report of alarm. All floats, pump & controls are working properly. Alarm possible called by excess water usage. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
12/05/2023 | Alternative | RoutineScheduled | 085-STS-34420 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | EZ Treat |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
07/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Panel box is deteriorated, needs new filter, also peat moss needs replaced they have tree roots in the system. We recommended they contact engineer to upgrade system. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
03/29/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | old timer recommend upgrading | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
07/31/2023 | Alternative | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Pressure | Discharge | Chlorination |  | ["None"] | ["None"] | [18 empty] | Recirc contactor loud when activated. System working fine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/31/2023 | 12:00 AM
01/03/2023 |  |  | 04-125-163 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/03/2023 |  |  |  |  | 1.100000 |  |  | Will be sent separately |  | BOD: BDL TSS: 1.10 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/03/2023 | 12:00 AM
10/26/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1000 | anua (puraflo) |  | Pump | Gravity | Trenches | Not Applicable | 100.000000 | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | added a clean out for the purflo units drainline, replaced the junction box. fixed drain line coming into the sample chamber | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/14/2023 | 05:00 PM
09/13/2023 | Alternative | RoutineScheduled | 02-125-301 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 14 - Bio Max tablets installed 3 - Blue Crystal tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/13/2023 | 12:00 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-19-0014-VU | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
07/31/2023 | Alternative | Follow-Up |  | Frederick | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | NA | [17 empty] | Replaced air blower and fixed air release valves that were broken. System in working condition at this time | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 08/06/2023 | 04:30 PM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/22/2023 | Alternative |  |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Crater | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Pad | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Level Sensor Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/22/2023 | Dec 30 1899 1:00PM
08/31/2023 | Alternative | Pump-Out Only |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Aqua Klear |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped trash tank empty - serviced. Pumped aeration tank empty - serviced. Refilled aeration tank with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | Dec 30 1899 10:45AM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
05/25/2023 | Alternative | Initial Visit | 18-120-0582A | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - red light is on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the disc filter. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The aerator needs to be raised out of the dirt. The pipe has settled in between the tanks - needs to be addressed and/or fixed. The UV is burnt up - needs to be fixed and/or replaced and needs flex hose instead of rigid conduit. Replaced the alarm light bulb. Could not locate the vacuum breakers - need the septic plans/permit. The timer is set to 10 minutes every 2 hours. Did not take BOD or Fecal samples due to the UV not working. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/25/2023 | Dec 30 1899 4:00PM
11/07/2023 | Alternative | Routine/Scheduled | 041-STS-260161 | Colonial Heights | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | Dec 30 1899 9:30AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | Dec 30 1899 3:58AM
02/03/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 07:50 AM
04/11/2023 | Alternative | RoutineScheduled | 115-11-0079 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | [17 empty] | Inspected | Septic tank - Trace of scum and 4-5" slduge, Treatment unit - Recirc zone 6" sludge, Discharge zone 8" sludge -Effluent filter cleaned- Biofilter was clean, Alarm works Ran in test mode. flushed and brushed spary manifold - spray manifold-has good even spray pattern- media is clean. Checked Floats, all good and alarm operational. Ran system in test mode. All is functional. Recirc pump meter reading- 2117.9 Hrs vs 1731.4 Hrs last year- 55469 cycles vs 26917 Cycles last year. Gravity discharge- | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 09:30 AM
08/18/2023 | Alternative | RoutineScheduled |  | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/18/2023 | 12:00 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/16/2023 | Alternative | RoutineScheduled |  | Rappahannock | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | Puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 10:20 AM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and fuji tank need pumped out. Also the septic tank inlet riser and lid need replaced looks like mower hit it and broke it. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | Dec 30 1899 1:44PM
09/04/2023 | Alternative | Routine/Scheduled | 109-10-0400 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 2.000000 |  | Multiflo ATU |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/04/2023 | 08:30 AM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Replaced enabler float while on site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/07/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-4805 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 12:05PM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | Dec 30 1899 5:20PM
03/09/2023 |  | RoutineScheduled | 2006-143-0334 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/19/2023 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced compressor & raised complete unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
04/03/2023 |  | RoutineScheduled | 05-192-015 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation","Dispersal System Operation","Control Operation","Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 12:00 AM
11/24/2023 | Alternative | RoutineScheduled Component Maintenance | 154-11-0158 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90493 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation"] | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation"] | NA | Musty | Cloudy | [5 empty] | 06/20/2023 |  | 322.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken, 322 mg/L; failed. Found breaker tripped for recirc panel, customer said this happened after floats were replaced by installer. Reset breaker and system started working so treatment should improve. RECIRC: HL 9, LL 20, OVERRIDE 511. DISCHARGE: HL 21, PEAK 14. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
03/23/2023 | Alternative |  | 14-137-0106 | Goochland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1250 | 1250 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","SludgeScum Accumulation","Effluent Screens","Level Sensor Operation"] | YES | Septic | Dark Brown |  |  | 17.000000 | [13 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/23/2023 | Dec 30 1899 1:30PM
09/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  | 1500 |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 2:45PM
03/14/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | [] | ["SludgeScum Accumulation","Dispersal System Operation"] | NA | [16 empty] | Pumped Out | A new solenoid was installed in zone 1. Replaced clean out cap. and pump out septic and atu | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/15/2023 | Dec 30 1899 5:00PM
01/24/2023 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 03:24 PM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
12/19/2023 | Alternative | Routine/Scheduled | 136-05-0586 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal Level 3" of sludge and 2" of solids Pulled and cleaned filter. No signs of surfacing in drainfield Discharge/Pump Tank Condition of above Component Notes for above Component Normal level All floats and pump functioning properly However they are aged. Pump chamber is cracked in multiple spots. Pump pulling 7.57amps Junction box with electrical outlet used for pump connections Peat Moss Condition of above Component Notes for above Component Tipping bucket is broken and Peat moss is heavily root bound. Roots have over taken the whole Peat module | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/22/2023 | 08:12 AM
08/25/2023 | Alternative | Routine/Scheduled | 166-04-435 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Advanced Septic | [6 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 65.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 05:44 PM
05/18/2023 |  | RoutineScheduled | 179-17-0442-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Recirc tank needs pump out due to solids. Spongy area in Drip field needs to be investigated further to see what is causing it. Drip rate plus field flush rates have slow down since start up. Will send proposal to pump tank and to investigate drip field issue. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
03/14/2023 |  | RoutineScheduled | 033-STS-90182 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The Orenco lid on the Septic Tank is damaged and should be replaced. There is effluent entering your yard from your neighbor's yard. This is unsafe and in violation of Virginia Department of Health regulations. It is also causing your drainfield to be wetter than it should be. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/15/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/22/2023 | Alternative | Routine/Scheduled | 151-10-0077 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 04:53 PM
01/11/2023 |  | RoutineScheduled | 179-07-0213-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Level Sensor Operation" ,"Recirculation Pump" ,"SludgeScum Accumulation" ,"Septic Tank Baffles"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection and alarm. Pump tank had been pumped six months prior and pumped out a year and a half ago. Drip filter in head works keeps cloging and reducing drip rate causing system to go into high level. After speaking with the manufacturer we highly recomend homeowner get their well water tested as the pump tank should not have to be pumped out so frequently. Manufacturer stated well water is creating a bacteria growth from well water. Oustanding proposal to correct infiltration on both tanks and correct rsv piping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | 033-06-0031-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/02/2023 |  | Follow-Up | 087-STS-6181 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Aquaklear | [6 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | 12:00 AM
02/02/2023 |  | RoutineScheduled | 10-125-158 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/02/2023 | 12:00 AM
02/24/2023 |  | Routine/Scheduled | 147-14-0034 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/24/2023 | Jan 1 1900 3:18PM
03/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1125 | septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/07/2023 | Alternative | RoutineScheduled | 04-100-0598 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Ecoflo | Gravity | Pressure | Pad | Not Applicable | 600.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | 11:40 AM
03/27/2023 |  | Pump-Out Only | 2005-143-0326 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 12:00 AM
01/13/2023 |  | Routine/Scheduled | 234029814 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/13/2023 | Jan 1 1900 10:55AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | 033-18-0227-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
12/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/24/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 12:44 PM
10/20/2023 | Alternative | Routine/Scheduled | 151-18-0096 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 50.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 06:44 PM
11/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | Dec 30 1899 8:55AM
03/21/2023 |  |  | 06-142-0080 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
06/23/2023 | Alternative | Follow-Up Component Maintenance | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 2.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Report covers weeks 1 - 3 in June 6-1-23 Pumped 4,000 Randy Mathers 6-5-23 Lime affected areas, general site check, odor and color in plant improving 6-8-23 Pumped 4,000 gallons Randy Mathers 6-9-23 Significant improvement in odor and clarity of final wastewater Media is light brown again result of better air transfer and adjusted recirc rates 6-14-23 Quarterly monitoring well samples collected Lime affected areas 6-15-23 Pumped 4,000 gallons Randy Mathers Advantage 6-20-23 ROUTINE SITE VISIT Pumped 4,000 gallons Randy Advantage 6-22-23 Pumped 4,000 gallons f perez Collect quarterly lab samples limed wet areas | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/30/2023 | 12:47 PM
09/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 3:40PM
10/25/2023 | Alternative | Reportable Incident Component Maintenance | SP-03-387 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for alarm horn not working. Replaced alarm horn, adjusted floats in pump tank and retimed pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
02/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [7 empty] | 03/29/2023 | Sample Chamber | 67.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental CONST, SVC | 1942001123 | bill | tucker | 1.000000 | 1500 | FAST0.625 |  | Pump | Pressure | Drip | UV | 360.000000 | ["Disinfection"] | ["Disinfection"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | Dec 30 1899 9:00AM
05/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Advantex Recirc. Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank-3"sludge 0"scum/ Recirc. Tank-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Recirc. pump intake cleaned/ Controls, pumps, floats and alarms functioning properly/ Counts: Watermeter-0,054,396.2/ Pump-1318 ETM-176h 54m/ High-11 On-8m 24s Off-2h 55m/ Drip rates-3.9 gpm No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/28/2023 | Alternative |  | 124-STS-2379 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [29 empty] | located in Hanover County - MWEbb 8/25/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
08/28/2023 | Alternative | Pump-Out Only |  | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Supervised pumpout of processing tank by Ducks Septic Service. Owner denied refill and was going to monitor and fill tank himself. Control panel turned OFF to prevent low level alarms. Owner responsible to re-activate control panel breakers. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/31/2023 | Dec 30 1899 8:30AM
02/11/2023 |  |  | 2008-01-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination |  | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.400000 |  |  | 2.200000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/14/2023 | 12:00 AM
08/21/2023 | Alternative | RoutineScheduled | 06-172-0285A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | Advantex |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
07/07/2023 | Alternative |  | 033-08-0155-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
05/12/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1200 |  |  | Pump | Pressure | Trenches |  | 600.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 01:30 PM
07/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | Dec 30 1899 12:46PM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0365-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Both brackets for gas struts came off, they need to be glued on. Treatment is cloudy due to grease in system. Broken lid on inlet side of recirc tank (renter said his going to order asap). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
04/11/2023 | Alternative | RoutineScheduled | 115-05-0407 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | [17 empty] | Inspected | Sludge level- 1" Scum & 8-12" Sludge in Septic tank. Recirc Zone 4-6"Sludge, Discharge zone 4" Sludge, Cleaned Effluent filter. Media was ok, Ran in test mode to flush off the media. Good spray pattern. ALL Floats test operational- but 4th LED dimly lites and return a weel later to replace wirenuts and it corrected the isue. wirenuts were blackened possibly water shorted them out and one wire was burned up now it is working. Alarm functional and pumps operational. RTU 140402 - Ran in Test mode- Good Spray pattern - Recirc pump 1022 time and 75642 cycles, Discharge pump 76 and 2264 cycles. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/17/2023 | 09:30 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/26/2023 | Alternative | Reportable Incident | 127-STS-32805 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Came out for an alarm call on a fuji clean to drip. Found alarm float bad. Replaced float onsite for free. Looked through system and found that fuji risers are showing signs of leaking. Talked with Customer about options | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/11/2023 | Dec 30 1899 3:23PM
03/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | pump tank needs pumped out. Also homeowner needs to weed wack around tanks hard to access | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
04/13/2023 |  | Routine/Scheduled | 133 07 0115 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 09:40 AM
01/07/2023 |  | RoutineScheduled | 124-STS-2379 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - West Piedmont | dovel enterprises | 1934000191 | jerry | dovel | 4.000000 | 2000 | 2000 |  |  | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Septic | Cloudy | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | 12:00 AM
06/23/2023 | Alternative | Routine/Scheduled | 157-11-0095 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Aeration tank - normal level - replaced failed compressor. Pump Tank - float sensors, pump and controls operating. DBox - above normal level - heavy rains last few days. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | 01:00 PM
05/30/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Multiflo FTB | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:36 PM
05/23/2023 |  | RoutineScheduled | 2017-143-0078 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | Norweco |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/06/2023 | Alternative | Pump-Out Only | 234-13-388 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/15/2023 | Dec 30 1899 10:00AM
06/20/2023 | Alternative | Initial Visit | 830-STS-6307 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled | 051-STS-16169 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/11/2023 | 12:00 AM
03/02/2023 |  | RoutineScheduled | 175-03-0829 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
09/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | Septic Tank-6"sludge 2"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Interior Control Panel, pumps, floats and alarm is functioning properly/ No counts or etm on the control box/ No breakout or spongy areas on the LPD Drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/10/2023 |  | RoutineScheduled |  | Frederick | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NO | [18 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/13/2023 | 07:05 AM
11/16/2023 | Alternative | Routine/Scheduled | 166-06-030 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 2 in of sludge less than 1 in of solids Pulled and cleaned filter Riser is below grade allowing water to intrude through lid -Discharge/Pump Tank Pump chamber: Normal level Tested floats and pump all working as should All plumbing intact and pump moving water Pump down and analyzed for cracks or breaks Found no cracks but however the sidewalls have minor bowing No signs of infiltration -Peat Moss: Tipping bucket and dispersal trays intact Raked out peat moss grass roots intruding throughout peat No cracks or breaks in module -Control Panel Alarm box: Alarms can be heard from outside -Drain Field Inspection port: No signs of surfacing or standing water | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:51 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 2090-04-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 6.800000 | 4.700000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 10/16/2023 | 12:58 PM
02/10/2023 |  | RoutineScheduled | 181-04-0231 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | [17 empty] | The system did not need to be pumped. The blower and spin filters were both cleaned. The pump was pulled and cleaned. The controls were operating as designed. There were no visible leaks in the drip field. There was return effluent from the drip field so the drip field was operating as designed. The pressure was adjusted to the permitted pressure. The two valve box lids were broken so they were replaced with new lids. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/11/2023 | 01:10 PM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0204-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Spinner closer to recirc pump came apart, cleaned and put back. Recirc pump was not building any pressure due to union having a flow inducer, removed it and pump starting pumping very good. Water quality was not good due to spinners not working and pump pressure not being enough, both problems were solved so we will do a follow up in couple weeks to see how is doing. Added root x to distribution box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/08/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | septic | Advantex | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 1" Scum, 6" of sludge in septic tank, 0 scum and a little loose sludge in outlet side. All alarms, floats pump, operational. 468 pump cycle, 35h 25m pump run time. 33578 recirc pump cycles, 559h 4 min run time. Change the recirc run time to off for 7 min per Reed. Field is wet on the left side at the end. Needs to be checked for small leak or have some more fill added. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 11:50 AM
01/02/2023 |  | RoutineScheduled | 16-192-024 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2023 | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled | VAG401862 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.160000 |  |  | 2.200000 |  | 06/26/2023 |  | 8.000000 |  |  | 11.400000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/13/2023 | 01:15 PM
01/18/2023 |  | RoutineScheduled | 179-STS-91905 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
09/29/2023 | Alternative | RoutineScheduled | 06-142-0387 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/31/2023 |  | RoutineScheduled | SWP-05-145 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Low level alarm caused by clogged Biotube filters. Recommended riser repairs to be completed in the near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
02/13/2023 | Alternative | Reportable Incident | 128-06-136 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | Distribution Pump Operation | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Alarm Event - Pump failure Pumped tank(s) empty (septic tank and pump basin) - replaced failed discharge pump with new. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/14/2023 | 08:00 AM
03/10/2023 |  | Initial Visit | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Hott's Septic Service LLC | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
05/08/2023 |  |  | 2010-143-0106 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
02/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-07-0389 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
07/19/2023 | Alternative | Routine/Scheduled | 02-174-0213 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/19/2023 | Dec 30 1899 1:41PM
05/12/2023 |  | RoutineScheduled | 177-17-0184-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
04/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Found interior alarm not working. Replaced float. system is working as it should | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
07/12/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0113-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Distribution Pump Operation"] | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and Advantex Rt tank pumped by others in coordination with this inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
09/06/2023 | Alternative | RoutineScheduled | 103-STS-101771 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check okay, sludge check | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/25/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Norweco |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic tank zone 2-3" scum and 34" sludge - Contact Foutz To pump out- treatment zone 4-6" trace of sludge - 2 biofilters pulled and cleaned. Treatemt zone - has good aeration and alarm is functional in treatment chamber - Pump tank- was opened, trace sludge, Plumbing is rusty and owner may consdier replacement in an off season,Maple tree roots have been obsered and are growing close to tanks. reccomend to cut them out. Roots were gorwing onto the float switches which appear ok at this time. Drainfield in front yard appears dry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 08:30 PM
11/27/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.400000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 02:30 PM
09/18/2023 | Alternative | Reportable Incident | PPIE-AJFN8F | Suffolk | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001063 | K.R. Trapper | Davis | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Returned to property for evaluation of previous repairs - found fractured / disconnected plumbing for drip supply line - excavated, repaired. Flushed field at air release vacuum breakers until effluent ran clear. Flushed field to pump tank return until effluent ran clear. Recommend follow-up in two to three weeks. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 10/05/2023 | Dec 30 1899 11:00AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/28/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-3709 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/28/2023 | Dec 30 1899 8:00AM
10/25/2023 | Alternative |  | 05-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/09/2023 |  | RoutineScheduled | 175-10-0176 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [7 empty] | 03/09/2023 | Sample Chamber | 98.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Pump Tank-0"sludge / No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-5549 ETM-55h 23m/ Peat turned in all 5 modules and peat is in good condition/ No breakout or spongy areas on the Pad Site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/07/2023 | Alternative | RoutineScheduled | 06-100-0159 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | JEFulbright Septic, LLC | 1942001131 | Jason | Fulbright | 1.000000 | 1000 | EcoFlo |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | [] | [] | NA | Musty | Clear | 7.330000 | 3.000000 |  |  |  | 12/07/2023 | Pump Chamber | 7.000000 |  |  | 4.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | 03:20 PM
04/19/2023 | Alternative | RoutineScheduled | 165-STS-333424 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0232-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Pump tank needs to be pumped out due to sludge levels. Discharge is pumping just below the minimum rate if slows down any more it will needs to be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
09/25/2023 | Alternative | RoutineScheduled | 151-13-0152 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | sludge checked, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/14/2023 | Alternative | Follow-Up | {FIPSCode}-STS-17787 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination | [21 empty] | Tablets are now stocked | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Filter element for blower canister filter replaced and air pre-filter cleaned as preventative maintenance. Aeration heavier towards mechanical end of the tank. Will monitor for now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
11/02/2023 | Alternative | Pump-Out Only | 800-STS-14519 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | [6 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 10:00AM
03/29/2023 | Alternative | Reportable Incident | 157-15-0036 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced degraded distribution box with new 8 port Concrete DBox. Found Conveyance line damaged - replaced with new 4" PVC. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 06:45 AM
05/02/2023 |  | RoutineScheduled | 099-09-0039-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | NA | [7 empty] | 05/02/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Collected BOD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
12/06/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 | 1000 |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 12:00 AM
02/13/2023 |  | Follow-Up | 15-120-0187A | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | None | None | NO | Musty | Clear | [5 empty] | 02/13/2023 | Sample Tap | 129.000000 |  |  | 35.000000 |  |  |  |  | 5 year sampling event. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/21/2023 | Jan 1 1900 7:15AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/28/2023 |  |  | SP-05-342 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/18/2023 | Alternative | RoutineScheduled | SD-14-116 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/28/2023 |  | RoutineScheduled | 177-11-0128-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | As noted previously, we recommend adding a 6" riser onto the Fralo Monster Box so that it is above ground level. We also recommend adding topsoil to the drainfield lines where they have settled to prevent water from ponding on top of them. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
10/02/2023 | Alternative | RoutineScheduled | 09-184-5002 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/02/2023 | 12:00 AM
01/31/2023 |  | RoutineScheduled | 18-100-0018 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled | 087-STS-6421 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1000 | 750 | 250 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles"] | YES | Pungent | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 12:00 AM
03/22/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity | Pad | Chlorination |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
12/22/2023 | Alternative | RoutineScheduled | 09-184-5003 | Scott | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | EHD - Lenowisco | Scott County Health Department | 1940001589 | Nathaniel | Rasnake |  |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None |  | 7.500000 | 0.000000 |  | 0.000000 | [11 empty] | Both chlorination and dechlorination tablets were present in their respective ports. The aerator appeared to be running at the time of the inspection. The discharge point was GPS'd. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/22/2023 | 12:00 AM
11/15/2023 | Alternative | RoutineScheduled | 169-STS-27621 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/15/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Annual Maintenance, pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/30/2023 | Alternative | RoutineScheduled | 191-STS-36019 | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 4 Chlorine 5 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/30/2023 | 12:00 AM
04/20/2023 |  | RoutineScheduled | -STS-92146 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
06/26/2023 | Alternative | Routine/Scheduled | 2010-143-0141 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/26/2023 | 03:35 PM
08/28/2023 | Alternative | RoutineScheduled | 03-125-082 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | FAST |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 - Blue Crystal tablets installed 6 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/28/2023 | 12:00 AM
03/21/2023 |  | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"SludgeScum Accumulation"] | ["SludgeScum Accumulation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Installed inlet riser and pumped primary tank Installed proper filter assembly with filter Land owner to cover small sections around tree root with dirt on top of drip tubing | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
01/10/2023 |  |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/02/2023 | Alternative | Routine/Scheduled | 166-11-093 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 05:10 PM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance | 179-18-0327-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
06/09/2023 | Alternative | Routine/Scheduled | 151-09-0161 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss in good condition - minor roots present - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 07:00 AM
12/11/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-337255 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
08/24/2023 | Alternative | RoutineScheduled | 03-197-034 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation","Level Sensor Operation","Dispersal System Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 12:00 AM
03/16/2023 |  | Initial Visit | 136-94-0422 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Sandfilter, High rate |  | Pump | Pressure | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - initial visit - new property owner. Primary septic tank - recommend pumpout. Sandfilter Dosing station - float sensors, pump and controls operating. Sandfilter - sand compacted below spray grid - debris present. Pump Station - float sensors, pump and controls operating. LPP field - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 07:45 AM
12/15/2023 | Alternative | Reportable Incident | S 093-19-0058 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Found panel in alarm Opened system and found septic at normal Level, recirc was above normal level, and discharge was at normal level Checked pump screen and it was free of debris. All floats were functioning properly. Noted that the high level alarm. Float was set at the same level was the recirculation pipe. I adjusted the alarm float. I also knocked the check ball for recirculation pipe out and removed from pipe per manufacturer recommendations Level dropped 4" while on site | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 10:14AM
05/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Loudoun Water | 1942001649 | Dakota | Lee | 6.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NO | Musty | Clear | 6.800000 | [12 empty] | Will be sent separately | Inspected | Yearly Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/06/2023 | 05:00 AM
12/18/2023 | Alternative | Reportable Incident | 136-16-0059 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Customer stated panel was in alarm System above normal level Tested and confirmed pump and floats were functioning properly. Performed a draw down. And pump is moving water. System is a clearstream time dosed system and there are signs of leaks in pump tank riser. Also noted the forcemain is leaking below grade Gave customers wife estimates. And then emailed to customer. Need to speak with customer for approval | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | 02:23 PM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/08/2023 | Alternative | Reportable Incident | 159-13-020 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | -Came out for an alarm call on a Clearstream. Found panel in alarm and system flooded. Found proper voltage to the panel. Tested timer and timer works like it should system began to pump itself down. Set timer to cut on every ten seconds for 30seconds. While that was going I dye tested the toilets and found that the toilets do not seem to be leaking at this moment in time. The system was functioning the entire time I was on site | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 09:35 AM
03/15/2023 |  | Follow-Up | {FIPSCode}-STS-1787 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 3.000000 | 3000 | Clearstream |  | Pump | Gravity | Discharge | UV | 900.000000 | None |  | N/A | Musty | Clear | [5 empty] | 03/15/2023 | Sample Chamber | [8 empty] | Sampling following repairs. Samples for BOD5, TSS, E-Coliform and TN obtained and transported to Universal Laboratories, Hampton. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | Jan 1 1900 8:35AM
03/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/16/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable | 175.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | 01:00 PM
02/21/2023 |  | Pump-Out Only | 228-15-0296 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 10:30AM
03/15/2023 | Alternative | RoutineScheduled | 159-11-161 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
10/14/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Delta Whitewater DF Series |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Annual inspection. 8" of accumulated solids in septic tank. 8" of solids in treatment unit, no solids crust. Adequate aeration. Cleaned blower air filter. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | 07:03 PM
10/25/2023 | Alternative |  | 18-100-0472 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
08/22/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-1192 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | Unable to check control. Customer was not home. 4 - Blue Crystal tablets installed 14 - Bio Max Tablets installed 1 - Feeder Tube | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/22/2023 | 12:00 AM
02/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
11/07/2023 | Alternative |  | 033-10-0079-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/09/2023 |  | RoutineScheduled | 03-197-A16 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/09/2023 | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0324 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
03/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | Dec 30 1899 12:35PM
12/21/2023 | Alternative | RoutineScheduled Component Maintenance | 107-07-0563 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Ecoflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced peat in media filter and pumped primary tank Recommend to clear area around drainfield and keep free from overgrowth | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
01/05/2023 |  | RoutineScheduled | 177-STS-90136 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | NA | None | Clear | [5 empty] | 01/05/2023 |  | 11.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
03/01/2023 | Alternative | RoutineScheduled | 154-13-0152 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/14/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.430000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 11:15 AM
06/26/2023 | Alternative | RoutineScheduled | 181-18-0109 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The recirculating and discharge pumps were both pulled and sprayed off. The spin filter was cleaned. The controls were operating as designed. There was return effluent returning to the treatment unit so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 09:15 PM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/23/2023 | Alternative | RoutineScheduled | SD-13-55 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | Pura-flo |  |  | Trenches | Not Applicable | 67.000000 | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 09:00 AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. AP 80 Compressor is bad and needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/29/2023 | 12:05 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/02/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | Modified Extended Aeration |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Total flow to drain fields November 2023 - 97,830 gallons. Average 3,494 gallons per day. All aspects of the system are operational. Wasting of settled mixed liquor from the clarifier to the digester and decanting of supernatant from digester are occurring regularly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 07:03 PM
08/01/2023 | Alternative | Initial Visit |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Control Operation"] | ["Control Operation"] | NA | [17 empty] | Initial start-up inspection visit. Set floats according to service memorandum per this unit's serial number. Not enough water to set recirculation pump rate or test pumps. Advised homeowner to use water so that water levels come up. Returned 8-19-2023 to set recirculation pump rate. Tested floats, pumps and alarm. Verified proper installation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 07:03 PM
04/11/2023 | Alternative | Follow-Up | 061-17-542 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Reattached Advantex lid with stainless steel bolts. Installed prop rod kit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
03/29/2023 |  | RoutineScheduled | 175-19-0029 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [5 empty] | 03/29/2023 | Pump Chamber | [6 empty] | Will be sent separately | Inspected | Annual inspection. Effluent sample collected for BOD test. Very minor regrowth seen attached to Microfast media (possibly filamentous). Talked to owner about discontinuing use of scent beads and liquid fabric softeners, and limiting use of antibacterial soap to just one sink. Redundant "off" float was slow to open. Red led for atu alarm was dim. Will recheck all of these items next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
03/13/2023 |  | Routine/Scheduled | 11-120-0347A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/13/2023 | Jan 1 1900 12:52PM
01/23/2023 | Alternative | Routine/Scheduled | 166-10-247 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 06:51 PM
10/31/2023 | Alternative | Routine/Scheduled | 2016-143-0010 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact and. Flushed and cleaned effluent screen. Due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Checked and confirmed recirculation floats are functioning properly. Riser lid is damaged. Due for pump out. Refill is required for proper operation and to prevent damage to components. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and found timer enable float had failed. Upgraded discharge floats while on site. Checked and confirmed discharge floats are functioning properly. -Media Sheets: Flushed and cleaned laterals. Cleaned media. -Control Panel: Checked and confirmed components within control panels are functioning properly. Checked and confirmed audible alarms are functioning properly. Checked and confirmed visual alarms are functioning properly. -Distribution Box: Water level normal normal. Structural integrity of distribution box appears to be intact -Drain Field: Found no signs of surfacing on dispersal field Replaced floats onsite | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 09:29 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-12-0046 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
02/13/2023 | Alternative | RoutineScheduled | 16-177-1036 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 8" of accumulated solids in septic tank. Cleaned septic tank filter. 3" of solids in recirculation portion of treatment unit. 1" of solids in discharge portion of treatment unit. Cleaned recirculation pump intake screen. Flushed treatment unit spray manifold. tested floats, pumps and alarm. Treatment unit fabric sheets have good color. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 07:03 PM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
03/13/2023 |  | Routine/Scheduled | 08-120-0515A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/13/2023 | Jan 1 1900 11:20AM
03/27/2023 | Alternative |  | 003-STS-33405 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  |  | Ivy Road, LLC | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/28/2023 | Alternative |  | 033-06-0272-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
04/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
04/24/2023 |  | RoutineScheduled | 177-STS-89028 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media starting to clogged due to grease. Blower 3.05. Customer contacted pumper to get system pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 11/27/2023 |  | 4.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0292-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted previously, there are roots growing into the Aerobic Treatment Unit and Pump Tank. We continue to strongly recommend eliminating the source of the roots. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
12/20/2023 | Alternative |  | {FIPSCode}-STS-18653 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 4.000000 |  | Septic Tank to Norweco ATU | EZ-Treat to Discharge Pump Tank | Pump | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | [18 empty] | Septic Tank-4"sludge 3"scum/ Norweco ATU-4"sludge 0"scum/ EZ-Treat Recirculation Tank-3"sludge 0"scum/ Discharge Pump Tank- 2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower is working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Discharge pump-23431 ETM-105731/ Jet UV-Light sleeve cleaned and light is functioning properly/ EZ-Treat panel in alarm during inspection, per owner tank may have leak during rain events/ May need visit during rain event to determine issue/ Discharge point is open. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/18/2023 | Alternative | Reportable Incident Component Maintenance | 179-06-0016-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to a clogged and crucshed dripo filter in the headworks not allowing system to process water. Replaced filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] |  | NA | [15 empty] | Will be sent separately | Inspected | System needs completely pumped out due to over usage. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/20/2023 | 02:30 PM
02/23/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Hydraulic unit lid was hit by landscape company and replaced by them. After they repaired they filled the hydraulic unit full of dirt. At this time the hydraulic unit is unserviceable and dirt needs removed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/13/2024 | Dec 30 1899 11:49AM
07/18/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 |  | Puraflo Trench |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 12:00 AM
04/03/2023 | Alternative | RoutineScheduled | 139-18-0035 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Aquasafe |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | 10:30 AM
12/19/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Cloudy | 7.600000 |  |  |  |  | 12/19/2023 |  | 21.000000 |  |  | 34.400000 |  |  |  |  | TSS was over the regulatory limit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 04:00 PM
11/02/2023 | Alternative | Routine/Scheduled | 093-17-0112 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Outlet tee appears to be intact. Not due for pump out. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. -Aeration: Water level below normal due to recent pump out. Inlet tee appears to be intact. -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. -Control Panel: Checked and confirmed components within control panels are functioning properly. Checked and confirmed audible alarms are functioning properly. Checked and confirmed visual alarms are functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | Dec 30 1899 11:30AM
05/11/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Gravity | Gravity | Discharge | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | 12:00 AM
08/12/2023 | Alternative | RoutineScheduled | 109-17-0203 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 13" of accumulated solids in septic tank. Cleaned septic tank solids filter. 16" of solids in recirculation portion of treatment unit. 12" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Cleared floating solids from recirculation pump area. Tested floats, pumps and alarm. A pump out may need to occur next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 07:03 PM
11/17/2023 | Alternative | RoutineScheduled | 13-197-048 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/17/2023 | 12:00 AM
06/14/2023 | Alternative | RoutineScheduled |  | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 1.000000 |  | EcoPod |  | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] |  | Musty | Clear |  |  | 14.000000 | [12 empty] | EcoPod trash compartment less than 1" fog, 5" sludge. Treatment unit 14% SS. Serviced compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/23/2023 | 07:35 PM
04/20/2023 |  | RoutineScheduled | 95-113-169 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 5 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/20/2023 | 12:00 AM
11/01/2023 | Alternative | Routine/Scheduled | 15-163-0057 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact and. Outlet tee appears to be intact. Not due for pump out -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly -Aeration: Water level normal. Flushed and cleaned biofilter assembly. -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Cleaned aerator shaft. -Control Panel: Checked and confirmed components within control panels are functioning properly. Checked and confirmed audible alarms are functioning properly. Checked and confirmed visual alarms are functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | Dec 30 1899 10:24AM
08/10/2023 | Alternative | Routine/Scheduled | 2019-126-079 (OSEW&S) | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/10/2023 | Dec 30 1899 10:25AM
03/23/2023 |  | Routine/Scheduled | 99-120-0448A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/23/2023 | Jan 1 1900 5:08PM
01/26/2023 |  | Routine/Scheduled | 800-05-0303 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 11:21AM
09/01/2023 | Alternative | Routine/Scheduled | 228-10-0460 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [12 empty] | Pumped Out | Replaced pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | Dec 30 1899 7:30AM
02/16/2023 |  | Pump-Out Only | {FIPSCode}-STS-3406 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | Jan 1 1900 9:30AM
06/08/2023 | Alternative | Reportable Incident |  | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced failing DBox with new 8 port concrete DBox Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 1:00PM
05/09/2023 |  | RoutineScheduled | 175-08-0349 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | Service call only: Replaced faulty Hydromatic pump with a Zoeller N-262 (115 Volts) Tested and now working properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Just a note NOT a defiency force main in pt was broken and fuse was blown on air blower. Both items were fixed and septic system is in working condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/12/2023 | Alternative | Routine/Scheduled | 800-03-0371 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge pump plumbing has exceeded life expectancy. Discharge floats are not properly secured. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. Media has exceeded life expectancy. Media lid safety support struts have failed -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | Dec 30 1899 2:48PM
09/01/2023 | Alternative | Routine/Scheduled | 550-STS-6377 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | Dec 30 1899 12:05PM
01/12/2023 |  | RoutineScheduled | 177-14-0294-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
09/21/2023 | Alternative | RoutineScheduled | 18-100-0389 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1500 | Septic Tank | Purasys SBR Model PS1-6 in 2nd | Gravity | Pressure | Trenches | Not Applicable | 600.000000 | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | 12:15 PM
11/01/2023 | Alternative | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Tanks pumped. Jumbo lid replaced. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/07/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled | 108-06-0014 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2500 | Septic Tank Only | MicroFast | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | [17 empty] | The system did not need to be pumped. The blower and spin filters were both pulled and cleaned. The discharge pump was pulled and sprayed off. The controls were operating as designed. There was effluent returning to the pump tank from the drip field so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | 07:55 PM
07/01/2023 | Alternative | RoutineScheduled | 109-04-0060 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | PuraFlo |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 6" of accumulated solids in septic tank. Cleaned septic tank solids filter. 3" of solids in pump chamber. Raked peat that had matted and settled from last year in all four treatment pods. The condition of the peat is good. Tested pump and alarm. excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 07:03 PM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 177-13-0048-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Control Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
04/11/2023 |  | Routine/Scheduled |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - recirc pump, media drapes & spray grid serviced. U.V. - bulb and housing serviced. Processing Tank - discharge - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 6:45AM
02/10/2023 |  | Pump-Out Only | {FIPSCode}-STS-1841 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | Jan 1 1900 11:30AM
03/04/2023 |  | RoutineScheduled | 2060-98-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 6.200000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
08/24/2023 | Alternative | RoutineScheduled | 10-120-0213A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 500 | Norweco Singulair |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens","Level Sensor Operation","Dispersal System Operation","Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [6 empty] | 1/2" sludge, 1/2" crust accummulation in tank | [9 empty] | Inspected | Recommend pumping in 2-3 years | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | Dec 30 1899 1:00PM
09/28/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | Dec 30 1899 10:30AM
10/09/2023 | Alternative | Routine/Scheduled | 157-06-0027 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The pressure switch on the aerator is not hooked up. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 04:30 PM
05/10/2023 |  | RoutineScheduled | 015-STS-336567 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Cloudy | 7.810000 | 7.050000 |  |  |  | 05/10/2023 |  | 2.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 07:03 PM
01/03/2023 |  | RoutineScheduled |  | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 01/03/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal Replaced blower panel | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
12/08/2023 | Alternative | RoutineScheduled |  | Rappahannock | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | EZ Treat |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump","Dispersal System Operation"] | NA | Septic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | 08:00 AM
11/09/2023 | Alternative | Routine/Scheduled | 151-12-0010 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Ecoflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 06:05 PM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
09/15/2023 | Alternative | Routine/Scheduled | 03-160-0528 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable |  | None | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 03:15 PM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
10/09/2023 | Alternative | Initial Visit | 163-STS-339544 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | Advantex AX20RT |  | Gravity | Pressure | Drip | Not Applicable |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Attached Growth Medium"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/29/2023 | 09:00 PM
03/06/2023 | Alternative | RoutineScheduled | 154-13-0121 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
11/02/2023 | Alternative | Routine/Scheduled | 800-11-0073 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 9:30AM
07/01/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Annual Inspection for 2023-nothing to report | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/01/2023 | 12:00 AM
12/14/2023 | Alternative |  | 107-08-0069 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Trenches | Not Applicable |  | ["Septic Tank Baffles","Attached Growth Medium"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 12:00 AM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-107 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots taking over peat, fluffed peat and added 1 can of root destroyer in each pod. Media starting to show its age, evaluate next year for replacement. Septic tank has a lot of wipes and grease, will need pumping next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping Microfast due to recent back up. There appears to be broken tubing underground. Lower zone appears to show signs of surfacing effluent. homeowner has contacted someone for repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/09/2023 | Alternative | RoutineScheduled | 17-160-0139 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Aquasafe | [6 empty] | [] | [] | [18 empty] | - pumped/cleaned pump chamber, pump chamber overflowing, pumped approx 1800gal - Advanced Environmental completing repairs | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/12/2023 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Micro fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/15/2023 | Alternative | Pump-Out Only | 157-13-0054 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Pad | Not Applicable | 450.000000 | SludgeScum Accumulation | SludgeScum Accumulation | [17 empty] | Pumped Out | Eljen inground synthetic sand filter. Pumpout of Pump Tank Only Pumped tank empty - removed accumulated sludge - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 09:00 AM
04/25/2023 |  |  | 08-113-080 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/25/2023 |  | 4.750000 |  |  | 3.730000 |  |  | Will be sent separately |  | BOD: 4.75 TSS: 3.73 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 12:00 AM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Best one tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/10/2023 | Alternative | Routine/Scheduled | 151-12-0167 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level, 3in of sludge and less than 1in of solids. Pulled and cleaned filter. -Discharge/Pump Tank: Found at normal level, tested floats and pump all working as they should. LB being used as a jbox. There is a splice on pump cord. -Peat Moss: Tipping bucket and trays are in working order. Raked out peat on both sides. Peat is broken down and compacted. Peat change recommended -Control Panel: 120 volts, audio and visual alarms working as they should. Pump pulled 7.4 amps. -Drain Field: No signs of surfacing. Unable to locate dbox due to depth | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 02:39 PM
03/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
04/28/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | garden on field new valve box lid and septic tank lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/21/2023 | 03:35 PM
02/19/2023 |  | Routine/Scheduled | 041-STS-259802 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/19/2023 | Jan 1 1900 11:00AM
11/20/2023 | Alternative |  | {FIPSCode}-STS-9358 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/20/2023 |  | 8.970000 |  |  | 6.600000 |  |  | Will be sent separately |  | BOD: 8.97 TSS: 6.60 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/20/2023 | 12:00 AM
07/26/2023 | Alternative |  | 08-197-A4 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 |  | 2.120000 |  |  | 2.000000 |  |  | Will be sent separately |  | BOD: 2.12 TSS: 2.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/02/2023 | Alternative | RoutineScheduled | 12-100-0136 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Gravity | Pad | UV | 450.000000 | [] | [] | NA | [17 empty] | SLUDGE JUDGE REVEALED 3-4" FROM BOTTOM, 2-3" FROM TOP FOR SEPTIC TANK SLUDGE JUDGE REVEALED < 1/3 SOLIDS IN AQUASAFE REPLACED FLOAT FOR PUMP STATION EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 02:40 PM
08/22/2023 | Alternative | Reportable Incident |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | 08/22/2023 - septic tank pumped for biofilter changeout. 08/24/2023 - removed spent peatmoss biofilter - replaced with new. Upgraded effluent screen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 06:15 AM
05/25/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 | 1500 | Saeptic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 48" liquid depth, 12" of sludge & minimal scum. Pump Tank is clean. Alarm, floats and pump are operational. Field is good and dry. Peat moss looks good with good flow. Raked out peat and cleaned filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 10:30 AM
01/31/2023 |  | RoutineScheduled | 179-13-0333-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
09/12/2023 | Alternative | Reportable Incident | 157-14-0134 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the septic tank. Installed an aerator rebuild kit. Changed the filter in the aerator. The septic tank needs to be pumped out and the Clearstream should be pumped out. The drainfield has a little wetness - once it dries need to keep an eye on it. The timer is set to 4 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/12/2023 | 04:45 PM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/03/2023 | Alternative | Routine/Scheduled | S 800-13-0190 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [16 empty] | Replaced aerator and diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | Dec 30 1899 5:30PM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/20/2023 |  | RoutineScheduled | 2073-05-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | 6.700000 |  |  | 1.700000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/22/2023 | 12:00 AM
12/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 10:35AM
01/27/2023 | Alternative | Routine/Scheduled | 166-03-172 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Ecoflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | 05:37 PM
11/07/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 12:00 AM
09/06/2023 | Alternative | RoutineScheduled | 185-STS-15925 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/06/2023 | 12:00 AM
05/03/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/27/2023 | Alternative | RoutineScheduled | VAG408298 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST |  | Gravity | Gravity | Discharge | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | None | [16 empty] | Not discharging at time of inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/12/2023 | 09:35 AM
12/22/2023 | Alternative | RoutineScheduled | 001-STS-92180 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | PURASYS |  | Pump | Gravity | Trenches | Not Applicable | 300.000000 | [] | [] | NA | [17 empty] | SLUDGE JUDGE OF SEPTIC TANK REVEALED <1" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/15/2024 | 11:25 AM
10/07/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | EZ Treat |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Second quarter 2023 inspection. Cleaned recirculation tank filter. Tested floats, pumps and alarm. Spray heads spraying very good. Restaurant is on a regular grease trap pump out schedule. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 07:03 PM
10/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0108-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Attached Growth Medium"] | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. treatment crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
12/12/2023 | Alternative | RoutineScheduled | 150-04-126 157-04-238 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | peat- okay, sludge checked, cleaned filters, system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/10/2023 | Alternative | Follow-Up | SD-12-439 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Removed top riser on septic tank to reseal it and discovered that no sealant had been used and only 4 screws to attach it. Installed new riser supplied by the owner (old riser had a fairly large chunk out of it). Original Microfast alarm panel would not alarm, and both led's were burnt out - installed new panel. Blower had quit running, replaced it and cleaned the air filter. Blower box had settled and deformed the pvc elbow. Supported the box with gravel and a cement block, and replaced the elbow. Septic odor should dissipate in a day or two. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
01/31/2023 |  | RoutineScheduled | 177-STS-89975 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. RECIRC: HL 3, LL 16, OVERRIDE 3953. DISCHARGE: HL 7, ETM 0M. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | -STS-93453 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank due to scum and sludge accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
09/27/2023 | Alternative | RoutineScheduled | 151-17-0087 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | 12:00 AM
08/05/2023 | Alternative | RoutineScheduled | 109-12-0345 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank filter. Flushed treatment unit spray manifold. 10" of solids in recirculation portion of treatment unit. 18" of solids in the discharge portion of treatment unit. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 07:03 PM
02/22/2023 |  | RoutineScheduled | SP-05-401 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1500 | 1-8 0-0 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 16.000000 | [11 empty] | Inspected | replaced 2 floats in recirc tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | 12:00 PM
12/08/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV ballast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 10:00AM
03/30/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | uv light bulb burnt out needs replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
02/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
09/07/2023 | Alternative | Routine/Scheduled | 800-STS-13820 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Using too much water - pump running on timer override. The drainfield has visible wetness / is bleeding out - needs to be addressed and/or fixed. The timer is set to 3 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/07/2023 | Dec 30 1899 11:00AM
11/02/2023 | Alternative | Routine/Scheduled | 166-15-172 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 05:28 PM
09/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 11:20AM
09/01/2023 | Alternative | RoutineScheduled Component Maintenance | -STS-93454 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Clear treatment. Couple candy wrappers in septic tank, spoke to customer about Do's and don'ts. Blower 2.92 amps. Cleaned air filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
12/26/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88638 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We have several recommendations that we recommend you share with your builder to see if the installer will help with any or all of them. Most importantly, both bottom floats are defective and stuck in the up position. The installer should be able to replace them under warranty. We also recommend raising the vent pipe on the ATU and installing a vent top. Additionally, both air release valves are approximately 24 inches above ground. These should be lowered and placed in air release valve housings. Finally, we recommend the drainfield be mowed and maintained in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
10/16/2023 | Alternative | Routine/Scheduled | 036-STS-34313 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 11:44AM
10/02/2023 | Alternative | RoutineScheduled | 177-06-0608-SWT | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Delta Whitewater |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Other","Effluent Screens"] | YES | Musty | Clear | [14 empty] | Inspected | Sludge/Scum - Septic 5" 3 Zone Drip - drip field flushed 15mins per zone. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 12:00 AM
01/24/2023 |  | Initial Visit | 14-172-0152A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 500.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit. Primary septic tank - normal level - riser is fractured. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced - field flushed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 11:00AM
02/21/2023 |  | Reportable Incident | 181-08-0005 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | New Client/ New Owner -Second trip- Due to alarm- Found inside the home Recirculation pump breaker was tripped off, turned it on and upon running in test mode the water level quickly corrected itself. Replaced the wirenuts in the junction box for the recirculation pump.. Signs of melted wires from pump running. PF300511 Pump - Water level in junctiob box was hgih enough to short out the circuit breaker. Currently the system is working normal and in rest mode. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/01/2023 | 09:30 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance | SD-06-111 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | On site to insect system. Peat moss is in ok condition for its age. Roots growing in pods 1 and 5. Proposal to be sent to remove roots, auger all 5 pods and add root destroyer to pod 1 and 5. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
04/26/2023 |  | Routine/Scheduled | {FIPSCode}-STS-5274 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 12:30PM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
01/24/2023 |  | Routine/Scheduled | 550-STS-6634 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/24/2023 |  | 3.000000 |  | 2.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 9:35AM
06/05/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | [8 empty] | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
07/24/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0196-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Bad low level alarm float, replaced. Pump tank needs pumping due to sludge levels, customer said she was calling pumper right away. HL 17, LL 30, OVERRIDE 30. Replaced bug bag. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
04/15/2023 |  | Reportable Incident | 113-STS-22131 | Madison | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | Aquasafe | pumptank | Gravity | Pressure | Drip | Not Applicable | 100.000000 | [] | [] | YES | Musty | Clear | [15 empty] | See attached | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/02/2023 | 08:20 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Uncovered distribution box due to what appeared to be nitrification around the box area. The box and surge box are functioning as designed. Recommend re-parging them to protect from future issues. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/03/2023 |  |  | 16-120-0316A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Purasys | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
01/20/2023 |  | RoutineScheduled | 179-16-0192-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 1-3 0-7 | 0[-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [17 empty] | Inspected | replaced n98 pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/20/2023 | 02:00 PM
05/02/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 01:07 PM
07/11/2023 | Alternative | RoutineScheduled | SD-05-356 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Mckim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Pad | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/20/2023 | 07:30 AM
11/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-15-0103-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Control Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
07/27/2023 | Alternative | RoutineScheduled | 09-163-0074 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 12:00 AM
10/23/2023 | Alternative | RoutineScheduled | 107-05-0566 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | 12:00 AM
07/25/2023 | Alternative | Routine/Scheduled | 550-STS-6474 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | Dec 30 1899 2:45PM
06/21/2023 | Alternative | Routine/Scheduled | 103-STS-92860 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 05:35 PM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/21/2023 | Alternative | Routine/Scheduled |  | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | Dec 30 1899 7:00AM
11/22/2023 | Alternative | RoutineScheduled | TFOX-8ZLLHD | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Norweco Singulair |  | Gravity | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 12:00 AM
11/14/2023 | Alternative | Routine/Scheduled | 057-STS-95277 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal level 4 in of sludge 1 in of solids No signs of infiltration -Discharge/Pump Tank: Normal level Less than 1 in of suspended solids Tested floats and pump all working properly All plumbing intact and pump moving water properly No signs of infiltration -Aeration: Normal level 13 in of suspended solids Pulled and cleaned weir Tested both floats working as should Pulled and cleared diffuser Air line intact and properly dispersing air No signs of infiltration -Air Pump/Blower: 120 volts coming in Pulled and cleaned filter Air pressure sensor properly working Air pump pulled .54 amps -Control Panel: 120 volts coming in All visual and audible alarms functional Pump pulled 8.28 amps All components working properly -Distribution Box: 6 lines all intact and properly taking water Speed balancers intact and functioning Pulled minor grass roots from top of lid -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 10:30 AM
01/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | Best 1 | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/30/2023 |  | RoutineScheduled | 099-07-0097-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
03/31/2023 | Alternative | RoutineScheduled | 154-07-0449 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
04/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | Dec 30 1899 4:23AM
02/22/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2346 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 3:00PM
06/08/2023 | Alternative | RoutineScheduled | SD-11-390 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
02/08/2023 |  | RoutineScheduled | 181-01-0042 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The pump operation was operating as designed. The controls were operating as designed. There were no visible leaks in the LPD leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/11/2023 | 12:50 PM
07/20/2023 | Alternative | Initial Visit |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | [] | [] | [18 empty] | Start up on Advantex Ax20/RT ORD 520874-9 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 12:00 AM
04/12/2023 |  | RoutineScheduled | 179-18-0272-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, we recommend replacing the lid on the Fralo Monster Box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
03/13/2023 | Alternative | Initial Visit | S800-13-0032 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | AOSS - Initial Visit Primary Septic tank - buried under paver walkway - inspection port present. Aeration Tank - normal level - NO mixing present - compressor diaphragms blown - repaired on property. Pump Tank - float sensors, pump and controls operating. DBox - appears to be a pressure manifold vs. Distribution Box. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/14/2023 | Dec 30 1899 7:30AM
01/27/2023 |  | RoutineScheduled | SP-04-131 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. System full to its capacity when we arrived both tanks were full due to dead pump. Replaced olds dead n140 with new n140 (11.64 amps). New pump doing 60 gallons per minute. New run time 50 seconds. Outstanding proposal to seal risers, repair broken cleanout, replace event counter and dig up D- box to inspect. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
12/02/2023 | Alternative | Initial Visit |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 RT |  | Pump | Gravity | Trenches |  |  | ["Control Operation","Recirculation Pump"] | ["Control Operation","Recirculation Pump"] | NA | [17 empty] | Initial start-up inspection. Verified proper installation. Programmed recirculation pump timers. Set recirculation pump flow rate. Tested floats, pumps and alarm. Tightened several loose unions in treatment unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | 07:03 PM
08/10/2023 | Alternative | RoutineScheduled | 181-12-0024 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2500 | Septic Tank Only | MicroFast | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NO | [17 empty] | The system did not need to be pumped. The return pipe entering the pump tank from the drain field was updated with a pressure gauge and a ball valve to be able to adjust the pressure on the drip field. The pressure was adjusted to the desired pressure. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 01:50 PM
11/06/2023 | Alternative | RoutineScheduled |  | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Battletown Environmental Consulting, LLC | 1942001135 | Robert | Charnley | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/18/2023 | Alternative | Routine/Scheduled | 151-03-395 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES |  |  |  |  | 33.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 07:02 PM
03/24/2023 | Alternative | Routine/Scheduled | 16-174-0238 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Dec 30 1899 7:30AM
05/17/2023 | Alternative | RoutineScheduled | 115-05-0384 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 12000 | Biomicrobics Fast 2.5 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Sludge levels- Very thick scum layer 6-8" and 24"+ sludge on both east and west side of school tanks. Reccomend to have both pumped out maybe approx 12000 gallon from the main east and west side tanks. Fast treatment unit 10-12" Slduge in center treatment unit is good and FAST Unit does not need pumping. Pump tanks trace sludge Good Aeration from Blower, cleaned blower motor filter , Clear Effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2022 | 12:30 PM
05/10/2023 |  | RoutineScheduled | 179-18-0013-VU | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Installed new regenerative blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
03/02/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | RB blower installed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
12/05/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0873 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
03/14/2023 |  | RoutineScheduled | 13-113-102 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","SludgeScum Accumulation","Effluent Screens","Control Operation","Auxiliary Filter"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/14/2023 | 12:00 AM
09/07/2023 | Alternative | Routine/Scheduled | 550-STS-6597 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 11:45AM
06/16/2023 | Alternative |  | 154-03-0333 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Mark | Leimhaas | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/12/2023 | Alternative | Routine/Scheduled | 234-17-290 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced aerator and diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | Dec 30 1899 10:00AM
12/20/2023 | Alternative | RoutineScheduled Component Maintenance | 182-01-0065 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
10/10/2023 | Alternative | Reportable Incident Component Maintenance | 175-11-0268 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed AP80 compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
12/07/2023 | Alternative | RoutineScheduled | 07-184-5002 | Scott | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Sulphitic | Cloudy | [16 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | pump tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
09/12/2023 | Alternative | RoutineScheduled | 108-97-0055 (LEGACY ALT. SYSTEM) | Bath | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation","Effluent Screens","BlowerCompressorAerator Operation","Auxiliary Filter"] | ["SludgeScum Accumulation","Effluent Screens","BlowerCompressorAerator Operation","Auxiliary Filter"] | YES | [16 empty] | Pumped Out | The MicroFast tank and pump tank was both pumped and cleaned. The blower and spin filters were both pulled and cleaned. The controls were operating as designed. There was return effluent returning to the pump tank from the drip field so the drip field was operating as designed. The blower pipe had settled and broke and wasn't blowing so the pipe was dug up and repaired. The blower is now functioning as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/09/2023 | 10:10 PM
02/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator control panel was replaced and the system appears to be functioning as designed at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
01/30/2023 |  | Routine/Scheduled |  | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Richmond | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2600 | Multiflo FTB |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 50.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | Jan 1 1900 5:47PM
10/19/2023 | Alternative | Reportable Incident | 12-163-0101 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Clearstream. Panel was in Alarm. Discharge in high level. Pump and floats working properly, pump moving water properly. Found that there wasn't a lot of water coming into the dbox. We cut the 4" 90 off the line in the dbox and turned the pump back on and it force another of dark brown water into the box and then clear water after that. Water is now moving properly and pumped the tank to normal level. We then glued the 90 back on but drilled a hole in the top of it to prevent and air pocket. Used alarm call | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 11:58AM
11/06/2023 | Alternative | RoutineScheduled | 132-04-0218 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Mound | Not Applicable | 150.000000 | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 11:05 AM
06/15/2023 |  |  | SP-05-93 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/11/2023 | Alternative | RoutineScheduled | 115-03-0340 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank | Ecoflo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | [15 empty] | Inspected | Sludge level-0.5"Scum layer & 12" Sludge in Septic tank. Cleaned Effluent filter and tipping tray -old style. System peat was replaced prior to time of sale. New Peat appears fluffy and moist on top, We turned all of the surface peat, Noted many new roots growing in the tank from the wooded lot of trees. in pump basin- Alarm functional and pump is operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 09:30 AM
01/19/2023 |  | RoutineScheduled | 179-07-0031-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 182-16-0189 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 09/26/2023 |  | 41.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal Replaced pressure gauge | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
03/28/2023 |  | Routine/Scheduled | 17-120-0333A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | The tank needs pumping | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/28/2023 | Jan 1 1900 8:26AM
07/26/2023 | Alternative | RoutineScheduled | 12-160-0071 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | ECOPOD |  | Gravity | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] |  | Septic | [7 empty] | Sample Tap | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 12:00 AM
04/13/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [28 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | 02:57 PM
01/04/2023 |  | RoutineScheduled | S 800-18-0049 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | JEF Septic LLC | 1942001131 | Jason | Fulbright | 1.000000 | 1000 | Clearstream ATU (600DC) |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | [] | [] | NA | Musty | Clear | 7.200000 | 3.500000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 12:00PM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | Dec 30 1899 11:24AM
11/02/2023 | Alternative | Routine/Scheduled | S 800-13-0153 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 10:50AM
02/08/2023 |  | RoutineScheduled | 179-STS-91636 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Disinfection" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Disinfection" ,"Attached Growth Medium"] | NA | [7 empty] | 02/08/2023 |  | 8.000000 |  | 1.800000 |  |  |  | Will be sent separately | Inspected | Routine inspection. Sample taken. Small leak on pump tank inlet riser uv gasket. Off float for discharge stock close. Called installer and his going back to fix problems. RECIRC: HL 1, LL 13. DISCHARGE: HL 5, ETM 0M, PEAK 5, ETM 0M. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
02/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:40PM
05/02/2023 |  | Routine/Scheduled | 036-STS-34542 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/02/2023 | Jan 1 1900 1:46PM
06/29/2023 | Alternative | Routine/Scheduled | 800-11-0009 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | Dec 30 1899 1:35PM
03/03/2023 |  | Routine/Scheduled | 03-163-0184 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. PUmp Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | Jan 1 1900 7:00AM
11/28/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV Bulb, glass housing & control head. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/06/2023 | Dec 30 1899 9:34AM
08/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/09/2023 |  | RoutineScheduled | 003-STS-31527 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | AquaSafe |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
03/13/2023 |  | RoutineScheduled | 12-152-A1 | Lee | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/13/2023 | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled | 107-17-0044 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0407-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We added a tee in the Fralo Monster Box to improve effluent distribution. We recommend cutting back the growth along the top of the upper line and along the end of all lines. We recommend the entire dispersal area be maintained in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/24/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:52 PM
03/29/2023 |  | RoutineScheduled | 107-02-0855 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
06/01/2023 | Alternative |  | 154-07-0498 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
01/27/2023 |  | Routine/Scheduled | 550-STS-6365 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 |  |  |  | 01/24/2023 |  | 6.000000 |  | 1.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | Jan 1 1900 11:10AM
11/28/2023 | Alternative | Routine/Scheduled |  | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Norweco Singulair ATU |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | N/A | [16 empty] | Pumped Out |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/10/2024 | 02:17 PM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92601 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. System will need pump out next year. Treatment is crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
04/25/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2292 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 11:55AM
12/28/2023 | Alternative | Reportable Incident | 228-07-0638 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced Zoehler 152 pump, on/off float, aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/28/2023 | Dec 30 1899 5:15PM
03/15/2023 | Alternative | RoutineScheduled | 159-10-0014 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/22/2023 |  | RoutineScheduled | 167-STS-15451 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/22/2023 | 12:00 AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping treatment unit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/03/2023 | Alternative | Initial Visit | 800-STS-15301 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 3.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1 minute every 2 hours. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | Dec 30 1899 11:30AM
09/27/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches |  | 450.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 10:36 AM
10/05/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1530 | Microfast |  | Pump | Pressure | Drip |  | 100.000000 | ["Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | The entire system is in compliance with the HD regulation and approved plans. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 11:00 AM
06/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled | 10-197-057 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/13/2023 | 12:00 AM
07/25/2023 | Alternative | Follow-Up | 136-15-0010 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Pad | Not Applicable | 450.000000 | Control Operation | Control Operation | N/A | [17 empty] | Replaced failed AdvanTex motherboard with new. Set program parameters from original permit. Replaced failed dual pump control panel with new. Set program parameters from original "As Built" and Inspection Reports. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/27/2023 | 06:30 AM
11/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Gravity |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 11:20AM
07/28/2023 | Alternative | RoutineScheduled | 107-01-0148 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
03/06/2023 |  |  | 085-STS-34341 | Hanover | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1525 | 1000 | 525 | Pump | Pressure | Pad | Not Applicable |  | [] | ["Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Control Operation","SludgeScum Accumulation"] |  | Sulphitic | Black | 6.000000 |  | 4.000000 | [13 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/06/2023 | Jan 1 1900 2:00PM
08/03/2023 | Alternative | Routine/Scheduled |  | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - Component Upgrades. Installed new riser access on septic tank - effluent screen serviced. Installed new riser access on pump tank - Resealed forcemain penetration Replacing access risers and parging tanks to prevent surface / ground water infiltration - next step is to replace the failed biofilter media. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/07/2023 | 09:00 AM
01/13/2023 |  | RoutineScheduled | SP-05-370 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Dispersal System Operation"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
02/14/2023 |  | RoutineScheduled | SP-05-861 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation"] | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. No wet spots by distribution box. Everything looks good after repairs were done. System might need to be pumped out next year. Found female products and sanitary wipes in septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/09/2023 | Alternative | Routine/Scheduled | S 800-18-0293 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 1:00PM
08/09/2023 | Alternative | Routine/Scheduled | 234-17-474 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 11:19AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
02/15/2023 | Alternative | Reportable Incident | 171-08-0557 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1000 | Bio Coir |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Other"] | ["Other"] | [18 empty] | There was little to none media left in Bio-Coir. What was left, was shoveled out and lime was applied and disposed of in trash bags at landfill. New coconut media was added along with lantec globe balls. Speed levels was added to distribution box also on each line | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/23/2023 | 10:00 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/14/2023 | Alternative |  | 14-100-0361 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
08/28/2023 | Alternative | RoutineScheduled | 107-05-0404 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
11/20/2023 | Alternative | Reportable Incident | 2017-143-0061 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Norweco. Found control panel was alarming and light was blinking. Discharge was at normal level. Was unable to run the pump due to bottom float not working properly. I jumped out the bottom float so it stopped low level Alarming and system is now working properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 02:10 PM
07/26/2023 | Alternative | Routine/Scheduled | S 800-19-0004 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip Field - headworks serviced - field flushed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | Dec 30 1899 9:00AM
10/11/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Attached Growth Medium"] | YES | [17 empty] | Unclogged all pod drain lines | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | Dec 30 1899 10:40AM
05/29/2023 | Alternative | Reportable Incident | 157-00-308 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | COSS - GMP2018-02 Pump tank lid collapse - pumped septic tank and pump tank empty for storage. Septic tank appears to be intact | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/01/2023 | 02:15 PM
06/19/2023 | Alternative | Reportable Incident | 159-96-367 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 300.000000 | None | None | [18 empty] | Neighbor reported system overflowing into yard! Tenant / hydraulically overloading treatment system ... Enjoying long baths in jacuzzi tub and doing entirely too much laundry! currently waiting on HD Permit to replace peatmoss biofilter media with new bioCor media. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 11:00 AM
04/05/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced uv bulb and cord. Septic system is in working condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/26/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0016 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 10:33 AM
10/10/2023 | Alternative |  | 171-08-0136 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Advantex |  | Pump | Gravity | Trenches |  | 450.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/31/2023 | 11:30 AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/09/2023 | Alternative | Routine/Scheduled | 550-STS-6598 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 10:10AM
11/07/2023 | Alternative | Reportable Incident | S 800-18-0027 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/07/2023 | Dec 30 1899 3:00PM
12/20/2023 | Alternative | Routine/Scheduled | 17-142-0251 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | Dec 30 1899 3:30PM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/02/2023 | Alternative | Routine/Scheduled | 119-STS-93808 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 400 |  |  | Pump | Gravity | Pad | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Processing Tank - Trash Tank - normal elvel Aeration Tank - mixing present - compressor serviced. Sludge Return - operating / flushed / adjusted. U.V. Disinfection - bulb and housing serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | 07:45 AM
07/14/2023 | Alternative | RoutineScheduled | 133-STS-101232 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/19/2023 | Alternative | Routine/Scheduled | 136-18-0357 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Purasys |  | Pump | Pressure | Mound | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank -= normal level Sequential Batch Reactor - float sensors, pumps and controls operating. Mound - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 02:00 PM
07/12/2023 | Alternative | RoutineScheduled | 182-17-0212 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Aqua Safe | [6 empty] | ["Auxiliary Filter","SludgeScum Accumulation"] | ["Auxiliary Filter","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | 12:00 AM
07/22/2023 | Alternative | RoutineScheduled |  | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2500 | septic | ISF | Gravity | Pressure | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/24/2023 | 08:00 AM
04/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/15/2023 |  | RoutineScheduled | 2018-143-0253 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Norweco Singulair |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | 12:00 AM
05/26/2023 |  | RoutineScheduled | 065-STS-32278 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/28/2023 | 12:00 AM
03/28/2023 |  | RoutineScheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Inlet clogged blower audible alarm bad panel replaced arcon, pumped tanks | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
11/28/2023 | Alternative | Pump-Out Only |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | Dec 30 1899 11:00AM
06/30/2023 | Alternative | Reportable Incident | 157-08-0034 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a rebuild kit on the aerator. Installed a 3/4" brass check valve on headworks. The timer is set to 3 minutes every 1.5 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/30/2023 | 01:30 PM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Power surge last week tripped Microfast blower breaker. Breaker was reset and system should return to designed operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/13/2023 | Alternative | RoutineScheduled | 107-02-0995 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.220000 |  |  |  |  | 12/13/2023 |  | 4.000000 |  |  | 2.400000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 10:00 AM
10/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled | 14-100-0135 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 7.000000 | 8750 | Septic Tank | Puraflo | Gravity | Pressure | Pad | Not Applicable | 3625.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | 10:15 AM
05/23/2023 | Alternative | RoutineScheduled | 105-04-0134 | Appomattox | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Septic Tank | Delta Whitewater | Pump | Gravity | Trenches | Not Applicable | 350.000000 | [] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation","Distribution Pump Operation"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 05:45 PM
09/19/2023 | Alternative | RoutineScheduled | 196-10-175 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | checked sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/09/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU | Clearstream ATU | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/09/2023 | Dec 30 1899 1:31PM
02/02/2023 |  | RoutineScheduled | {FIPSCode}-STS-4810 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/02/2023 | 12:00 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/07/2023 | Alternative | RoutineScheduled | 109-06-0493 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | NA | [16 empty] | Inspected | Replaced the new lid and completed the conduit burial process added 1 new wire for the pump. System returned to normal operation after our visit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/30/2023 | 09:30 AM
06/19/2023 | Alternative | RoutineScheduled |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock-Rapidan | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1500 | Ecopod |  | Gravity | Gravity | Trenches | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | The entire system is in compliance with the health department regulations and approved plans | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 05:00 AM
04/25/2023 |  | Reportable Incident |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced DBox with new 8 port concrete DBox. Spliced to exiting conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | 12:45 PM
10/02/2023 | Alternative | RoutineScheduled | 19-142-0138 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/29/2023 |  | RoutineScheduled |  | Page | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | inlet t blocked purple zone valve leak needs repaired Recommend pump primary tank 1 1/2 x 1 1/4 inlet | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/28/2023 | 02:17 PM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter"] | ["Disinfection" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
03/14/2023 |  | Routine/Scheduled | 550-STS-6641 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Jan 1 1900 12:35PM
01/10/2023 |  |  | 041-STS-257936 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Multi Flo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Effluent Screens","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | 12:00 AM
08/30/2023 | Alternative | Routine/Scheduled | 2007-143-0230 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/30/2023 | 09:36 AM
05/03/2023 |  | Initial Visit |  | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a red light on. Serviced system. Checked the pump and floats (ok). Cleaned the filter in the Clearstream and cleaned the disc filter. Changed the diffuser in the Clearstream and changed the filter in the aerator. Owner wants the aerator raised. Replaced the relay, replaced the mute button, and replaced the pump breaker. The UV is burnt up - needs to be replaced. The septic tank needs additional risers on it to be properly inspected in the future. The timer is set to 8 minutes every 2 hours. Did not take BOD and Fecal samples due to the UV not working. The timer is set to 8 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/03/2023 | Jan 1 1900 6:00PM
03/02/2023 |  | RoutineScheduled | 179-STS-88721 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Dark Brown | [13 empty] | Will be sent separately | Inspected | The drainfield trenches are not absorbing water and effluent is surfacing at the distribution box. As noted previously, we recommend that an AOSE evaluate repair options. System is currently impacted by the effects of chemotherapy. We recommend pumping all the tanks, scraping the Advantex sheets, and cleaning all pumps & filters when chemotherapy is completed in May. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast Needs Pumped out. Also broken ARV in field on zone 2 needs repaired so zone 2 can be used. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 154-05-0330 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend removing the trees that are growing around the Septic Tank and Puraflo modules to prevent root intrusions. The peat in the Puraflo modules has settled but is still in good condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
04/24/2023 |  | Routine/Scheduled |  | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 07:30 AM
09/11/2023 | Alternative |  | 17-100-0507 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lines were unevenly nitrified upon arrival. The Distribution Box was uncovered and re-leveled. The system should return to proper function. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/13/2023 | Alternative | RoutineScheduled | 147-06-0202 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | None | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | SD-14-095 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens" ,"Distribution Pump Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
09/06/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | [] | [] | [8 empty] | 09/06/2023 | Sample Chamber | 57.000000 | [5 empty] | Attached to this report |  | Sample results only/ Great Falls Septic is the maintenance provider. I don't have info to make a proper certification so I am stating the system may return to normal, don't know if the provider made any repairs or if any are needed but the sample results are high/ May need a pump out to bring the sample results in compliance. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/20/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped and cleaned the Clearstream tank and pump tank. Replaced the spinfilter screen and the diffuser in the Clearstream. Cut the UV off and disconnected the pressure switch due to the pumping of tanks. Need to flush out the drainfield, set pressures, and perform a draw down test. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/20/2023 | Dec 30 1899 12:00PM
11/03/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/30/2024 | 12:00 PM
06/14/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
01/19/2023 |  | Routine/Scheduled | 19-120-0173A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/19/2023 | Jan 1 1900 4:04PM
12/28/2023 | Alternative | RoutineScheduled | 165-STS-335690 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
07/26/2023 | Alternative | Reportable Incident | 136-18-0110 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The timer is set to 4 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/26/2023 | 09:00 AM
12/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/18/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 12:00 AM
11/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Tanks Pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
02/21/2023 |  | RoutineScheduled | SP-04-544 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance | 137-STS-22120 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Distribution Pump Operation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
05/22/2023 | Alternative | RoutineScheduled | S-05-111-0167 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did need to be pumped but will be pumped at the end of June. The return line from the drip field will also be rerouted to the pump tank at the end of June. The return line is creating wash over to the treatment side of the tank. This is the reason for the rerouting. The blower and spin filter were both cleaned. The controls were operating as designed. There were no visible leaks in the drip field. There was return effluent returning to the pump tank so the drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | Jan 1 1900 10:35PM
06/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/15/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs new UV bulb. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | Jan 1 1900 12:26PM
08/08/2023 | Alternative | RoutineScheduled | 12-142-0182 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 | Alternative | RoutineScheduled | 154-02-1047 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | PuraFlo 4 module |  | Pump | Gravity | Trenches |  | 150.000000 | ["Control Operation","Auxiliary Filter","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 09:15 AM
10/10/2023 | Alternative | RoutineScheduled | 041-STS-260675 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Effluent Screens","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation","Auxiliary Filter"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0005-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0932 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Whitewater ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
05/11/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Puraflo peat needs replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Jan 1 1900 12:05PM
07/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2024 | 12:23 PM
06/07/2023 | Alternative | Pump-Out Only | 147-17-0079 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Multiflo FTB |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Pumped primary septic tank and aeration tank as recommended from last service event. Aeration tank refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 10:00AM
02/24/2023 |  | Routine/Scheduled | 147-11-0051 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | Jan 1 1900 8:30AM
06/02/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92582 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend removing the trees that are planted in the drip dispersal area in order to prevent roots from damaging the system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
06/22/2023 | Alternative | Routine/Scheduled | S 800-19-0037 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 4 modules -Peat;moss in good condition - standing water in sample chamber! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | Dec 30 1899 12:00AM
10/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 10/10/2023 | Sample Chamber | 7.000000 | [5 empty] | Attached to this report |  | Septic Tank-12"sludge 3"scum/ Microfast-14"sludge/ Pump Tank-0"sludge 0"scum/ May need pump out of the Septic-Microfast Tank next year/ Noted: Excessive cover over the tanks (5') Owner informed/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-3264 ETM-104h 15m/ Pump2-3044 ETM-101h 2m On-2m2s Off-6h/ Peak-14 Peak Off-4h 48m/ / No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/03/2023 | Alternative | RoutineScheduled | 115-13-0326 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | [17 empty] | Inspected | Pump Out by Foutz on this treatment unit, It was full of suldge and paper. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 05:30 PM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0488 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 7.200000 | 12.800000 | [11 empty] | Will be sent separately | Inspected | 1 D80 Compressor | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 01/30/2024 | 01:28 PM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/02/2023 | Alternative | RoutineScheduled | 179-STS-87167 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 1.000000 | 1500 | 0-1 | 0-1 | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | None | Clear |  |  | 3.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 10:00 AM
12/20/2023 | Alternative |  | 132-08-0097 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Jonathan | Elliott | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/19/2023 | Alternative | RoutineScheduled | SD-06-84 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 3.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 43.750000 | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 05:30 PM
02/13/2023 |  | Reportable Incident | 228-11-0654 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/13/2023 | Jan 1 1900 10:00AM
08/16/2023 | Alternative | RoutineScheduled | 107-14-0174 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
05/15/2023 |  | RoutineScheduled | 2073-05-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Recirculation Pump"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump"] | NA | Musty | Clear | 7.900000 |  |  | 1.800000 |  | 05/25/2023 | Sample Chamber | 20.000000 |  |  | 11.100000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/07/2023 | 12:00 AM
10/12/2023 | Alternative | Reportable Incident Component Maintenance | SD-07-579 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Owner called for service because a neighbor had heard the septic alarm. Neither tank was in alarm, but pump tank walls were wet up to the high level float and a small, but steady inflow was seen in the recirc tank. Control panel electronic log had recorded 1 high level alarm in the recirc tank yesterday (date & time may not be accurate). Gave owner dye tablets to check for leaking toilets. One was showing a small leak. Owner said she will get the fill valve and flush valve for that toilet replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
10/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
07/03/2023 | Alternative | Routine/Scheduled | 228-13-0051 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/03/2023 | Dec 30 1899 8:05AM
07/12/2023 | Alternative | Routine/Scheduled | 228-19-0062 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 12:25PM
05/05/2023 | Alternative | Reportable Incident Component Maintenance | 175-03-0597 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced effluent pump #F2M102-T2510 1 hp 230 v. Air line to ATU is broken. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
03/22/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
09/01/2023 | Alternative | Routine/Scheduled | 136-06-0351 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal levle. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Dbox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 07:45 AM
11/21/2023 | Alternative | Routine/Scheduled | 157-04-092 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Tank at normal level Has 2" of solids with 7" of sludge Pulled and cleaned filter Riser is showing signs of leaking -Discharge/Pump Tank: At normal level Tank showing some signs of bulging in the bottom Components are spliced in an un sealed LB Pump are aged but working -Peat Moss: Chamber has concrete blocks holding it down Tipping bucket and trays working There is alot of peat in the chamber but it's more like dirt with gravel in it. -Control Panel: Panel working properly but is aged Discharge pump pulling 5.24amps | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 03:39 PM
07/17/2023 | Alternative | RoutineScheduled | 107-03-0320 (LEGACY ALT. SYSTEM) | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [18 empty] | media and laterals cleaned. Baffle cleaned (clogged) | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/10/2023 | 12:00 AM
12/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced buzzer | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 12:20PM
08/17/2023 | Alternative | Initial Visit | 025-STS-15630 | Brunswick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Southside | Matthews Sanitation Services Llc | 1942001226 | Brian | Matthews | 1.000000 | 1250 |  |  | Gravity | Pressure | Pad | Not Applicable | 600.000000 | [] | [] | NA | None | [15 empty] | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/17/2023 | 12:00 AM
01/12/2023 | Alternative | RoutineScheduled | 151-10-0001 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1250 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 12:00 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/01/2023 | Alternative | RoutineScheduled | 143-STS-17079 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank Pumped | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multi-Flo |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Musty | [15 empty] | Inspected | Sludge level-in Septic Tank - NO ACCESS unable to check - Treatment tank has some stong odor and signs of a bacteria die off likely due to washing chemical or anti septic cleaners-Treatment tank smells septic- Reccomended to stop/reduce all chemicals which affect bacterial growth. Clear Effluent on top. But the filter socks had some slime build up. System was very recently installed as an upgrade and the visit was to determine if it is installed c orrectly, It looked to be installed correctly and should return to normal operation after the chemicals are either pumped out and fresh weater refilled or they dilute away. Good Aeration in the tank and the alarm is functional. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/30/2023 | 09:30 AM
11/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Micro Fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/16/2023 |  | Follow-Up |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Ecoflo |  | Gravity | Gravity | Trenches |  |  | Dispersal System Operation | Dispersal System Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/20/2023 | 02:48 PM
04/11/2023 |  | Routine/Scheduled | 041-STS-259815 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Fuji |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/11/2023 | Jan 1 1900 8:34AM
07/07/2023 | Alternative | Initial Visit | 136-09-0293 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 |  | BioMicrobics Micro Fast 0.5 |  | Gravity | Gravity | Pad | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | NA | Musty | Clear | [14 empty] | Pumped Out | Upon inspection found improper size aerator. Replaced with correct spec aerator. Pumped out septic tank and treatment tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/07/2023 | 12:00 AM
02/15/2023 |  | RoutineScheduled | VAG408425 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  | Pump | Gravity | Discharge |  |  | ["BlowerCompressorAerator Operation","Other"] | ["BlowerCompressorAerator Operation"] | [18 empty] | trees need to be removed from ET bed. no discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/15/2023 | 12:00 AM
11/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 11:45AM
03/11/2023 | Alternative | RoutineScheduled | 171-17-0093 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | EZ-Treat |  | Gravity | Gravity | Discharge | UV |  | ["Attached Growth Medium","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA |  |  | 7.250000 | 8.900000 |  |  |  | 02/27/2023 | Sample Chamber | 6.300000 |  |  | 4.600000 |  |  | Will be sent separately | Inspected | Septic Tank under 1" scum laye-6-8" sludge on bottom in Septic tank - Recirc zone of tank 1" scum and 12-16" sludge, Owner replaced UV bulb and took lab samples to Pace, Blower unit runs and owner cleaned/replaced aitfilter, Clear Effluent on top, Pumps operational, 1 min on 15 min off but not accurate per owner. alarm operational, all floats tested operational. DO 8.94 and pH7.65, Owner takes samples to Eden PACE Analytical lab in NC for testing. TSS - 4.6, BOD - 6.3 Ecoli N.D. Total Coliforms 1410 mpn/100ml. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/23/2023 | 09:30 AM
11/13/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 7.600000 | [14 empty] | Blower not operational | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/13/2023 | 11:30 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Strongly recommend moving the new tree that is in between the lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/09/2023 | Alternative | RoutineScheduled | 087-STS-6191 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/16/2023 | Alternative | RoutineScheduled | VAG401883 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Gravity | Discharge | Chlorination |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [17 empty] | Pumped Out | No discharge at this time | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/14/2023 | 12:00 AM
08/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 4"scum/ Microfast-14"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Recommend pump out of the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-1876 ETM-125h/ Pump2-1849 ETM-124h 2m/ Peak-27/ High-10/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled | 179-18-0024-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock | Mckim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 1500 | 2000 |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/20/2023 | 07:45 AM
01/05/2023 |  | RoutineScheduled | {FIPSCode}-STS-12380 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Cloverleaf Environmental Consulting, Inc | 1942001135 | Robert | Charnley |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Control Operation"] | ["SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection was performed. System components need to be updated. Will re-file once components are updated. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Force main in pump tank is broken. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/15/2023 | Dec 30 1899 1:44PM
09/12/2023 | Alternative | Initial Visit | 800-STS-14165 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 6.000000 |  | 5.000000 | [5 empty] | Owner called due to the red light being on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The aerator should be raised. Replaced the UV light bulb. The timer is set to 2.5 minutes every 2 hours. Took initial BOD and Fecal samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/12/2023 | Dec 30 1899 9:30AM
07/24/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-92387 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
06/28/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 11:52 AM
10/26/2023 | Alternative |  | 085-STS-34371 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","SludgeScum Accumulation","Dispersal System Operation","Effluent Screens","Recirculation Pump"] | YES | Pungent | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 9:30AM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced valve box | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM
05/15/2023 | Alternative | Reportable Incident | S 800-19-0041 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/15/2023 | Dec 30 1899 8:00AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 107-02-0650 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
04/17/2023 |  | RoutineScheduled | SP-05-257 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"SludgeScum Accumulation"] |  | NO | [15 empty] | Will be sent separately | Inspected | Septic Tank and Pump Tank need to be pumped Filters Cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | Dec 30 1899 2:41PM
10/25/2023 | Alternative |  | 033-17-0086-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/07/2023 | Alternative | Reportable Incident Component Maintenance | 179-13-0056-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to a failed blower. Replaced blower. Tanks were pumped before our site visit. Inlet wedge lid leaks inlet riser needs to be installed. Let the home owner know to use garbage disposal very lightly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
07/21/2023 | Alternative | Routine/Scheduled | 228-16-0440 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | Dec 30 1899 10:20AM
07/21/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0022-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the air release valve housing and lid on the lower zone of the drip dispersal area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lower line appears to show signs of nitrification outside of the trench area. There are no signs of wet or soggy areas though. Recommend rebalancing D-Box and checking header connection to ensure that effluent isn't bleeding down to lower line. Camera headers if necessary. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
08/15/2023 | Alternative | RoutineScheduled | 035-STS-37285 | Carroll | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Eco Pure |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
06/22/2023 | Alternative | RoutineScheduled | 03-163-0063 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Advantex |  | Gravity | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Recirculation Pump"] |  | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/11/2023 |  | RoutineScheduled |  | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 04/11/2023 |  | 48.000000 | [5 empty] | Will be sent separately | Inspected | Replaced all pressure gauges Replaced cracked and clogged filter Recommend to not have activities on top of drainfield | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
02/15/2023 |  |  | SWP-04-54 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
03/08/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | N98 pump needs replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | Jan 1 1900 12:26PM
09/26/2023 | Alternative | RoutineScheduled | 10-117-044 | Carroll | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 0.000000 | 1000 | AS 500 | N/A | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["Other"] | ["Other","SludgeScum Accumulation"] | NA | None | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | Dec 30 1899 11:30AM
07/22/2023 | Alternative | Routine/Scheduled | 119-STS-94264 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. LPP Field - valves exercised, no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 10:15 AM
12/23/2023 | Alternative | RoutineScheduled | SD-12-060 | Madison | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Advantex | Gravity | Gravity | Discharge | UV |  | [] | [] | YES | Musty | Clear | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/02/2024 | 11:30 AM
06/05/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-702 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/16/2023 | Alternative | Reportable Incident | 196-12-151 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
12/08/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 8:30AM
08/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Ecoflo | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
12/11/2023 | Alternative | Reportable Incident Component Maintenance | 179-14-0212-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm started after heavy rain. Observed fairly heavy groundwater infiltration occuring around sewer inlet pipe (boot appears to be compromised). Also saw a slow drip near left/front corner of topseam, inlet end of septic tank. Event log in Aquaworx Panel showed about a 14" increase in water level over a 4 hour period Sunday night after all day raining. Inlet pipe needs dug up, boot checked and resealed. Corner of septic tank topseam should also be looked at. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There is no power getting to the Norweco control panel. Aerator/alarm are not functioning due to this. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
07/07/2023 | Alternative |  | ST-05-579 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
02/03/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NO | [17 empty] | Maintenance inspection/replace 1 float | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | Dec 30 1899 10:30AM
03/07/2023 | Alternative | Pump-Out Only | 800-STS-14487 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 10000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 14000.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Primary septic tank pumped empty as recommended during previous service visit. Secondary septic tank skimmed to remove scum layer as recommended during previous service visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/08/2023 | Dec 30 1899 10:30AM
04/05/2023 |  | RoutineScheduled | 07-184-5011 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/05/2023 | 12:00 AM
02/20/2023 |  | RoutineScheduled | SWP-05-418 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 5" of water in sample port, tried to pump it out but kept coming in. Customer said they had alot of rain couple days before inspection, will stop by on a dry week or next site visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
07/05/2023 | Alternative | Routine/Scheduled | 136-06-0169 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Biofilter - concrete - peatmoss in good condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBoix - plastic - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 07:00 AM
09/06/2023 | Alternative | Pump-Out Only | 093-STS-13843 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Supervised pumpout by Goodman's Septic Service - refilled processing tank for re-start. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 1:00PM
08/29/2023 | Alternative | RoutineScheduled Component Maintenance | 099-18-0157 C-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Broken wire for filter flush silinoid to close to base so had to replace it. Septic tank has tampons and grease, provided copy of Do's and don'ts. Treatment is crystal clear. 38 psi. RECIRC: HL-5, LL-22, OVERRIDE-421. DISCHARGE: HL-4, LL-13,OVERRIDE-0. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
02/09/2023 |  | RoutineScheduled | SWP-02-110 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Owner is going to repair defective emitter. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | 12:05 PM
04/06/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
05/03/2023 |  | Routine/Scheduled | 02-120-0171A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/03/2023 | Jan 1 1900 2:04PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Effluent Screens" ,"Disinfection"] | ["Disinfection" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | Dec 30 1899 12:46PM
01/27/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Aquarobic Mini Plant |  | Pump | Pressure | Drip |  | 300.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 09:35 AM
07/19/2023 | Alternative | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 300.000000 | [] | [] |  |  |  | 7.770000 | 5.120000 | 10.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 04:50 PM
03/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air line had broken. DSS moved the blower and replaced the air line. System appears to be functioning as designed at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
07/12/2023 | Alternative | Reportable Incident Component Maintenance | 033-13-0012-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation"] | ["Distribution Pump Operation" ,"Dispersal System Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | On site to repair broken air release valves which made a fairly big wet spot. Installed 2 new ARV's, flushed tubing, and then cleaned under solenoid diaphragms to remove debris. Spin filter was crushed and dirty, installed new one. Advised owner to get several wheelbarrow loads of topsoil to fill in depressed area around ARV's. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
04/14/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Anew drain field line was installed. An old line was shut off. Was inspected and backfilled. System is in working condition at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/18/2023 |  | Pump-Out Only | {FIPSCode}-STS-1293 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [28 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 9:00AM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0189-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
05/17/2023 |  | RoutineScheduled | 175-08-0034 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-12"sludge 0"scum ( May need pump out next year ) Pump Tank- 1"sludge 0"scum/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Puraflo Peat turned in all 5 modules and in good condition/ Counts: Pump-11414 ETM-110h 28m/ High-18/ Peak- N/A On-36s Off-2h Dose- 35 gal @ 58.8 gpm/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/24/2023 | Alternative | Initial Visit | 136-18-0205 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to to the alarm - red light on. Serviced system. Checked the panel and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Repaired broken fitting on pump headworks. The septic tank needs to be pumped out. Pump tank needs 2 - 6" x 20" risers and lids. Broken 4" 90 on the drainfield - needs to be addressed and/or fixed. Needs 4" plug on cleanout and a 6" x 12" riser and lid over the plug. Distribution box needs a new lid. The timer is set to 14 minutes every 0 hours. Did not take sample due to the aerator not working on arrival. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/24/2023 | 12:30 PM
12/26/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0326-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The peat in the Puraflo modules will need to be replaced in the near future. We have provided the owner with permit and design information along with possible Alternative Onsite Soil Evaluators who may be able to design a different alternative treatment unit. Additionally, there are roots in the distribution and header lines that will need to be removed with a machine . Finally, the pump tank is leaking under the pump lines. If peat is replaced in the Puraflo modules, we recommend the drain manifold be uncovered and unclogged. Please contact our office if you have any questions about these recommendations or next steps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
08/23/2023 | Alternative | Routine/Scheduled |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 4000 | Clearstream | Clearstream | Pump | Gravity | Trenches | Not Applicable | 3000.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Secondary septic tank - normal level - effluent screen serviced. Flow Equalization tanks (2) - float sensors, pump and controls operating. Aeration Tanks (2) - normal level - mixing present - compressors serviced. Pump tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 09:30 AM
08/31/2023 | Alternative | RoutineScheduled | 14-183-038 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | 12:00 AM
08/14/2023 | Alternative | RoutineScheduled | 150-15-0123 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Control Operation","BlowerCompressorAerator Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/08/2023 | Alternative |  | 177-06-0542-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable | 750.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 10:10AM
05/21/2023 | Alternative | RoutineScheduled | SD-14-239 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 08:20 AM
11/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-3"sludge 4"scum/ Microfast ATU-4"sludge (Media is clogged and requires chemical cleaning and pump out)/ Pump Tank-0"sludge/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-432 ETM-28h 20m/ Pump2-416 ETM-27h 22m/ Peak-13/ High level-9/ Installed new end cap for LPD Trench/ No breakout or spongy areas on the LPD Pad Site and dosing properly. Returned on 12/13/2023 for the chemical cleaning and pump out/ Reset the pH level. System returning to normal function. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/30/2023 | Alternative | Routine/Scheduled | 05-174-0271 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - recommend pumpout - effluent screen serviced. Biofilter - peatmoss spent - requires replacing - raked / turned best able. Pump Basin - float sensors, pump and controls operating. DBox - Intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | Dec 30 1899 1:45PM
07/27/2023 | Alternative | Reportable Incident | 159-10-185 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | UV | 450.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped trash tank, aeration tank and pump tank as recommended during last service visit. - aeration tank refilled with fresh water for restart. Found buried wire for pump tank adjacent to septic riser - found to be damaged and will require Electrical to install conduit and pull new wire. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/31/2023 | 06:45 AM
06/02/2023 | Alternative | Reportable Incident | 151-08-0291 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS- Repair - treatment module riser damaged by lawn care. Pumped septic tank empty - replaced effluent screen Pumped pump basin empty - removed and replaced damaged riser sections. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 12:00 PM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Puraflo Peat Moss |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-1" scum-6-8" sludge in Septic tank - 6- sludge trace in Pump tank, Peat was dry and fluffy, turned and broke up peat and it drained. Alarm and pump are operational, float switches respond, Pump has 21545 pump cycles on meter 2103 cycles since last visit 12-2021 . and ran abouit 29.3 hours since last inspection, @ 285.72 Hrs. cleaned effluent filter- | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend adding ball valves. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-557 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | 08:44 AM
05/15/2023 |  | Routine/Scheduled | 550-STS-6632 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | Jan 1 1900 12:15PM
05/25/2023 | Alternative | Reportable Incident | C 800-17-0229 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm and red light on for at least a week. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the UV circuit board, replaced the UV light bulb, and replaced the UV cord. Meet with the pumping company and pumped out. Disconnected the pressure switch and the UV due to the pumping. The timer is set to 3 minutes every 1 hour. Need to go back and hook the pressure switch back on, cut UV on, and perform a drawn down test. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/25/2023 | Dec 30 1899 10:15AM
11/08/2023 | Alternative | Routine/Scheduled | 166-04-043 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 1500 | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [11 empty] | Pumped Out | Replaced peat moss | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/08/2023 | 06:30 PM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/10/2023 | Alternative | Follow-Up | 139-09-0125 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"SludgeScum Accumulation" ,"Distribution Pump Operation"] | ["Control Operation" ,"SludgeScum Accumulation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Dug up buried wedge lid for septic tank to give the pumper (Arthur's Septic) better access. Both tanks were pumped out today. Had owner run water in house to refill septic tank while other repairs were underway. Replaced the wedge lid with a plastic riser and lid to grade for a water tight connection. Properly sealed the buried wedge lid for the pump tank. Sealed a small hole in the long (uphill) side of the pump tank (active infiltration observed) with hydraulic cement. Cleaned out mud, sludge, parts of broken plastic lid and other debris from the pump tank. Added an additional 4x8x16" block to make a proper 16"x16" pump stand (installer had only used 1 block). Removed the two 3/4" lines from end of pump tank. Installed a 4" pvc pipe sleeve through the wall and ran 2" pipe through the wall before reducing it down. Capped both ends of the 4" sleeve with 4x2 Ferncos. Parged around 4" pipe with hydraulic cement. Moved return-to-septic line over to side of pump tank and brought it into the tank through a separate knock-out. Parged and tarred that pipe penetration. Added water to pump tank and ran test cycle. Cleaned small debris from under both solenoid valve diaphragms. All repairs are considered complete. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
06/12/2023 | Alternative | Routine/Scheduled | 166-03-800 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 06:11 PM
09/06/2023 | Alternative | RoutineScheduled | 195-Discharge-19263 North Fork River | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | MULTIFLO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/06/2023 | 12:00 AM
01/27/2023 | Alternative | RoutineScheduled | 061-STS-26121 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/29/2023 | 01:40 PM
10/03/2023 | Alternative | Reportable Incident | 12-125-022 | Dickenson | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | Septic Inc. |  | Michael | Yates | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Other"] | ["Other"] | NO | Septic | Dark Brown | [14 empty] | Pumped Out |  | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/03/2023 | 12:00 AM
01/24/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/23/2023 |  | RoutineScheduled | 179-STS-91626 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 8900.000000 | [] | [] |  |  |  | 7.050000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | 05:20 PM
12/30/2023 | Alternative | RoutineScheduled | 067-STS-38685 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | Modified Extended Aeration |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Total flow to drain fields December 2023 -76,460 gallons. Average 2,731 gallons per day. All aspects of the system are operational. Wasting of settled mixed liquor from the clarifier to the digester and decanting of supernatant from digester are occurring regularly. Digester pumped out on 12-10-2023. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2024 | 07:03 PM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | SD-91-197 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | As previously noted, we recommend replacing the aerator stone. We also recommend replacing the concrete lid on the pump tank and repairing the pump line. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
03/13/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0721 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Tank pumping is required. Filterbed vent pipe is missing from one side of the manifold. The manifold is clogged and needs to be replaced asap. Conduit at house for remote alarm has settled and separated from bottom hub of the LB connector (wires showing). The 4" junction box outside the blower housing is broken (wires showing). Cleaned debris from the blower housing and cleaned the air pre-filter as preventative maintenance. The emergency pump override float switch has failed and needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/08/2023 | 06:43 AM
01/19/2023 | Alternative | RoutineScheduled | 154-05-0606 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Sand Tank | Gravity | Pressure | Discharge | Chlorination | 450.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
09/01/2023 | Alternative | Routine/Scheduled | S 800-18-0027 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | Dec 30 1899 9:45AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommended to homeowner that the sump pump drain is diverted away from the ends of the lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 182-16-0124 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 10/11/2023 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected | Silence function doesnt work on blower panel Lab Normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
03/16/2023 |  | RoutineScheduled | 01-192-214 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 5 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/16/2023 | 12:00 AM
07/28/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-67020 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
06/02/2023 | Alternative | Follow-Up Component Maintenance | 099-06-0253-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank pumped out by others 2 days prior. Degraded peat was removed by hand with shovels/pitch forks and new peat was installed. Peat was purchased at Wrights Ready Mix. Degraded peat was disposed at Spotsylvania Refuse. Cracks in pod, not ideal but since it's a pad site, not super critical yet. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 177-09-0050-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens"] | ["Effluent Screens" ,"Distribution Pump Operation"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | One of the Puraflo modules does not appear to be draining properly. A follow-up visit is planned to evaluate if a repair will be cost effective based on the life of the peat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
02/13/2023 |  | RoutineScheduled | S10-237-0003 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | Discolored | [14 empty] | Inspected | - recommend tank be pumped/cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/17/2023 | 12:00 AM
05/16/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [16 empty] | Inspected | Septic Tank minimal scum, 8" sludge, Pump Tank 10" sludge. Peat Pods peat is in New conditon. Turned peat and looks good, Cleaned Effluent filter. Alarm sounds indoors and pump runs on timers dosing. Floats appear to function. Owner will keep tress and shrubs cut around the peat tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
06/03/2023 | Alternative | Routine/Scheduled | 149-STS-10954 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Siphon | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | Dec 30 1899 9:30AM
11/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | UVis burned up and parts need repaired. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | Dec 30 1899 2:02PM
10/03/2023 | Alternative | RoutineScheduled | 2019-143-0029 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/07/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new hydraulic unit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | Dec 30 1899 12:46PM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/29/2023 | Alternative | Routine/Scheduled | 093-06-0329 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Gravity |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | Dec 30 1899 10:00AM
11/25/2023 | Alternative | Routine/Scheduled | 05-160-0281 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 57.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/25/2023 | 10:30 AM
04/17/2023 | Alternative | Reportable Incident | 061-17-398 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Rebuilt failed compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/23/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  | 600.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] |  | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/07/2023 | 10:15 AM
11/06/2023 | Alternative | RoutineScheduled | 041-STS-260466 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 1750 | 750 | 250 | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Pungent | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | Dec 30 1899 5:00PM
04/25/2023 |  | Initial Visit | 182-11-0262 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Elgin | [6 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | remove roots from dbox and adjust timers | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 12:00 AM
08/24/2023 | Alternative | Routine/Scheduled | 087-STS-6589 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/24/2023 | 10:47 AM
09/08/2023 | Alternative | RoutineScheduled | 2005-143-0267 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [18 empty] | Replaced Blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/05/2023 | Alternative | Routine/Scheduled | 234-16-332 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | Dec 30 1899 2:31PM
09/18/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The Clearstream tank should be pumped out. The timer is set to 1.5 minutes every 1.5 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/18/2023 | Dec 30 1899 4:30PM
02/22/2023 |  | RoutineScheduled | 145-09-0034 | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2000 | Septic Tank Only | Sand Filter | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The effluent filters were both pulled and cleaned. The sand filter was inspected and was in good operating condition. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 09:10 AM
05/16/2023 |  |  | 124-STS-2379 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Distribution Pump Operation","Control Operation","Effluent Screens"] | [18 empty] | -Replaced step 20 pump -Replaced ORENCO control panel -Replaced Aquarium air pump -Replace alarm float -Replaced chlorine and de-chlor tablets | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/05/2023 | 12:00 AM
04/27/2023 |  | RoutineScheduled | 175-03-0881 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Mound | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","Dispersal System Operation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 2"scum/ Microfast-16"sludge 0"scum / Pump Tank-5"sludge 0"scum/ Pump out of the Septic Microfast Tank is required/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-21410 ETM-243891/ Watermeter-1,121,473/ Drip mound zone1 is bleeding out due to unequal dosing caused by faulty zone check valves. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
07/14/2023 | Alternative | Routine/Scheduled | 04-120-0643A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced - recommend pumpout. Treatment Module - media drapes & spray grid serviced. Pump tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 9:30AM
03/03/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced N140 effluent pump & 2" Brass check valve. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/13/2023 | Dec 30 1899 11:23AM
05/26/2023 |  | RoutineScheduled | 179-15-0390-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspections. 39 psi | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
08/09/2023 | Alternative | RoutineScheduled | 182-04-0500 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Control Operation","Auxiliary Filter","SludgeScum Accumulation"] | ["Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Control panel replaced. Septic pumped | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/09/2023 | 12:00 AM
10/17/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Homeowner to have septic/FAST pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 12:00 AM
07/21/2023 | Alternative | Routine/Scheduled | 550-STS-5872 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the septic tank. Changed the filter in the aerator. Replaced the UV light bulb. The Clearstream tank needs to be pumped out. The septic tank needs a 6" x 24" riser and lid (was hit by a lawnmower). The timer is set to 10 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | Dec 30 1899 8:30AM
09/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 |  | RoutineScheduled | 101-07-0080 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/28/2023 | 12:00 AM
02/20/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | arcon 3.LA blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
12/04/2023 | Alternative | Reportable Incident Component Maintenance | 179-14-0372-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed enable float. Replaced failed float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/12/2023 | Alternative | Reportable Incident | 099-14-0094-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | None | Clear | [14 empty] | Inspected | replaced transducer | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 01:00 PM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/18/2023 | Dec 30 1899 8:36AM
06/14/2023 | Alternative | Routine/Scheduled | 06-120-0648A Disc | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Biomicrobics MicroFAST |  | Gravity | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [7 empty] | 06/14/2023 | Sample Chamber | 2.000000 |  | 7.400000 | 594.000000 |  |  | Attached to this report |  |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/14/2023 | Dec 30 1899 2:41PM
11/02/2023 | Alternative | Routine/Scheduled | 093-12-0053 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 10:45AM
03/02/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/05/2023 | Dec 30 1899 11:50AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/03/2023 |  |  | 08-197-176 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/03/2023 |  | 3.970000 |  |  | 1.500000 |  |  | Will be sent separately |  | BOD: 3.97 TSS: 1.50 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | 12:00 AM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | 177-10-0037-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | EcoPod | none | Pump | Gravity | Pad | UV |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced UV bulb. Cleaned air blower filter, need to special order due to filter being different size. Blower 3.85 amps. Hand-131, High Level-160, Override-2. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
07/20/2023 | Alternative | Pump-Out Only | 12-160-0149 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0336-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
08/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
08/17/2023 | Alternative | Reportable Incident | 151-11-0177 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Changed the diffuser in the Clearstream and change the filter in the aerator. Installed an aerator rebuild kit. The septic tank needs to be pumped out and the Clearstream tank needs to be pumped out. The timer is set to 2.75 minutes every 4 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/17/2023 | 03:40 PM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/10/2023 |  | RoutineScheduled | 2015-143-0048 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Delta Ecopod |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/24/2023 |  | 42.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal Repaired broken valve and gauge | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
03/27/2023 |  | RoutineScheduled | 177-STS-88842 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend replacing the O Ring for the spin filter in the headworks box. We removed debris that was clogging the inlet tee. Referred customer to Plumbing Innovators to have the sewar line examined by camera & jetted if necessary. Tanks should be pumped when this work is complete. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
03/06/2023 |  | RoutineScheduled | SWT-04-592 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
12/20/2023 | Alternative | Reportable Incident Component Maintenance | 099-19-0045 SPSA | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Complaint inspection. System on high level due to broken rsv valve outside riser letting water into bot tanks every time it rains. Will send proposal for repair asap. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
07/17/2023 | Alternative | Reportable Incident | 234-15-214 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | Dec 30 1899 8:00AM
07/17/2023 | Alternative | Routine/Scheduled | 550-STS-6756 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | UV | 600.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Processing Tank - media drapes & spray grid serviced, recirc pump serviced. U.V. - bulb and housing serviced. Pump Tank - float sensors, pump and controls operating. Drip Field - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 8:00AM
07/14/2023 | Alternative | Follow-Up | 550-STS-6722 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 7.000000 |  | 1.000000 | [5 empty] | Took BOD and Fecal samples. Replaced the valve box on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/04/2023 | Dec 30 1899 12:00PM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1125 | septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-8890 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 6 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/02/2023 | 12:00 AM
01/18/2023 |  | Reportable Incident | 177-17-0068-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for waste water running out of the tanks. Discharge pump failed. Replaced discharge pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
08/16/2023 | Alternative | Routine/Scheduled |  | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 08:00 AM
05/03/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Drip loop was repaired. System is functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0108-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
02/22/2023 |  | Routine/Scheduled | 136-10-0214 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - ALARM EVENT Primary septic tank - no Riser present - effluent screen serviced. BioFilter - flooded due to pump failure - Peatmoss in POOR condition. Pump Basin - replaced failed pump - pumped system out of alarm. DBox - intact - removed minor root infiltration. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/23/2023 | 07:30 AM
04/28/2023 | Alternative | RoutineScheduled | 05-197-179 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Eco Pad |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/28/2023 | 12:00 AM
02/16/2023 |  |  | 179-13-0259-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
09/23/2023 | Alternative | RoutineScheduled | 019-STS-29347 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | NONE, LPD System |  | Pump | Pressure | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Annual inspection. Flushed all eight (8) low pressure lines. Only a few of the lines had minimal solids flushed out. 10" of accumulated solids in septic tank. 2" of very loose solids in pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 07:03 PM
12/08/2023 | Alternative | RoutineScheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 |  |  | Gravity | Gravity | Mound | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | YES | None | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | 12:00 AM
08/01/2023 | Alternative | Reportable Incident |  | Isle Of Wight | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | System Alarming - Found aeration failure - diaphragms failed. Septic tank - normal level Aeration tank - compressor rebuild conducted - mixing restored Pump Tank - transducer and controls operating. Discharge point clear of debris. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 08/02/2023 | Dec 30 1899 8:00AM
11/29/2023 | Alternative |  | 087-STS-6420 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Other"] | ["Other"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 12:00 AM
03/01/2023 |  | RoutineScheduled | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001682 | Frank | Hogan | 2.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | This is a test report. Please let me know when you get it | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | 02:21 PM
01/25/2023 |  | RoutineScheduled | SP-05-445 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Control Operation" ,"Recirculation Pump" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Float #2 for discharge pump was not showing in board due to bad contact Fixed. Leak on recirc tank inlet riser roots infiltration. Leak on pump tank outlet riser small root. Sheets sagging bad due to age and bad rods, recommend replacing with new style sheets. Will send proposal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-90229 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
01/12/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 01/12/2023 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected | Replaced cracked filter and repaired pump assembly | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
01/04/2023 |  | RoutineScheduled | 15-163-0105 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Aquasafe |  | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | [] | [18 empty] | Septic tank needs pumping . Aquasafe sludge level needs monitoring. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 12:00 AM
07/11/2023 | Alternative | Routine/Scheduled | 05-190-103 | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration Tank - recommend pumpout and refill - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 11:15AM
12/22/2023 | Alternative | RoutineScheduled | 08-184-5007 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 4.500000 | 8.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/02/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Best 1 |  | Pump | Gravity | Trenches |  | 750.000000 | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:01 PM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/18/2023 |  | RoutineScheduled | 11-172-0014A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | Advantex |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | Jan 1 1900 11:40AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/24/2023 | Alternative | RoutineScheduled | 08-174-0010 | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2000 | 1000 | 1000 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | YES | Pungent | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 12:00 AM
03/23/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
01/03/2023 |  | RoutineScheduled | 107-13-0270 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 12:00 AM
03/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
10/01/2023 | Alternative | Routine/Scheduled | 041-STS-261409 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1000 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/01/2023 | Dec 30 1899 9:30AM
08/11/2023 | Alternative | RoutineScheduled | 15-113-047 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation","Disinfection"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 14 - Bio Max tablets installed 4 - Blue Crystal tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/11/2023 | 12:00 AM
04/27/2023 |  | Routine/Scheduled | 228-09-0585A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | Jan 1 1900 2:00PM
12/05/2023 | Alternative |  | 94-184-5001 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/05/2023 |  | 18.900000 |  |  | 6.500000 |  |  | Will be sent separately |  | BOD: 18.9 TSS: 6.50 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
10/05/2023 | Alternative | RoutineScheduled | 061-STS-22021 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | sludge checked, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/30/2023 | Alternative | RoutineScheduled | 181-14-0008 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [16 empty] | Pumped Out | The MicroFast and pump tank were both pumped and cleaned. The blower and spin filters were both cleaned. The effluent screen on the discharge pump was sprayed off. The controls were operating as designed. There were no visible leaks in the drip field. There was effluent returning to the pump tank so the drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 11:00 PM
01/19/2023 | Alternative | RoutineScheduled | SD-96-436 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
04/14/2023 | Alternative | Follow-Up | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 2.000000 | 4000 | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Recirculation Pump"] | ["Recirculation Pump"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 4/10/2023 Pump 6 low amp checked pump, not working replaced contactor pump working 4/11/2023 RT in high level due top pump 6 not working. pumped 4,000 gallons advantage 4/14/23 Dosing tanks in high level, pumped by hand res set drip dosing to turn zone 5 % 6 back on Limed wet areas | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/02/2023 | 07:08 AM
11/02/2023 | Alternative | RoutineScheduled | 18-163-0224 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Level Sensor Operation","Distribution Pump Operation","Effluent Screens"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 12:00 AM
07/19/2023 | Alternative | Follow-Up |  | Culpeper | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","SludgeScum Accumulation"] | NA | [17 empty] | Follow up for chemical cleaning of the Microfast Unit and pump out. Unit now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | Dec 30 1899 5:20PM
05/11/2023 |  | RoutineScheduled | 04-172-0041A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | MicroFAST |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
10/10/2023 | Alternative | Pump-Out Only | 175-03-0838 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Septic and pumping | 1942001330 | Michelle | McKim | 3.000000 |  |  | 1000 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Other"] | NA | [16 empty] | Pumped Out |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/10/2023 | 09:00 AM
11/28/2023 | Alternative | RoutineScheduled | VAG401449 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.590000 |  |  | 0.710000 |  | 11/28/2023 |  | 71.000000 |  |  | 34.300000 |  |  |  |  | System needs to be pumped and then retested. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 11:30 AM
07/24/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-2311 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/24/2023 | Dec 30 1899 1:00PM
09/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [7 empty] | 09/21/2023 | Sample Chamber | 30.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Pump Tank-2"sludge/ No pump out needed at this time/ Controls, pumps, floats and alarms are functioning properly/ Puraflo peat was turned and is in good condition at this time/ Counts: Pump1-13969 ETM-134h 43m/ Pump2-14168 ETM-136h 47m/ Peak-77/ High-60/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Trash tank level was high due to filter being clogged. Cleaned filter and level returned to normal. Recommend pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/23/2023 | Alternative | Routine/Scheduled | 159-12-050 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Cajun Aire ATU |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | During routine service and compressor replacement, noted excess settleable solids. Trash tank and aeration tank pumped empty and serviced. Refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 08:30 AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 4 EZ treat nozzles required replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/01/2023 | Alternative | RoutineScheduled | 067-STS-38739 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | NONE |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Meters - A - 940, B -670, C - 910. Tested both discharge pumps in "HAND", both pumping. Still no gallons pumped to drain field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 07:03 PM
01/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | UV Bulb needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | Dec 30 1899 11:08AM
12/06/2023 | Alternative | RoutineScheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | JEFulbright Septic, LLC | 194200131 | Jason | Fulbright | 1.000000 | 1000 | Clearstream 600DC | Norweco UV Disinfection Unit | Pump | Pressure | Drip | UV | 600.000000 | [] | [] | YES | Musty | Clear | 7.180000 | 5.200000 |  |  |  | 12/06/2023 | Pump Chamber | 1.000000 |  | 0.500000 | 9.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | Dec 30 1899 12:00PM
02/09/2023 | Alternative |  | 101-10-0195 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Charles & Gloria | McSwain | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/28/2023 |  | Routine/Scheduled | 234-14-278 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/28/2023 | Jan 1 1900 11:05AM
11/06/2023 | Alternative | Routine/Scheduled | 18-120-0466AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/06/2023 | Dec 30 1899 1:38PM
12/06/2023 | Alternative | RoutineScheduled | VAG401509 | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/28/2023 | 01:00 PM
03/09/2023 |  | RoutineScheduled | 101-06-0436 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
06/24/2023 | Alternative | RoutineScheduled | 2060-98-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | YES | Musty | Clear | 6.600000 |  |  | 1.800000 |  | 07/03/2023 | Sample Chamber | 3.000000 |  |  | 11.200000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/18/2023 | 12:00 AM
03/09/2023 | Alternative | Follow-Up | 159-01-056 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 2000 | Clearstream |  | Pump | Pressure | Trenches | Not Applicable | 1500.000000 | ["Control Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | Discharge tank was in high level, the old checks didn't seem to be holding. We left to do another job and came back with the parts to install new checks. Re installed the discharge pumps and ran the tank empty multiple times but the tank keeps filling back up. After about 4 pump outs the water level randomly stopped coming up. The eq tank has had water pouring into it the whole time we've been here and have been pumping it down when it goes into alarm. The panels are aged and should be quoted for replacement or the times need to be changed. System was at normal level when we left. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/13/2023 | 08:30 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
12/15/2023 | Alternative | RoutineScheduled | 15-137-0168 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 2.000000 | 1850 | Multiflo |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | 12:00 AM
10/23/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 10:10AM
09/22/2023 | Alternative | RoutineScheduled | 18-160-0048 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1000 | AS 500 |  | Pump | Pressure | Trenches | UV | 450.000000 | ["Other"] | ["Other","SludgeScum Accumulation"] | NA | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 12:20 PM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Multiflo FTB | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
01/11/2023 |  | RoutineScheduled | 179-18-0445-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Effluent Screens" ,"Control Operation" ,"Dispersal System Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Effluent continues to surface in the dispersal area. New aerator, control panel insert, and female plug were installed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
09/15/2023 | Alternative | RoutineScheduled Component Maintenance | 196-05-729 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Installed new Clearstream Diffuser. The aerator and pressure switch are not working and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
07/11/2023 | Alternative | Routine/Scheduled | 157-13-0136 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV light bulb. The timer is set to 2 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/11/2023 | 03:30 PM
01/24/2023 |  | Routine/Scheduled | 550-STS-6614 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/24/2023 |  | 15.000000 |  | 53.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 8:33AM
04/26/2023 |  | Reportable Incident |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced failing DBox with new 8 port concrete DBox. Parged leaking septic tank. Spliced to existing conveyance line. Replaced header lines with 4" PVC. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 06:15 AM
11/30/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0706 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
11/30/2023 | Alternative | Routine/Scheduled | 093-12-0083 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal Level 3" of sludge and 1" of solids Pulled and cleaned filter No signs of infiltration -Discharge/Pump Tank: Normal Level All floats and pump are functioning properly -Peat Moss: Tipping bucket is broken Dispersal trays are functioning properly Peat moss was broken down but raked out good. Customer has 4 bags of Peat moss in his shed from previous Peat change. We added 2 bags to each side. -Distribution Box: Box is deteriorated Lid is broken 3 lines balanced but box is above normal level and water was clear -Drain Field: Drainfield not taking water | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 3:53PM
05/24/2023 |  | RoutineScheduled | 179-STS-91745 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
09/05/2023 | Alternative | RoutineScheduled | 175-14-0172 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Septic Tank to Norweco ATU | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [17 empty] | Septic Tank-8"sludge 2"scum/ Norweco ATU-0"sludge 0"scum/ Pump Tank-3"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-051544 ETM-0017912 On-2.5m Off-6h/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/21/2023 | Alternative | RoutineScheduled | 12-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None |  | 6.500000 | 3.000000 |  | -1.000000 | No tablets | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/20/2023 |  | RoutineScheduled | SWP-02-436 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | As previously noted, the peat has deteriorated and is no longer providing proper treatment. We recommend the peat be replaced or that a different treatment unit be installed. Owner was exploring installation of a different treatment system. We recommend the tanks be resealed when a new treatment system is installed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
09/28/2023 | Alternative | Routine/Scheduled | 800-STS-14992 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | Dec 30 1899 12:05PM
09/08/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20170 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Water level in pump tank was all the way down to the pump intake. Diagnosed and replaced the failed timer float switch. Had the owner run enough water into the tank to verify the pump was not burnt up. Treatment side of Microfast tank has a fair amount of sludge buildup. Recommend a pump-out in late fall. After pumping, owner needs to run a bathtub for about 4 hours to refill the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
08/22/2023 | Alternative | RoutineScheduled | 182-07-0169 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","SludgeScum Accumulation","Dispersal System Operation","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","SludgeScum Accumulation","Dispersal System Operation","BlowerCompressorAerator Operation"] | [17 empty] | Pumped Out | pumped septic and FAST tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 12:00 AM
10/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/23/2023 |  | Routine/Scheduled | 07-120-0324A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | The peat is starting to hold water and turning to mud | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/23/2023 | Jan 1 1900 9:31AM
04/27/2023 |  | Reportable Incident |  | Charles City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | New property Owner - system in alarm condition. Primary septic tank - grade issues - installed lower than Aeration tank, causing high level conditions in septic tank. Recommend pumpout. Aeration Tank - Access riser located Below grade - no mixing present - compressor not operating - broken air supply line. Pump Tank - plumbing has settled - riser installed with "spray foam" recommend replacing. Surge box - plastic - bottom fractured. DBox - plastic - settled - deformed - root clogged. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/01/2023 | Jan 1 1900 7:15AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend bringing risers slightly above grade | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | Dec 30 1899 11:24AM
08/10/2023 | Alternative | RoutineScheduled | 107-03-0565 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles","Other"] | ["Attached Growth Medium","Septic Tank Baffles","Other"] | [18 empty] | Replaced lid. Washed down Advantex. Bio tube filter cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 12:00 AM
10/18/2023 | Alternative | Follow-Up | 175-STS-15038 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 10/18/2023 |  | 8.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | Dec 30 1899 1:00PM
09/08/2023 | Alternative | Reportable Incident | 07-163-0094 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - no alarm on arrival. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 8:30AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 175-96-0226 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
10/05/2023 | Alternative | Routine/Scheduled | 095-STS-5090 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 1" of solids with 7" of sludge -Discharge/Pump Tank 1 (Septic Pump): At normal level Pump and floats functioning properly 1" of sludge -Discharge/Pump Tank 2: At normal level Pump and floats functioning properly Pulled and cleaned pump and disc filter 4" of sludge -Aeration: At normal level Aerator working properly 1" of suspended solids Socks in good shape -Control Panel: Both panels functioning properly Septic pump pulling 5.41amps Aerator pulling 2.01amps Discharge pump pulling 5.41amps -Drip Field: Customer said the field has been failing ever since install, has gotten worse in the areas with less dirt. Said the company who designed it won't get back with him to fix it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 9:31AM
05/17/2023 | Alternative | Routine/Scheduled | 151-94-358 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 04:37 PM
11/02/2023 | Alternative | RoutineScheduled Component Maintenance | SD-02-222 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Peat is worn out and needs to be replaced. Septic tank is about due for pumping and will be done just prior to peat replacement. Pump tank will also be pumped out. That will be a good time to replumb the pump piping to make the pumps accessible without entering the tank (code requirement). Bottom float switch was initially stuck on, needs to be replaced. Recommend adding pvc float collars on a 1" pvc pipe to facilitate float maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
09/18/2023 | Alternative | RoutineScheduled | 128-05-303 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, flushed drip, checked sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/22/2023 | Alternative | RoutineScheduled | 001-STS-92248 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1500 | PURASYS |  | Pump | Gravity | Trenches |  | 450.000000 | [] | [] | NA | [17 empty] | SLUDGE JUDGE OF SEPTIC TANK REVEALED 1-2" FROM BOTTOM. EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 10:30 AM
08/24/2023 | Alternative | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:45 PM
03/06/2023 |  | RoutineScheduled | 179-08-0263-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/29/2023 |  | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Gravity | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/11/2023 | 01:22 PM
12/18/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 9:45AM
12/06/2023 | Alternative |  | 14-192-113 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/06/2023 |  | 14.900000 |  |  | 3.200000 |  |  | Will be sent separately |  | BOD: 14.9 TSS: 3.20 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/06/2023 | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled | 043-STS-33595 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
04/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | EZ Treat |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Recirculation Pump","Control Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Level Sensor Operation"] | YES | None | Clear | [15 empty] | Not in New Kent. Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 12:00 AM
10/20/2023 | Alternative | Routine/Scheduled | 151-11-0056 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3500 |  |  | Pump | Gravity | Pad |  |  | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 06:58 PM
03/14/2023 |  | RoutineScheduled | SR-02-552 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | A significant amount of paint has been washed into the system. There is paint on the Advantex textile media and in all tanks. We recommend power washing the Advantex sheets & pumping the tanks afterwards. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/02/2023 | Alternative | RoutineScheduled | 16-142-0125 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/04/2023 | 12:00 AM
10/11/2023 | Alternative | Initial Visit Component Maintenance | 061-STS-25449 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Startup inspection with the installer, David Day. System already looked at by Robert at M&M Soils. Recirc high level count at 3, low level count at 17. All "R" counts reset to zero. Return to septic line tees into the sewer line near the recirc tank. Return flow is visible by looking inside the clean-out closer to tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/03/2023 |  | RoutineScheduled | 175-16-0234 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
09/11/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-9611 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/11/2023 | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89611 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Zone 2 Solenoid is not opening and the pump is deadheading against the valve. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
07/12/2023 | Alternative | Initial Visit | 550-STS-6834 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 52.000000 |  | 6000.000000 | [5 empty] | Owner called due to an alarm (yellow light, muted it, now light is off). Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream (was stopped up with paint). Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter (paint on screen). The pipe in the Clearstream is backgrading - needs to be addressed and/or fixed. Replaced cracked fitting on headworks. The UV has exposed wires - needs to be addressed and/or fixed. Recommend installing the UV in the pump tank or at least installing risers and lid. There is paint in all the tanks - should be pumped out and cleaned. Appears to be wet around toe of the mound, not sure if it is surface water or mound leaking - need to keep an eye on it. The timer is set to 8 minutes every 2 hours. Took initial BOD and Fecal samples. NOTE : Sample results were high - possibly due to the paint. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/12/2023 | Dec 30 1899 12:00PM
06/07/2023 | Alternative | RoutineScheduled | 08-172-0081A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | MicroFAST |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
03/14/2023 | Alternative | Routine/Scheduled | 093-14-0072 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filer in the aerator. Disconnected the pressure switch on the aerator. The pipe is settled between the house and tank - needs to be addressed. There is a wet spot in the yard in the gravel pad. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Dec 30 1899 12:00PM
06/30/2023 | Alternative | RoutineScheduled |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 09:20 AM
12/07/2023 | Alternative | Routine/Scheduled | 06-177-1036 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | 02:30 PM
08/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | NO | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 3:35AM
11/24/2023 | Alternative | RoutineScheduled | 02-192-142 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/24/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled | 179-18-0350-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Disinfection" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | There is effluent coming to the surface along the far end of the drip mound. There was not enough water to fully test the system. We will plan a follow up visit that allows time to add water to the system, if necessary, & evaluate further. We also noted the riser over the drip pump is leaking at its base. We will recommend addressing this after we understand more about the mound. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/02/2023 | 07:49 AM
04/11/2023 | Alternative | RoutineScheduled | SD-15-16 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
03/13/2023 |  | RoutineScheduled | 033-06-0071-SP | Caroline | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock | Drainfield Solutions | 2705163102 | Michele | Ware | 2.000000 |  | Puraflo | [6 empty] | [] | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Septic Tank replacement is necessary-AOSE information was provided Feb 2022 and March 13, 2023. 4/14/23 - MW sent DF solutions email for an update. Will send NOAV is needed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/12/2023 | 12:00 AM
11/09/2023 | Alternative | RoutineScheduled | 166-17-091 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/12/2023 | Alternative | Reportable Incident | 073-STS-93567 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - backup into residence - septic tank pumped - effluent screen serviced. Found sewer line and inlet baffle full of FOG Sewer line has belly, septic tank is fractured from inlet to mid-seam. New Owner ... AOSS requires annual service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 02:15 PM
11/21/2023 | Alternative | Routine/Scheduled | 196-14-060 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/21/2023 | 06:35 PM
01/05/2023 |  | RoutineScheduled | 09-163-0074 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 9:15AM
04/18/2023 |  | RoutineScheduled | 001-STS-92206 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJICLEAN |  | Pump | Pressure | Mound | UV | 600.000000 | [] | [] | [18 empty] | EVERYTHING WORKING AS IT SHOULD-CLEANED HIGH PRESSURE FILTER | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/19/2023 | 10:00 AM
08/30/2023 | Alternative | RoutineScheduled | 181-06-0301 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 2.000000 | 2500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. No apparent leaks in system or drain field area. Control panel, blower, and alarms functioning properly. System did not need to be pumped. Lids were properly secured | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/16/2023 | 09:25 AM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | 182-07-0342 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 08/17/2023 |  | 16.000000 | [5 empty] | Will be sent separately | Inspected | lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
01/27/2023 |  | RoutineScheduled | 027-STS-16062 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/27/2023 | 12:00 AM
05/04/2023 | Alternative | Reportable Incident | 073-STS-104960 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced distribution box with new 8 port concrete DBox. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 07:30 AM
03/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
12/20/2023 | Alternative |  | 001-STS-92314 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001719 | Eric | Washbon | [9 empty] | [] | [] | [18 empty] | See attached Memorandum Report regarding total nitrogen exceedance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2024 | 12:00 AM
11/08/2023 | Alternative | Routine/Scheduled | 2004-143-0023 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/08/2023 | 09:14 AM
03/07/2023 | Alternative | Reportable Incident | 157-17-0067 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | NO | [16 empty] | Pumped Out | Pump Out Only - No Service Agreement in Place - unknown IF owner has a service provider - unknown if system has been serviced regularly. Homeowner called in for pumpout due to back-up in residence and described system as Conventional! | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/08/2023 | 11:00 AM
05/03/2023 | Alternative | Routine/Scheduled | -STS-15911 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Drip | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 2.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | Dec 30 1899 12:30PM
12/01/2023 | Alternative | RoutineScheduled | Discharge | Pulaski | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - New River | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/01/2023 | 12:00 AM
03/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | ["Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | Zone 2 both air release valve and pipes are broken. Also recommend that all the buckets get raised up above the air release valves so they don't get damaged. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/10/2023 | Dec 30 1899 9:40AM
04/17/2023 | Alternative |  | 132-18-0038 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Clarence | Jordon | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/18/2023 | Alternative | RoutineScheduled | 061-17-217 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | MicroFast Blower panel has a permanent fault - will not alarm. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
12/27/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1250 | Anua/Puraflo |  | Pump | Gravity | Trenches | Not Applicable | 120.000000 | ["Effluent Screens","Level Sensor Operation"] | ["Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [15 empty] | The entire system is in compliance with the health department and approved plans. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 03:00 PM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/24/2023 | Alternative | Reportable Incident | 133-STS-101897 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Repair - VDH permit 166-22-279 - GMP2018-02 Pumped septic tank empty for repair. Installed cannister style effluent screen & riser access to grade. Installed new absorption field as per permit & AOSE Specifications. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | 07:45 AM
03/29/2023 |  | Routine/Scheduled | 234-18-121 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Jan 1 1900 1:20PM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | Dec 30 1899 11:08AM
12/06/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.710000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/09/2023 | Alternative | RoutineScheduled Component Maintenance | 107-18-0068 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 099-10-0022-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment looks more clear than last year it doesn't have that black color in the bottom of tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
03/17/2023 |  | Routine/Scheduled | 2007-143-0093 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 08:45 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
01/18/2023 |  | Routine/Scheduled | 550-STS-6348 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 11:15AM
12/14/2023 | Alternative | Initial Visit Component Maintenance | 179-07-0061-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/22/2023 | Alternative | RoutineScheduled | VAG408161 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | increased ventilation (more holes) in vent pipe. Need to add tablets. No discharge at this time | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/22/2023 | 12:00 AM
07/24/2023 | Alternative | RoutineScheduled | 150-10-0023 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Clearstream |  | Gravity | Gravity | Trenches |  |  | [] | ["Level Sensor Operation","Control Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 12:00 AM
03/06/2023 |  | RoutineScheduled |  | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | rsv CLOG cleaned | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
05/08/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  | 450.000000 | None | None | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 10:55 AM
11/27/2023 | Alternative | Reportable Incident Component Maintenance | SD-02-805 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | ATU alarm. Replaced failed blower, ensured bubbling was taking place in tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
08/21/2023 | Alternative | RoutineScheduled | 12-172-0104A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | Eljen Sandfilter |  | Pump | Pressure | Mound |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
05/12/2023 |  | Routine/Scheduled | 087-STS-6476 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 400 | Fuji |  | Gravity | Gravity | Pad | Not Applicable | 100.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Recirculation Pump"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Recirculation Pump"] | N/A | [17 empty] | Performed routine Fuii maintenance. Replaced compressor filter. System does not currently need pumping out. Next visit planned for on or around 11/01/2023. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | 09:29 AM
06/01/2023 |  | RoutineScheduled | 07-163-0021 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Ecoflo |  | Pump | Gravity | Mound |  |  | [] | ["Attached Growth Medium","Control Operation","Effluent Screens","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 12:00 AM
03/29/2023 |  | Routine/Scheduled | 234-17-434 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Jan 1 1900 11:35AM
10/12/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 8.010000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 03:45 PM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001763 | Jessica | Young | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/25/2023 | 12:04 PM
02/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 4.000000 |  | Septic Tank to 2 Clearstream ATU units | Discharge pump tank | Pump | Pressure | Mound | UV |  | ["SludgeScum Accumulation"] | [] | NA | [17 empty] | Septic Tank-4"sludge 3"scum/ ATU #1-18"sludge 1"scum (Requires pump out)/ ATU #2-3"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Blowers and UV-Light functioning properly/ Controls, pump, floats and alarms functioning properly/ No counts or ETM readings capable on the control box/ No breakout or spongy areas on the drip mound. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/22/2023 | Alternative | Routine/Scheduled | 08-160-0123 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 87.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | 09:30 AM
12/13/2023 | Alternative | Follow-Up | 04-160-0598 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner |  |  | LPD | [6 empty] | [] | [] | [18 empty] | - repaired existing riser (lid and ring) - repaired/upgraded electrical (6x6 box) - replaced valve box cover - installed riser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
09/28/2023 | Alternative | Routine/Scheduled | 149-STS-10849 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/28/2023 | Dec 30 1899 4:27PM
04/13/2023 |  | Routine/Scheduled | 133 07 0092 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 11:30 AM
11/28/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | Dec 30 1899 8:00AM
10/17/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-28697 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drip Field: Flushed and cleaned disk filters. Found no signs of surfacing on dispersal field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 10:28AM
11/27/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.470000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 02:30 PM
05/01/2023 |  | Routine/Scheduled | 550-STS-6646 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | Jan 1 1900 11:40AM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
09/14/2023 | Alternative | Reportable Incident | 17-120-0623A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Septic Pro of Virginia | 1942001780 | Eric | Tambourine | 1.000000 |  | Aquaklear AK6S245C/600 |  | Gravity | Gravity | Trenches | Not Applicable | 360.000000 | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [14 empty] | Pumped Out | Cleaned blower filter, leveled the blower pad, pumped and cleaned treatment tank and dbox. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/25/2023 | Dec 30 1899 12:20PM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0103 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
10/04/2023 | Alternative |  | 179-STS-90260 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
07/24/2023 | Alternative | Reportable Incident Component Maintenance | SWP-03-67 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed effluent pump. Replaced failed pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | SD-07-579 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Completed annual inspection and routine maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System is connected to 36001 and has the same issues. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/20/2023 | Alternative | RoutineScheduled | 075-STS-32075 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 500 | Norweco Singulair |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [6 empty] | approx 12" of crust in trash compartment | [9 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | Dec 30 1899 1:10PM
08/04/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Other"] | ["Other"] | NO | [17 empty] | Service call only: Replaced damaged 30"x12" riser , 30"riser lid. Rewired junction box and tested system. Functioning properly | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was off at time of inspection. It was turned on and appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/31/2023 | Alternative | RoutineScheduled | 133-STS-100582 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["Dispersal System Operation"] | ["Dispersal System Operation"] | YES | [16 empty] | Pumped Out | Replace Distribution box- full of roots | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | Dec 30 1899 4:00PM
01/09/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0038 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Water meter needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | 02:41 PM
03/10/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Jan 1 1900 12:26PM
07/06/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0294 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance | 154-15-0090 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["Disinfection" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
11/14/2023 | Alternative | Routine/Scheduled | 03-160-0565 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 05:00 PM
02/08/2023 |  | RoutineScheduled | 033-06-0507-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
06/05/2023 | Alternative | Pump-Out Only | C 800-16-0105 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Supervised Pump out by Goodmans Septic Service as recommended at last service event. Serviced drip headworks Aeration tank refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | Dec 30 1899 7:15AM
09/01/2023 | Alternative | Routine/Scheduled | 550-STS-6595 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | Dec 30 1899 1:25PM
01/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | Dec 30 1899 11:08AM
12/18/2023 | Alternative | RoutineScheduled |  | Hopewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | filter clog | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
09/19/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV: Flushed and cleaned RSV. Checked and confirmed RSV is free of debris and functioning properly. RSV cage design is known for frequently clogging in other systems -Discharge/Pump Tank: Water level. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Discharge pump has exceeded life expectancy. Noted sound of additional inflow within the discharge tank that is now associated with the discharge pump and drip system or the Advantex system. Conducted a draw down for the discharge pump and found that it's drawing down about 12 gallons per minute. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy. Noted that the programming was set for discharge pump to run in demand dose. Design of system is for discharge pump to run on a timed dose. I reprogrammed the control panel and set discharge times per permit design. This may result to alarm issues that was previously masked by the control panel programming -Drip Field: Noted some minor wet spots but found no signs of surfacing or blow outs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | Dec 30 1899 12:53PM
01/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/14/2023 |  | Reportable Incident |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced degraded dBox with new 8 port concrete DBox. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 10:30 AM
04/12/2023 |  | RoutineScheduled | SWP-00-586 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
04/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Only one zone appears to be functioning. Could not get the system to switch zones for the remote zone valves. Filter flush solenoids do not appear to be functioning as well. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
02/13/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | End caps repaired. System appears to be functioning as designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/19/2023 | Alternative | Routine/Scheduled | -STS-6606 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/19/2023 | 03:31 PM
04/17/2023 |  | RoutineScheduled | SWP-04-172 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 2.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend cutting back the trees growing around the edges of the drainfield to prevent roots from growing into the drainfield lines | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
12/23/2023 | Alternative | RoutineScheduled | 109-15-0283 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 750 | Delta Environmental Products DFSeries |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank with 1" of surface crust. Treatment unit has a 2" solids crust with 0" of solids on the bottom. Cleaned blower air filter. Good aeration and good treatment quality. The septic tank and treatment unit may need to be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2024 | 07:03 PM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping treatment unit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/13/2023 | Alternative | Initial Visit | 159-10-185 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | UV | 450.000000 | ["Control Operation","Disinfection","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Initial Visit - Previous Service Provider = Churchview Septic Service. System alarming - homeowner relates that system failed REI 2 years ago, been limping along waiting for public sewer - service provider not returning calls! Primary septic tank - high level due to discharge pump failure. Aeration Tank - high level - mixing present - compressor serviced. Pump Tank - discharge pump failed - pulling 3 amps - believe head has stripped. U.V. - Salcor - headworks under water - not functioning. High Head P20 pump ordered and scheduled to be installed Friday 07/14/2023. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | 06:30 AM
05/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [7 empty] | 05/10/2023 | Sample Chamber | 20.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | Septic Tank-4"sludge 4"scum/ Microfast-19"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ Pump out required on the Septic-Microfast Tank/ Controls, pump, floats and alarms functioning properly/ UV-Light sleeve cleaned/ Blower air filter cleaned and working correctly/ Counts: Pump-4688 ETM-1171h 21m/ High-13/ Peak-11 On-15m 36s Off-1h 48m/ Watermeter-0,286,875.5/ No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/07/2023 |  | RoutineScheduled | 193-STS-93712 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/14/2023 | Alternative | Initial Visit | 073-STS-96005 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 4.000000 | [7 empty] | Serviced system. Checked the pump and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The alarm lights inside the panel work but the lights on top do not - needs to be addressed and/or fixed. Audible alarm does work. The timer is set to 5 minutes every 1 hour. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | 07:45 AM
10/06/2023 | Alternative | Routine/Scheduled | 136-04-195 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has less than 1" of sludge with 8" of sludge Pulled and cleaned filter -Discharge/Pump Tank: At normal level Pump and floats working properly Has 1" of sludge -Peat Moss: Tipping bucket intact Peat still in good shape Raked out any imperfections From what I can tell the edges of the mound have dried up since Peat was replaced. -Control Panel: Panel working properly Visual and audible alarms working Pump pulling 11.17amps | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 09:52 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator is not functioning. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
01/26/2023 |  | Routine/Scheduled | 234-17-384 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 11:00AM
08/10/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed N137 effluent pump & 3 control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | Dec 30 1899 3:58AM
09/05/2023 | Alternative | Routine/Scheduled | 14-172-0307A | Powhatan | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. U.V. Disinfection - Failed - housing has partially MELTED Pump Tank - float sensors, pump and controls operating. Dbox - intact | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/07/2023 | Dec 30 1899 11:00AM
10/19/2023 | Alternative | Routine/Scheduled | 045-STS-42348 | Craig | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | Dec 30 1899 1:00PM
03/22/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
07/28/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced solenoids in hydraulic unit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/29/2023 | Dec 30 1899 3:58AM
05/03/2023 | Alternative | RoutineScheduled | 154-07-0109 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | As our staff mentioned while onsite, we recommend removing sprinklers from the dispersal area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
06/05/2023 | Alternative | Reportable Incident | 157-10-0188 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Advanced Septic |  | Pump | Gravity | Mound | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Real Estate Inspection. Primary septic tank pumped empty and inspected. Pump Tank - float sensors, pump and controls operating. DBox - plastic intact - Eljen synthetic sand filter present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 07:00 AM
11/03/2023 | Alternative | RoutineScheduled | 019-STS-24187 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT-3 to Trenches |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic tank 6-10" sludge, recirculation zone 7" sludge and discharge zone 10" light trace of sludge. System does not need pumping at this time. Checked floats, alarm and wiring, All Test ok, recir pump pulled 10.8 amps and discharge pulled 11.2. slightly Opened the nitrogen reudction recirculation valve on this visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
11/22/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0111-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
01/31/2023 | Alternative | RoutineScheduled | 154-06-0698 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
01/29/2023 |  | Routine/Scheduled | 053-STS-9933 | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [16 empty] | Recommend Pump out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/29/2023 | Jan 1 1900 12:00PM
06/22/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-89596 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend contacting Pruitt Contracting Group to replace the defective timer enable float in the drip pump tank & to repair the posts that hold the control panels. The Motherboard is not recognizing the push to silence button. The manufacturer is sending us a warranty replacement. We recommend replacing the housing and lid on the lower zone air release valve. 7/18/23 - MW reached out to Ed Scott with EcoSeptix for update. He is working with Orenco to replace the issues with the control panel (under warranty , so no expense to owner). Ed said he will reach out next week as the Orenco POC is on vacation. Ed stated he sends all of his reports to Roger Riggins with Pruitt so he can fix them. Will wait and if need be send an NOAV once Ed revisits. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
12/09/2023 | Alternative | RoutineScheduled | 109-13-0257 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 2000 | Orenco Advantex 2 AX20 |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank - First section - 15" accumulated solids, Second section - 6" accumulated solids. 0" of solids in discharge pump tank. Flushed both treatment unit's spray manifolds. Cleaned recirculation pump solids basket filter. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2024 | 07:03 PM
11/17/2023 | Alternative | RoutineScheduled | 04-163-0286 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Blower replaced 9/20/23 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/20/2023 | 12:00 AM
03/27/2023 | Alternative | RoutineScheduled | 18-160-0106 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | ATL |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation","SludgeScum Accumulation"] | [] | NA | Septic | Dark Brown | [14 empty] | Inspected | - both tanks need to be pumped and cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/13/2023 | 12:00 AM
11/17/2023 | Alternative | RoutineScheduled | 175-12-0184 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast Tank |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 1"scum/ Microfast-8"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower is functioning properly/ Blower control and alarm functioning properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/24/2023 | Alternative | Routine/Scheduled | 093-STS-13843 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash tAnk - recommend pumpout. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Dec 30 1899 7:45AM
01/12/2023 |  | RoutineScheduled | 175-03-0234 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 02:21 PM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/17/2023 |  | RoutineScheduled | ST-02-195 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Effluent level was even with invert of the recirc tank inlet tee. Lowered recirc high level float 2", may do a little more after additional monitoring. Fairly aggressive root growth observed coming in at top seam of Advantex tank near the baffle wall. Recommend that all 4 holly trees be cut down as they are only 5 to 6 feet from edge of tanks. After trees are gone, a repair proposal will be provided to the owners to reseal the recirc tank at point of penetration. Discharge pump is over-sized. Should be replaced with less powerful pump when it fails. Removed roots from d-box and effluent level was below the dial-a-flows. Recommend attempting to reseal the Tuftite box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
09/25/2023 | Alternative | Routine/Scheduled | S-175-14-0019 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 10:18AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/29/2023 | Alternative | Reportable Incident | 073-STS-99995 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced degraded Distribution Box with new 8 port Concrete DBox. Spliced to existing Conveyance Line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 06:45 AM
10/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 4:15PM
10/09/2023 | Alternative | RoutineScheduled | SD-03-368 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic | Microfast | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 07:20 AM
06/27/2023 | Alternative | Routine/Scheduled | 16-120-0489ACR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - Dosing - float sensors, pump and controls operating. BioFilters - peatmoss in fair condition - raked / turned. Pump Basin - discharge - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | Dec 30 1899 11:00AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
06/02/2023 | Alternative | RoutineScheduled | 06-120-0215r | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2250 | 1250 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Distribution Pump Operation","SludgeScum Accumulation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Pungent | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled | 94-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/13/2023 | 12:00 AM
11/20/2023 | Alternative | Routine/Scheduled | 03-142-0459 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level high due to broken pump plumbing. Repaired pump plumbing under warranty. Water level normal upon departure. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Not due for pump out -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy -Distribution Box: Water level normal. Lid is cracked though intact. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | Dec 30 1899 3:10PM
08/28/2023 | Alternative | RoutineScheduled | 182-06-0526 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Dispersal System Operation","Control Operation"] | ["Auxiliary Filter","Dispersal System Operation","Control Operation"] | [18 empty] | replaced blower panel. Need to eliminate ground hog from valve box in drip field | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/28/2023 | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88881 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [5 empty] | 08/30/2023 |  | 29.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Sheets had a layer of sludge on top, looks like dead bacteria as if they had water treatment system or some is on meds. Treatment still ok. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
01/09/2023 |  | Routine/Scheduled | 550-STS-6450 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 1:25PM
09/11/2023 | Alternative | RoutineScheduled | 15-177-1089 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1500 | Aqua Safe 500- 5231 Wilderness Rd | Aqua Safe 500 - 5329 Wilderness Rd 65-1-42 | Gravity | Gravity | Trenches | Not Applicable | 900.000000 | ["Effluent Screens"] | ["Other","Effluent Screens","SludgeScum Accumulation"] | YES | None | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 05:00 PM
06/23/2023 | Alternative | Reportable Incident | 166-14-003 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Readjusted timer float | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled | 107-06-0175 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
11/17/2023 | Alternative | RoutineScheduled | 181-00-0093 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | SEPTIC TANK ONLY |  | Pump | Pressure | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out | THE 1000 GALLON SEPTIC AND 1000 GALLON PUMP TANKS WERE BOTH PUMPED AND CLEANED. THE CONTROLS WERE OPERATING AS DESIGNED. THERE WERE NO VISIBLE LEAKS IN THE LEECH FIELD. THE LPD WAS OPERATING AS DESIGNED. THE LIDS WERE SECURED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 12:10 PM
04/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 139-00-0261 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 10/31/2023 |  | 3.000000 | [5 empty] | Will be sent separately | Inspected | Unable to add riser as no access available | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
04/24/2023 |  | RoutineScheduled | 04-125-055 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/24/2023 | 12:00 AM
01/09/2023 |  | Routine/Scheduled | 234-12-34 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 1:50PM
04/06/2023 | Alternative | Reportable Incident | S-05-111-0156 | Botetourt | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1200 | Biomicrobics Fast |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","BlowerCompressorAerator Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | NA | [16 empty] | Inspected | Follow up Visit- Pump tank appears to be pumping as it should, Replaced the air blower motor and reset the alarm control inside the alarm control panel for the fast unit. Reccomended to seal the buried lids with sand to make it easy to re dig in the future for service. The drip system appears to reach 20psi and both zoners and air relief valves are operational. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/07/2023 | Jan 1 1900 9:30AM
06/01/2023 | Alternative | Reportable Incident Component Maintenance | 177-11-0011-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Discharge pump tank in high level due to clogger spin filter plus clogged pump intake, cleaned both and tested gpm to both zones. Recommended to minimize water usage for the next 24 hours to aloud system to catch up. System most likely will need pump out by the end of the summer, will send proposal for pumping recirc tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
12/11/2023 | Alternative | RoutineScheduled | 2018-143-0045 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/10/2023 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Z140 effluent pump, 2" brass check valve & 4 control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/03/2023 | Alternative | RoutineScheduled | 05-160-0344 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | - replaced pump, completed annual inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 12:00 AM
01/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/08/2023 |  | RoutineScheduled | 021-STS-35879 | Bland | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/08/2023 | 12:00 AM
08/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
12/13/2023 | Alternative | Routine/Scheduled | 127-STS-34867 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 1:00PM
12/27/2023 | Alternative | RoutineScheduled | 132-19-0023 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation","Auxiliary Filter"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
02/01/2023 |  | Routine/Scheduled | NYII-B9RMWK | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | Jan 1 1900 2:30PM
02/22/2023 | Alternative | RoutineScheduled | 150-05-191 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | 12:00 AM
02/16/2023 |  | RoutineScheduled | SWP-04-629 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | A new pump & float installed. The pump tank was pumped to facilitate repair. The peat has settled and is showing signs of age. It is likely that peat replacement or the installation of a different treatment system will be recommended in the near future. We recommend removing the pine trees around the Puraflo modules to prevent root intrusions into the peat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/30/2023 | Alternative | Routine/Scheduled | 234-16-135 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | Dec 30 1899 1:55PM
05/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Effluent Screens" ,"SludgeScum Accumulation"] | ["Effluent Screens"] | YES | Musty | Clear | [5 empty] | 05/25/2023 |  | 18.000000 |  | 1600.000000 |  |  |  | Will be sent separately | Inspected | Recirculation tank needs pumping. EZ Treat UV units need repairing & bulbs & plugs. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Dec 30 1899 12:05PM
12/06/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | [8 empty] | 600.000000 | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
04/11/2023 |  | RoutineScheduled | 179-15-0179-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. N137 pump was not pumping enough to dose field, replaced pump with new CPE5-12 pump. 31.3 gpm on new pump, 8.13 amps. New run time 4m49s to get rid of 150 gallon dose. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
12/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 12/12/2023 |  | 5.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0108-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media showing its age mostly likely will need replacement next year. Will check next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
08/09/2023 | Alternative | RoutineScheduled | 175-15-0457 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [7 empty] | 08/09/2023 | Sample Chamber | 6.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | BOD is in the permitted limits, the Fecal test is not/ Septic Tank-6"sludge 2"scum/ Microfast-4"sludge/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ UV-Light sleeve cleaned, light not burned out/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-1545 ETM-518h 16m/ Peak-19 ETM-94h 33m/ High-0/ Watermeter- 0,254,266.81/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled | 109-08-0457 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Effluent filter installed or maintained | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Septic alarm monitoring alert me to a development in the system and suspected float switch issue. Owner open the junction boxes to find settling had occurred and pulled the wires taught to the extent that repair was unable. The owner then ran new wiring to the tank and retested the system. I visited for a moment when he was working on it. Since then the alarms have ended and he repaired it. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/21/2023 | 04:30 PM
08/04/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-21231 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Alarm was muted on septic control panel. No wires run from the pressure switch to the control panel, so no alarm when the blower fails. Also no wires run from the Salcor uv, so no alarm when lamp burns out. Installer did not use watertight flexible conduit (as per Salcor instructions). Instead, a bare uf cable was routed inside the Salcor control box through an over-sized hole and the circuit board/ ballast are now showing signs of corrosion. Salcor control box is inside the pump tank (very humid environment) so that the green power led is not readily visible. Replaced uv lamp as preventative maintenance and rinsed off the sleeve. Checked the pump intake, cleaned the spin filter, and then ran a test cycle. Unfortunately, this is a continuous flush drip system (no flow meter), so measuring the drip rate with any degree of accuracy is impossible. Drip rate and flush rate are critical measurements to determine the health of the drip tubing: high drip = possible break in the line/ fitting or bad emitter, low drip = possible clogged emitters; low flush rate = possible crimped tubing. System was allowed to pressurize, both ball valves then closed (no flushing), and tape measure used before and after 2 min run time. Return line pressure was less than 50 psi during the test, so a flow meter could be added for testing purposes (drip and total flow). Ball valves were then cracked open and adjusted to allow for adequate filter and field flushing. Atu diffuser was replaced as preventative maintenance. Effluent was a little cloudy in the atu, but reasonably clear at the outlet end of pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/13/2023 |  | RoutineScheduled | SWP-04-206 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots growing in sample box, removed and sealed inside and out plus added root destroyer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
12/29/2023 | Alternative |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | Both monthly December report and Semi-Annual MW reports are attached | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
07/26/2023 | Alternative | RoutineScheduled | 159-15-176 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/29/2023 | Alternative | RoutineScheduled | SD-06-79 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["SludgeScum Accumulation","Attached Growth Medium"] | ["SludgeScum Accumulation","Effluent Screens","Dispersal System Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 12:00 AM
03/08/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Puraflo | n/a | Pump | Gravity | Trenches | Not Applicable | 330.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 02:30 PM
04/06/2023 |  | RoutineScheduled | 107-07-0586 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Drip field located on neighboring property. Blower running hotter than normal/elevated level in FAST | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled | 181-01-0142 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The blower and spin clean filters were both pulled and cleaned. The controls were operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | 10:05 PM
10/16/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | Dec 30 1899 2:45PM
10/12/2023 | Alternative |  | 179-STS-92194 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/30/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Best1 |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Effluent Screens","Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Septic zone 8"Scum layer & 5" Sludge in septic zone, Reduce FOG (Fat oil and Grease input in septic system for improved operation. Treatment tank 10" sludge, Discharge zone 10" sludge and Pump Tank 8" sludge. Cleaned Effluent Filter brush, cleaned Blower filter and cleaned spin filter. Pump count 5481 vs 4309 (1,172 cycles for the year)Pump run time meter11654 min vs 9427Min last year (2,227 min or 37.1 hours for the year total) HLA 53 secondary count 146. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 09:30 AM
11/02/2023 | Alternative | RoutineScheduled | 185-STS-17513 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/02/2023 | 12:00 AM
03/09/2023 | Alternative | RoutineScheduled | 023-STS-42917 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Western Virginia Water Authority | 1942001145 | Michael | Doss | [9 empty] | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 03/09/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | Jan 1 1900 5:45AM
04/17/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Chlorination |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | added tablets and riser to primary | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
01/03/2023 |  | Reportable Incident | 175-17-0388 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced control head UV unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
01/30/2023 |  | Routine/Scheduled | 136-97-0786 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump tank - float sensors, pump and controls operating. BioFilter - 4 modules - Peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 07:45 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/05/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0469 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/18/2023 | 08:36 AM
03/14/2023 | Alternative | Pump-Out Only | S 800-19-0037 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Pumped septic tank empty for confined space entry. Reparged seams and appurtenances to stop leakage. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/16/2023 | Dec 30 1899 7:15AM
04/10/2023 |  | RoutineScheduled | 015-STS-333216 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
08/03/2023 | Alternative | RoutineScheduled | 182-16-0094 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 12:00 AM
10/23/2023 | Alternative | Reportable Incident | S 093-19-0058 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Ez treat. Found septic tank flooded, everything else was normal level. St filter was clogged, let system get back to normal level before we left and got customer to flush, everything came through clear. Alarm call | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 2:29PM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-92002 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. 20psi. Slimy stuff everywhere in system something being used in the house that's causing it. Swreiter still need replacement. Flush was slower this year will check next year if it is the same next year we will do a bleach flush. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
01/30/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
07/25/2023 | Alternative |  | 10-125-157 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/25/2023 |  | 9.490000 |  |  | 21.600000 |  |  | Will be sent separately |  | BOD: 9.49 TSS: 21.6 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/25/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
12/28/2023 | Alternative | Follow-Up Component Maintenance | 175-17-0435 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 12/21/2023 |  | 13.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
02/09/2023 | Alternative | Follow-Up | 154-10-0053 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Biomicrobics Microfast .5l |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["SludgeScum Accumulation"] | [17 empty] | Pumped Out | Septic and Treatment Unit Pumped | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/09/2023 | 10:00 AM
03/22/2023 |  | RoutineScheduled | 179-06-0174-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots starting to grow inside septic tank outlet riser, removed. Recommend to seal from outside. Will send price for repair. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
06/01/2023 |  | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [9 empty] | Control Operation | Control Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 12:41 PM
11/20/2023 | Alternative | Routine/Scheduled | 151-11-0172 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Ecoflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 06:49 PM
04/18/2023 | Alternative | RoutineScheduled | 07-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/18/2023 | 12:00 AM
02/28/2023 |  | RoutineScheduled | 177-09-0102-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The Monster Box lid appears to have been damaged by a lawn mower and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
05/24/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Blower replaced. Riser and lid installed. Heavy scum layer (tank pumped) | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/24/2023 | 12:00 AM
03/31/2023 |  | Routine/Scheduled | 234-17-345 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | Jan 1 1900 12:45PM
11/17/2023 | Alternative | RoutineScheduled | 14-163-0015 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream | [6 empty] | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 12:00 AM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-89836 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Roots are growing through the seals of the distribution box. We removed what we could by hand. We recommend excavating by machine and resealing and/or replacing the seals. Earlier in the week, the owner was contacted by a neighbor regarding odor from the septic system. We found no evidence of odor and the system functioning normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
08/14/2023 | Alternative | Routine/Scheduled | 157-02-043 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream, cleaned the filter in the aerator, and changed the filter in the aerator. Changed the diffuser in the Clearstream. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 04:30 PM
12/12/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0029-SWT | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Owner had alarm due to tripped breaker from pump spiking high amperage. New pump was installed on 15 Dec 23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
12/22/2023 | Alternative | RoutineScheduled | 2018-143-0026 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/03/2023 |  | Routine/Scheduled | 234-18-242 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | Jan 1 1900 11:15AM
08/29/2023 | Alternative | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Fuji |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - normal level - mixing present - nitrogen return adjusted - compressor serviced. PUmp Tank - float sensors, pump and controls operating. DBox - intact - hairline crack in bottom noted! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 07:30 AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Two lateral ends are broken. Homeowner has scheduled repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/15/2023 | 06:51 AM
10/26/2023 | Alternative | Follow-Up | 151-12-0167 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Replacement of Ecoflo Biofilter - includes: - Purchase & delivery of new Biofilter (specialty peat moss) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 07:56 AM
05/22/2023 | Alternative | RoutineScheduled | 137-18-052 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment crystal clear. HL 9, LL 15, OVERRIDE 3. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity |  | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | 7.100000 | 9.100000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 09/15/2023 | Dec 30 1899 2:41PM
10/26/2023 | Alternative | Reportable Incident | 136-16-0045 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV ballast. The septic tank needs to be pumped out. The timer is set to 2 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/26/2023 | 10:00 AM
08/23/2023 | Alternative | Routine/Scheduled | 18-137-0195 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Orenco Advantex |  | Pump | Pressure | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Cleaned effluent filter and flushed manifold. System appears to be operating normally. Averaged. 5 overrides per day. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | Dec 30 1899 1:26PM
07/27/2023 | Alternative |  | 03-197-151 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/27/2023 |  | 11.000000 |  |  | 7.200000 |  |  | Will be sent separately |  | BOD: 11.0 TSS: 7.20 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 12:00 AM
04/24/2023 | Alternative | RoutineScheduled | 159-08-134 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Ecoflo |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:00 AM
04/07/2023 |  | Routine/Scheduled |  | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration Tank - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | Jan 1 1900 8:30AM
11/16/2023 | Alternative | RoutineScheduled | 04-135-3003 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | MONTGOMERY SANITATION SERVICES INC | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | Pumped/cleaned septic tank; septic system is not functioning at this time as there are components that are recommended to be repaired/replaced or drainfield repairs/upgrades are needed. - LPD drainfiled giving customer trouble. Will need further inspection of system. - Customer is working on system himself. - Tank is cracked on the bottom and side of the tank. - Customer wants someone to look at his system 12-8-23 Customer decided to wait to sign up for required maintenance until system is functional, without maintenance agreement MSS Inc unable to proceed with inspection or any repairs | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/19/2023 | 12:00 AM
03/16/2023 |  | Initial Visit | 199-STS-5011 | York | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Repaired the air line assembly. Ran the wires to hook up the pressure switch on the aerator. Replaced the UV light bulb. The septic tank needs to be pumped out. The timer is set to 2 minutes every 3 hours. Did not take samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/16/2023 | Jan 1 1900 11:00AM
08/04/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 0 scum and very little sludge in septic tank. filter is clean. peat moss looks recently changed. pump tank is clean, All alarms, floats and pump is working. Everything looks good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 11:00 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/26/2023 |  | RoutineScheduled | 179-STS-89884 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Bottom zone looks wet but inspection was done after rain, gallons per minute are rigth. will check next visit. RECIRC: HL 1, LL 11, OVERRIDE 146. DISCHARGE: HL 5, LL15, OVERRIDE 5. "R " counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
12/05/2023 | Alternative | RoutineScheduled | 139-04-0265 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 11:00 AM
09/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Bio Tank | Time does | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 |  | RoutineScheduled | SWP 97-210 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation"] | ["Dispersal System Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
01/10/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
06/01/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
01/24/2023 |  | Routine/Scheduled | 234-14-232 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 12:10PM
03/10/2023 | Alternative | RoutineScheduled | 05-160-0344 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 |  |  | 3.000000 | 1100 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Other"] | [] | YES | Septic | Cloudy | [14 empty] | Inspected | Pump is not working, recommend pump service to evaluate and complete repair(s) | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/29/2023 | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
10/17/2023 | Alternative | Initial Visit |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 14.500000 |  | 2.000000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the mesh screen in the spinfilter. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 5 minutes every 1 hour 55 minutes. Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 3:45PM
06/02/2023 | Alternative | Reportable Incident | 175-09-0496 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Distribution Pump Operation"] | ["Dispersal System Operation"] | [18 empty] | Alarm Service call only: Replaced faulty STEP-20 pump, counts-45203 ETM-679248. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled | 109-15-0058 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Musty | [15 empty] | Inspected | Sludge levels-Trace scum layer, 8" Sludge in Septic tank - Treatmeant tank 36" sludge at dischagre -- Pump Tank 10" Sludge, Pump Run time 172hrs 47 min vs 141 hrs 54 min. last year & 2637 cycles vs 2155 Cycles last year, High level 8 Secondary count 110 Power failure 35. Goulds effluent pump- Runs when called. Clear Effluent on top. cleaned air filter. Flushed system. Drip Drain field appears fine. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
07/28/2023 | Alternative | RoutineScheduled | 09-173-089 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Norweco |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | Dec 30 1899 11:30AM
03/20/2023 | Alternative | Routine/Scheduled | 151-05-102 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/21/2023 | 07:15 AM
05/08/2023 |  | Initial Visit | 165-STS-333254 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Drip |  |  | ["Auxiliary Filter","Dispersal System Operation","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","Dispersal System Operation","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled | 115-02-0457 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | [15 empty] | Inspected | Sludge level- minimal Scum & 6" Sludge in Septic tank. Pump tank had trace fine sludge. Pump Runs good after testing. Minor leak at union adapter in pump tank due to age as noted last year. Tipping tray was good. Peat shows its age and is moist and clumped with little use and had no standing water. Shows signs of breakdown due to normal age. Turned, raked and broke up peat in all 4 quadrants. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | 2035-12-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | 7.500000 | 4.400000 | [11 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 107-15-0252 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 09/21/2023 |  | 71.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
10/18/2023 | Alternative | Routine/Scheduled | 05-177-1234 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 11:00 AM
11/28/2023 | Alternative |  |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Battletown Environmental Consulting, LLC. | 1942001135 | Robert | Charnley |  |  | Sand Filter |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium","SludgeScum Accumulation","Effluent Screens"] | YES | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/08/2023 | 12:00 AM
08/21/2023 | Alternative | Routine/Scheduled |  | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Advanced Septic |  | Pump | Pressure | Drip | UV | 450.000000 | Dispersal System Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service - AquaSafe ATU Trash tank - normal level Aeration tank - normal level - mixing present - compressor serviced. U.V. - bulb and housing serviced. PUmp Tank - float sensors, pump and controls operating. Hydraulic splitter Valve - serviced - appears to be camming properly. Drip Field - headworks serviced - lowermost zone has surfacing - been that way from day one due to hydraulic overload from zones 1 & 2 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | Dec 30 1899 6:45AM
05/19/2023 | Alternative | Routine/Scheduled | 136-07-0469 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tnak - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 02:00 PM
10/18/2023 | Alternative | RoutineScheduled | 015-STS-337630 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
08/29/2023 | Alternative | Routine/Scheduled | 234-14-71 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 8:40AM
02/13/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | End caps repaired. System appears to be functioning as designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/20/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS repaired air release valve and cleaned Advantex spray heads. Effluent pump had failed. The system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/11/2023 |  | RoutineScheduled | 179-09-0110-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The peat is beginning to deteriorate. It may stop providing treatment in the next year or two. When that occurs, you can replace the peat, or you may wish to consider a different alternative treatment system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Blower was no connected and has not been for a while. due to no treatment occuring sludge level within tanks is high. Need to pump everything and have a fresh start when blower is reconnected. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
12/04/2023 | Alternative | Initial Visit | 124-STS-2379 | New Kent | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | The Norweco UV is not wired correctly and should be relocated into the pump tank on the inlet side - (would need a EZ Set flat ring, 6" riser, and lid). The aerator should be raised out of the ground. Airline is leaking by the aerator - fittings are too low. Fixed the timer override in the pump tank but still no high level alarm. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/04/2023 | 12:00 PM
09/18/2023 | Alternative | Reportable Incident | 136-16-0139 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Customer stated alarm light was on and didnt hear the air pump opened system and found at normal level Pulled and cleaned weir found Diaphragms are broken for air pump quoted estimates and Brain approved to rebuild air pump and replace diffuser. Rebuilt air pump and replaced diffuser. Tested and confirmed that all components are functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 02:32 PM
05/12/2023 | Alternative | RoutineScheduled | SD-12-05 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1200 | septic | BEST 1 ATU | Gravity | Gravity | Discharge | Chlorination |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/06/2023 | 07:55 AM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
01/17/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.450000 |  |  |  |  | 01/17/2023 |  | 130.000000 |  |  | 46.200000 |  |  |  |  | IES will revisit to determine the cause of the high results. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/14/2023 | 08:00 AM
03/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 | Alternative | RoutineScheduled | 04-160-0398 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | EcoFlow STB 650 |  | Pump | Gravity | Trenches | Not Applicable | 300.000000 | ["Attached Growth Medium","Effluent Screens"] | [] | NO | [17 empty] | System needs peat replaced and effluent screens replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/24/2023 | 12:00 AM
04/04/2023 |  | RoutineScheduled | 175-17-0114 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | 7.100000 | 12.100000 | [11 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
09/26/2023 | Alternative | Routine/Scheduled | 157-13-0067 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal Level 10" of sludge and 1"of solids Pulled and cleaned filter No signs of infiltration -Discharge/Pump Tank: Normal Level All floats and pump are functioning properly -Peat Moss: Peat moss is very compacted and has water ponding on it. Raked out Peat moss into muddy consistency -Control Panel: 120v into panel All audible and visual alarms are functioning properly Pump pulled 5.36amps Panel is Aged -Distribution Box: Plastic distribution box about 5" below grade in good condition at normal Level with 2 lines balanced and taking water All seals are intact -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 01:18 PM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/26/2023 |  | RoutineScheduled | ST-05-201 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend scrubbing the Advantex sheets & pumping the tank at your next inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/16/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","SludgeScum Accumulation"] | [18 empty] | Service call only: Chemical cleaning and pump out of the Septic- Microfast Tank. Reset pH after cleaning. Media is clear now | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/18/2023 | Alternative | RoutineScheduled | 057-STS-94515 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 1,000 | PuraSys GeoMat |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation","BlowerCompressorAerator Operation"] | ["SludgeScum Accumulation","Level Sensor Operation","Effluent Screens","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | NA | [6 empty] | Gravelless trench; no crust accumulation, recommend pumping in 3-4 years | [9 empty] | Inspected | No crust, recommend pumping in 3-4 years | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 01:15 PM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
11/01/2023 | Alternative | RoutineScheduled | 98-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/23/2023 | Alternative | RoutineScheduled | SD-02-374 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic/trash | microfast | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear |  | 8.400000 |  | 1.010000 |  | 04/23/2023 | Sample Chamber | 2.000000 | 0.000000 |  | 11.600000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/11/2023 | 09:30 AM
11/09/2023 | Alternative | Routine/Scheduled | 157-17-0038 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal level 20 in of sludge 1 in of solids No signs of infiltration Recommend pumping -Discharge/Pump Tank: Normal level Less than 1 in of suspended solids Tested floats and pump all working as should All plumbing intact and pump moving water properly No signs of infiltration -Aeration: Normal level Pulled and cleaned aspirator Pulled and cleaned bio kinetic filter and housing All working as should No signs of infiltration 14" of suspended solids Recommend pumping and refilling -Control Panel: 120 volts coming in all visual and audible alarms functioning properly Discharge pump pulled 6.85 amps Aspirator pulled 4.3 amps All components working as should -Distribution Box: Unable to locate due to heavy brush and lack of visibility -Drain Field: Unable to locate due to heavy brush and lack of visibility | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 02:03 PM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0065 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-87654 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Disinfection" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Disinfection" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced uv bulb. 39 psi. RECIRC: HL-8, LL-22, OVERRIDE-54. DISCHARGE: HL7, LL-10, OVERRIDE-0. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
02/22/2023 |  | RoutineScheduled | VAG401999 | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1000 | Septic tank only | Re-circulating sand filter | Pump | Pressure | Discharge | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | There was no discharge at time of service. Chlorinator and de-chlorinator contained tablets. Wetlands plants present and sufficient mulch available to prevent ponding or effluent. No sand filter ponding or buildup. Effluent pipe structurally sound. Sign posted at discharge point. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 08:45 PM
01/12/2023 |  | Routine/Scheduled | 04-142-0408 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 7:15AM
12/14/2023 | Alternative | RoutineScheduled | 150-16-0063 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/14/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced D80 compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/17/2023 | 12:44 PM
07/19/2023 | Alternative | RoutineScheduled | 015-STS-335572 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [18 empty] | Baffle cleaned. Placed proper screws in lids. Recommend spin filter for drip | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
04/12/2023 | Alternative | Pump-Out Only | 04-177-1322 | Pulaski | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Ecoflo (peat moss) | [6 empty] | [] | [] | [17 empty] | Pumped Out | - arrived onsite and found that system is Ecoflo - pumped and cleaned septic tank - filter needs to be replaced and alternative inspection needs to be completed - customer does not want to proceed with required maintenance | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 12:00 AM
01/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation","Level Sensor Operation","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles"] | NA | [17 empty] | Has 2 broken air release valves. Filter housing filter cracked and Peak float not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/31/2023 | Dec 30 1899 3:30PM
03/13/2023 |  | RoutineScheduled | 02-197-A6 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/13/2023 | 12:00 AM
02/02/2023 | Alternative | Routine/Scheduled | 061-STS-21336 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | EZ Treat Sandfilter | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 01:18 PM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-02-602 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Inlet wedge lid leaks on pump tank and septic tank. Drain field is overgrown and needs to be cleared. Pod 2 was full of roots. Proposal to be sent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/07/2023 | Alternative | RoutineScheduled | 157-15-0103 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Aquaworx |  | Pump | Gravity | Mound |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 12:00 AM
06/21/2023 | Alternative | Reportable Incident | 103-STS-106344 | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | Distribution Pump Operation | NO | [16 empty] | Pumped Out | AOSS - Initial Visit - ALARM Event - Owner wanted NOTHING done other than to get the pump operating - no service conducted - no service agreement in place. Pumped pump tank empty to access pump and components. Replaced discharge pump only ! NO OTHER SERVICE CONDUCTED> | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/22/2023 | 01:15 PM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | EZ treat unit might need servicing in the near future | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
12/01/2023 | Alternative | RoutineScheduled | 2100-05-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Discharge | Chlorination |  | ["Attached Growth Medium","Disinfection"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-6"sludge 1"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Puraflo Peat turned and is in good condition/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-0034962 ETM-014347/ Need to add Chlorination and Dechlornation tablets (Owner informed) Counts: Pump-0034962 ETM-014347 On-62s Off-2h | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/31/2023 | Alternative | RoutineScheduled | 151-11-0091 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service, LLC | 1942001034 | Kent | Cuthbertson | 4.000000 | 45000 | 15000 | 15000 | Pump | Gravity | Trenches | UV | 19513.000000 | ["None"] | ["None"] | YES | [8 empty] | Sample Chamber | [6 empty] | Attached to this report |  | This is a 0.05 MGD waste water treatment facility that discharges into two separate drain fields. Samples are taken weekly IAW VA Sewage Regulations and are attached. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 01:15 PM
01/31/2023 |  | RoutineScheduled | 17-100-0507 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 12:00 AM
05/04/2023 |  | RoutineScheduled | 107-19-0120 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | NA | [7 empty] | 05/04/2023 |  | 105.000000 | [5 empty] | Will be sent separately | Inspected | Repaired float issue and timers | This AOSS should now return to normal function after having provided the above state routine maintenance | 06/21/2023 | 03:35 PM
09/08/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-01-163 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media looking dryer this year customer said only 2 people living in the house now, fluffed it and still has little fiver so can go 1 more year but recommend replacing as soon as they can afford it (customer say he's saving up for it already). Proposal has been sent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
01/10/2023 |  | Routine/Scheduled | 228-19-0001 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 9:45AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Advantex should be pumped and manifold needs to be cleaned to function properly. Air release valve in the field is broken and there is effluent surfacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
01/30/2023 |  | RoutineScheduled | 177-14-0086-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Advised owner of tree growth recommended for removal on lower portion of the dispersal area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
05/08/2023 |  | RoutineScheduled | 177-STS-87266 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Disinfection" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Disinfection" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Installed a new recirculation pump - Orenco PF300511 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-11-0013-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 07:22 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
01/10/2023 |  |  | 2005-143-0251 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
12/14/2023 | Alternative | RoutineScheduled | VAG408061 | Rockingham | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.610000 |  |  |  |  | 12/14/2023 |  | 147.000000 |  |  | 32.100000 |  |  |  |  | Sludge level at 70%. System needs to be pumped. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 12/28/2023 | 02:00 PM
04/13/2023 |  | Routine/Scheduled |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - normal level - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 9:00AM
01/24/2023 |  | RoutineScheduled | 17-160-0126 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | Aqua Safe ST 750 |  | Gravity | Gravity | Trenches | UV | 250.000000 | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | [18 empty] | Replaced blower, will replace UV light as soon as it is delivered, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | 12:00 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/15/2023 | Alternative | Reportable Incident | 193-STS-102259 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Microfast. Found system in Alarm. Discharge in high level. Customer said they lost power the other day for a little and a couple hours later the alarm came on. I found that the pump breaker was tripped. I was able to dose the tank out of alarm and told them not to use large amounts of water for a couple days | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 01:16 PM
11/22/2023 | Alternative | Routine/Scheduled | 093-09-0176 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 15" of sludge and 6" of solids, customer approved to be pumped out. Riser has root intrusion, customer approved replacement -Discharge/Pump Tank: At normal level Customer approved to replaced leaking riser, aged floats and dated plumbing. Tank has 2" of sludge -Aeration: At normal level Customer approved to have it pumped out with the septic tank. -Air Pump/Blower: Air pump was not working when I arrived, customer approved to replace it. -Control Panel: Discharge alarm box/ control panel working properly -Drain Field: Not sure where drainfield is, need to request permit for next year 11/28: -Supervise Pump out and Refill -Installation of 6"-12" Riser on the Septic Tank -Installation of 18" Riser on the Pump Tank -Installation of a Fuji Pump -Installation of 2 new Floats Installation of a Float Tree Assembly to secure Floats -Installation of a Plumbing Kit | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/06/2023 | Dec 30 1899 8:51AM
07/10/2023 | Alternative | Routine/Scheduled | 147-16-0055 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/10/2023 | Dec 30 1899 2:55PM
03/15/2023 | Alternative | RoutineScheduled | 159-11-160 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
01/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-10"sludge 3"scum/ Microfast-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump1-435 ETM-14h 42m/ Pump2-426 ETM-14h 27m/ Peak-10/ High-9/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled | 10-173-069 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Advantex |  | Pump | Gravity | Discharge |  | 450.000000 | ["Effluent Screens"] | ["Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | Dec 30 1899 11:30AM
08/20/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/20/2023 | Dec 30 1899 9:00AM
05/08/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  | 450.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:20 PM
12/11/2023 | Alternative | RoutineScheduled | 109-08-0304 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Acres of Virginia, Inc. |  | Melvin | Collins | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/12/2024 | 12:00 AM
05/11/2023 |  | Pump-Out Only | 234-17-304 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/11/2023 | Jan 1 1900 11:50AM
12/11/2023 | Alternative | RoutineScheduled Component Maintenance | SWP 97-210 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"Effluent Screens" ,"Dispersal System Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Owner recently experienced back up due to clogged effluent filter that did not have an access riser. We strongly recommend adding a riser to the outlet of the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
03/21/2023 |  |  | 06-120-0441A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Septic | Dark Brown | 4.000000 |  | 4.000000 | [13 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/21/2023 | Jan 1 1900 12:30PM
01/10/2023 |  | Routine/Scheduled | 08-142-0095 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Trenches | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Cleaned air filter. Checked trash tank. System appears to be operating normally. Ct 26758, etm 23876, hl 104, LL 40, ovr 1339 risers still need to be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 11:43AM
05/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/26/2023 | Alternative | RoutineScheduled | 12-152-A1 | Lee | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/26/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-90062 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
04/16/2023 | Alternative | Routine/Scheduled | 149-STS-10403 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | Dec 30 1899 10:30AM
03/31/2023 |  | Reportable Incident | 234-15-259 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced pump relay, timer, 20 AMP breaker, Timer enable float, alarm float and override float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Jan 1 1900 9:00AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There are four small trees planted near the end of the lines. Advised homeowner of potential issues and recommended moving them. Lower corner of the field on the house side appears to be evenly nitrified. Recommend homeowner monitor for changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/06/2023 |  | RoutineScheduled | 175-19-0024 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-10"sludge 4"scum/ Microfast-8"sludge/ Pump Tank-1"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-1545 ETM-69h 57m/ High-12/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/15/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20170 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level inside and outside. Replaced failed Zoeller N98 (didn't even last 4 years) with a Zoeller N137. New pump did 43.2 gpm. Reduced run time slightly to maintain 180 gal dose. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
11/22/2023 | Alternative | RoutineScheduled | 03-163-0161 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [18 empty] | Replaced discharge pump, and repiped pump lines and replaced 2 floats. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/15/2023 | Alternative | Routine/Scheduled | 12-142-0237 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 250.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | Dec 30 1899 3:12PM
11/16/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches |  | 100.000000 | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | Replaced junction box, pump, and added a clean out on the peat moss units outlet pipe. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/21/2023 | 08:00 PM
06/26/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches |  | 750.000000 | ["Attached Growth Medium","Effluent Screens"] | Effluent Screens | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/12/2023 | 11:08 AM
04/03/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS repaired break in tubing. System should return to proper function. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/29/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1500 | Micro-fast |  | Pump | Pressure | Drip | Not Applicable | 100.000000 | ["Auxiliary Filter","Dispersal System Operation","Effluent Screens"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | The system is operating as intended now. there was a small leak in the drip field that corrected at the time of inspection. it was rec. for the system to be pumped | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/14/2023 | 03:00 PM
06/29/2023 | Alternative | Routine/Scheduled | 175-07-0069 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 11:20AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/13/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-20069 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 5.500000 | 6.000000 |  | 0.000000 | No tablets | [10 empty] | No tablets | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/09/2023 | Alternative | Reportable Incident Component Maintenance | SD-14-303 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm in Advantex recirc tank due to RSV malfunction. One of the plastic spheres in the RSV was about 90% full of water and therefore not buoyant, not properly sealing the RSV to allow effluent to transfer over to the discharge tank. Also the rubber tip at bottom of RSV stinger had fallen off. Used a plastic toy ball as a temporary fix until correct parts can be obtained. Ran a few test cycles to verify effluent was flowing over to the discharge tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
04/03/2023 |  | Routine/Scheduled |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump tank - float sensors, pump and controls operating. Drip - Headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | Jan 1 1900 6:30AM
12/21/2023 | Alternative | RoutineScheduled | 115-01-0455 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Biomicrobics Fast 0.5 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | NA | Musty | [15 empty] | Inspected | Sludge levels-Scum layer minimal and 12" in. sludge in Septic tank- Treatment zone - observation port OK-good aeration, No access or back side sludge port to check sludge levels in treatment. Alarm functional, new blower 2 years ago. Good Aeration. Due to no access port we cannot check the sludge in the fast treamtnet to so we reccomend frequent pumping or adding the access port to tank to check sludge. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:30 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/09/2023 | Alternative | RoutineScheduled | 05-125-073 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 12:00 AM
01/31/2023 |  | Routine/Scheduled | 228-17-0358 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Microfast |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [14 empty] | Pumped Out | Replaced pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 8:00AM
08/21/2023 | Alternative | Follow-Up | 041-STS-260673 | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Chesterfield | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped and cleaned all the tanks. Disconnected the pressure switch due to the pumping of the tanks. The UV is still not hooked up - needs to be fixed and/or addressed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/21/2023 | Dec 30 1899 11:00AM
05/02/2023 |  | RoutineScheduled | 199-08-0080 | York | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Delta |  | Pump | Gravity | Trenches |  |  | [] | ["Control Operation","BlowerCompressorAerator Operation","Level Sensor Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/02/2023 | 12:00 AM
09/20/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The pressure switch for the aerator is not hooked up. The UV is not working. Replaced the relay in the control panel, replaced the alarm light bulb, and replaced the buzzer. The timer is set to 8 minutes every 2 hours. Owner wants splice box replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/20/2023 | Dec 30 1899 11:30AM
10/30/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.560000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 02:30 PM
05/19/2023 | Alternative | Routine/Scheduled | 159-02-446 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | routine Service Primary septic tank - normal level - effluent screen serviced. Aeratin tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox not examined. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 02:00 PM
01/14/2023 |  | RoutineScheduled | 132-19-0017 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Purasys SBR (Anua) |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Auxiliary Filter","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Auxiliary Filter","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/05/2023 | 12:00 PM
12/11/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine annual, nothing to report | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | 12:00 AM
03/30/2023 | Alternative | Routine/Scheduled | 175-STS-13778 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Gravity |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | Dec 30 1899 12:05PM
04/24/2023 |  | Routine/Scheduled |  | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tnak - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 7:15AM
03/27/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
01/20/2023 |  | RoutineScheduled | 17-113-087 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/20/2023 | 12:00 AM
08/16/2023 | Alternative | Follow-Up |  | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | Dispersal System Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Site visited by MAOSE / MAOSSO to evaluate absorption field. Verified that correct drip tubing was utilized and installed. Fully flushed system - much sand and other debris removed - believe three to four of the laterals are functioning - two laterals fully dry and believe that supply & return lines may be sand clogged. Pump timer adjusted to keep system out of alarm condition - homeowner advised to please reduce water usage. Proposal is to return with several workers - hand excavate the supply and return lines - cut the ends of each to fully flush (add air release / vacuum breakers) and pressure flush drip laterals to remove debris. Drip field not functioning as designed, drip mound is heavily saturated on left side, but is functioning. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/17/2023 | Dec 30 1899 6:30AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommended to homeowner that the sump pump drain is diverted away from the ends of the lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/16/2023 |  | Routine/Scheduled | SWP-04-101 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Peat checked. System appears to be operating normally. Pipe between septic tank and pump tank appears to be going uphill and is causing the pipe to stand half full of effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 11:01 AM
04/03/2023 |  | RoutineScheduled | 17-137-0175 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | EZ Treat |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:00 AM
10/25/2023 | Alternative | Reportable Incident Component Maintenance | SD-05-92 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | End Puraflo pod (closest to driveway) was damaged by a utility contractor clearing/cutting alongside the road. A new replacement pod, with new peat, was ordered from Warrenton Vamac. Another septic installer (David Day) replaced that pod & lid (with peat inside). He stated that no dewatering was needed and used peat was disposed of at the Spotsylvania Refuse Center. Peat in other 4 pods was compacted to about 3" below the spreader bars, but otherwise appeared to be in good condition. There was no ponding in any of the pods. No signs of effluent surfacing in the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
04/04/2023 |  | Routine/Scheduled | 2006-143-0292 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | 09:15 AM
06/27/2023 | Alternative | RoutineScheduled | 19-142-0061 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 1.000000 | 1250 | Norweco |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge Scum Accumulation - Septic 12", ATU 4" Filter Cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | Dec 30 1899 10:00AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | new blower | This AOSS should now return to normal function after having provided the above state routine maintenance | 07/06/2023 | 08:40 AM
11/07/2023 | Alternative | Routine/Scheduled | 15-118-0026 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Not due for pump out. -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Direct Discharge: Upgraded UV bulb. Checked and confirmed UV system is functioning properly. Checked and confirmed required signage is present. Checked and confirmed rodent protective cover is intact. Checked and confirmed outlet is free of debris and free flowing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 11:51AM
11/06/2023 | Alternative | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 10.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 01:21 PM
06/13/2023 | Alternative | RoutineScheduled | SD-06-303 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Sand Tank | Gravity | Pressure | Discharge | Chlorination | 600.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES |  |  | 7.500000 | 7.400000 |  |  |  | 06/13/2023 | Sample Chamber | 2.000000 | 1.900000 |  | 2.200000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 12:00 AM
04/24/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/22/2023 | Alternative | Reportable Incident | 03-172-0060A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Advantex ax20. Recirc alarms every time it rains. Found ground water infiltration through both orenco risers. Customer would like to do the re seal int the spring because he is getting a fence put up right now and will need to save some money. I have emailed the estimates to him | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | Dec 30 1899 9:01AM
10/12/2023 | Alternative | RoutineScheduled | 2017-143-0139 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
03/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | NO | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | Dec 30 1899 1:30PM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:40PM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance | 099-10-0003-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Cloudy | [5 empty] | 07/10/2023 |  | 36.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. 15psi. Blower 2.92 amps. Media is really dirty so treatment is not good, recommend to do a chemical clean (tank needs pump out due to solids). Field has a few wet areas No water above ground and gallons per minute are lower than last year so we recommend to do a bleach flush. Board holding blower panel is rotten needs to be replaced. Will send proposal for all this work. High level 42, low level 25, override 2261. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
08/16/2023 | Alternative |  | 003-STS-30580 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | David & Lisa | Weyher | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Multiflo | Gravity | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | NA | [17 empty] | 3.5' overall liquid depth, 0 scum, 12" of sludge, Recommend pumping septic tank and multiflo before next inspection. No sludge in aerator tank on Multiflo. Aerator working. Effluent flowing through sample box. Alarm works and field is dry. Inlet was clogged when arrive. Unblocked by pushing it out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 10:00 AM
04/03/2023 | Alternative |  | 099-06-0296-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | EcoFlo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/12/2023 | Alternative | RoutineScheduled | 2010-143-0082 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/01/2023 | Alternative | RoutineScheduled | 166-11-077 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/10/2023 | Alternative | Routine/Scheduled | 041-STS-259111 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/10/2023 | Dec 30 1899 2:26PM
09/12/2023 | Alternative | Routine/Scheduled | 07-160-0210 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 04:30 PM
05/15/2023 | Alternative |  | 03-183-159 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/15/2023 |  | 2.540000 |  |  | 1.000000 |  |  | Will be sent separately |  | BOD: 2.54 TSS: 1.00 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/15/2023 | 12:00 AM
02/15/2023 |  | RoutineScheduled | 179-10-0011-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [7 empty] | 02/16/2023 |  | 10.000000 | [5 empty] | Will be sent separately | Inspected | Onsite for routine inspection and collected BOD. All tanks will need to be pumped out during next years inspection. Saw signs of fabric softener and scent beads in the system. Spoke to homeowner they will stop using these products. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/10/2023 | Alternative | RoutineScheduled |  | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1250 | N/A |  | Pump | Pressure | Trenches | Not Applicable | 75.000000 | ["Effluent Screens"] | ["Effluent Screens","Level Sensor Operation"] | YES | Musty | Cloudy | [15 empty] | The entire system is in compliance with the health department regulations and approved plans. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 11:00 AM
02/21/2023 |  | Routine/Scheduled | 087-STS-6645 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Manifold flushed. System appears to be operating normally. Averaged 1.1 overrides per day. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | 10:37 AM
06/22/2023 | Alternative | Follow-Up |  | Frederick | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Gravity | Discharge | Chlorination |  | Control Operation | Control Operation | N/A | [18 empty] | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 06/27/2023 | 09:57 AM
06/05/2023 | Alternative | Routine/Scheduled | 2007-143-0172 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 07:30 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/09/2023 |  | Routine/Scheduled | 2013-143-0135 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/09/2023 | 09:47 AM
04/25/2023 |  | RoutineScheduled | 177-06-0458-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | There is paint in the Advantex tank. We recommend pumping it out as soon as possible to prevent paint from clogging the textile media sheets. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
01/13/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Reset set hydraulic box from machine damage. Found sewer clean out damaged by machine. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | Dec 30 1899 11:08AM
08/11/2023 | Alternative |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 | 1000 | 1000 | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled | 115-06-0486 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | [15 empty] | Inspected | Sludge level-minimal Scum level & 5" Sludge in Septic tank. Pump Chamber 5-6" sludge. Cleaned Effluent screen filter. Alarm functional and pump is operational, Peat was replaced in 2020. Peat was moist.. We Turned peat in all 4 quadrants. Drains good. The tipping tray was ok. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
03/22/2023 | Alternative | Routine/Scheduled | 199-13-0034 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 2000 | Norweco Singulair ATU | Norweco Singulair ATU | Pump | Pressure | Trenches | Not Applicable | 900.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Service - System #1 Primary septic tank - normal level Processing Tank - trash tank - normal level Aeration Tank - mixing present - aspirators (2) serviced. Clarifier - effluent screens (2) serviced. Pump Tank - float sensors, pump and controls operating. LPP - multiple locations of slight surfacing present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | Dec 30 1899 9:30AM
11/08/2023 | Alternative | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 2831.000000 | [] | [] |  |  |  | 7.910000 | 6.790000 | 22.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 12:30 PM
08/24/2023 | Alternative | Reportable Incident | 157-02-104 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 03:15 PM
08/22/2023 | Alternative | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - System Commissioning / Start-up Trash Tank - filled while on property. Aeration Tank - filled with fresh water for start-up - compressor operating - mixing present. Pump Tank - float sensors, pump and controls operating. - drawdowns conducted - timed dosing adjusted. Drip Headworks - automatic - both zones operating. Drip Field - remote - confirmed that both zones obtaining effluent - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 08:00 AM
05/01/2023 | Alternative |  | 150-05-0051 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Premier Tech Ecoflo |  | Pump | Gravity | Mound |  |  | [] | ["Attached Growth Medium","Dispersal System Operation","Control Operation","Level Sensor Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 12:00 AM
05/31/2023 | Alternative | RoutineScheduled | 17-160-0195 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | Aquasafe |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Septic | Dark Brown | [5 empty] | 05/31/2023 | Sample Tap | 398.000000 |  |  | 5360.000000 |  |  | Attached to this report | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 12:00 AM
11/28/2023 | Alternative | Reportable Incident | 04-142-0083 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [29 empty] | Vortex filter is clogged and torn -replaced while on site | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 2:11PM
03/16/2023 |  | RoutineScheduled | 175-16-0241 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
07/19/2023 | Alternative |  | 101-14-0205 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | J.H. "Rip" | Verkerke | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/30/2023 |  | Routine/Scheduled |  | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Richmond | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Clearstream ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | Jan 1 1900 5:49PM
07/06/2023 | Alternative | Routine/Scheduled | 03-120-0468A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 2.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | Dec 30 1899 5:02PM
07/06/2023 | Alternative | RoutineScheduled | 087-STS-6218 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
04/11/2023 |  | RoutineScheduled | 179-18-0166-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
07/28/2023 | Alternative | RoutineScheduled | 159-06-0372 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001302 | Anthony | Santucci-Curci |  |  |  |  | Gravity | Gravity | Discharge |  |  | ["Other"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
09/25/2023 | Alternative | RoutineScheduled | 167-STS-15634 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/25/2023 | 12:00 AM
04/18/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/21/2023 | 12:30 PM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
03/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NO | [17 empty] | All 3 tanks need pumped out. When we arrived the airblower was off. Not sure how long blower was off. Also T was clogged when we arrived. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/15/2023 | Dec 30 1899 4:20PM
06/28/2023 | Alternative |  | 033-12-0131-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/11/2023 | Alternative | Reportable Incident | 128.02.042 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, system check - okay | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/25/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 |  |  | Pump | Pressure | Trenches |  | 600.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | 10:38 AM
02/15/2023 | Alternative |  | 101-16-0272 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | JPH | Trust | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/06/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-152 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Drip rate was initially high on zone 2. Went back to normal after replacing the diaphragm for zone 1 (puckered and not sealing) and cleaning the finger screen there. Zone master solenoid was chattering and not fully opening. Cut out old butt splices and old wire nuts in hydraulic unit and stripped wire ends for fresh connections. Solenoid working again. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
04/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/31/2023 | Alternative |  | 124-STS-2379 | Fairfax | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | Plant taken partially off line due to PLC issues and repairs. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12:00 AM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | Dec 30 1899 9:34AM
02/14/2023 | Alternative | Reportable Incident | 136-03-0296 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Control Operation | ["Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NO | [16 empty] | Pumped Out | Alarm Event Control panel failure - System pumped empty for storage - control panel ordered. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/15/2023 | 11:15 AM
02/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
07/31/2023 | Alternative | RoutineScheduled | 10-113-117 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/31/2023 | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled | 193-STS-102238 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 11/08/2023 | [9 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/14/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Gravity | Trenches |  |  | [] | [] | YES | Septic | [15 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | 12:00 AM
03/14/2023 |  | Routine/Scheduled | 550-STS-6634 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Jan 1 1900 1:20PM
04/07/2023 |  | Pump-Out Only |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | 06:30 PM
01/06/2023 |  | RoutineScheduled | 132-18-0079 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
10/25/2023 | Alternative |  | 17-100-0507 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled | 175-09-0396 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Septic & Pumping | 1942001330 | michelle | Pumping | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/29/2023 | 04:50 PM
08/01/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service - AquaKlear ATU Primary septic tank - normal level Aeration Tank - normal level - mixing present compressor serviced. PUmp Tank - float sensors, pump and controls operating. Drip Field - headworks serviced - mechanical splitter valve serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | Dec 30 1899 8:00AM
04/26/2023 |  | RoutineScheduled | 033-17-0072-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Puraflo peat needs replacement. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/17/2023 | 12:44 PM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/20/2023 |  | RoutineScheduled | 177-08-0145-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | 90-Day Inspection Upon arrival the RSV, Advantex plumbing & the top of the fabric sheets were covered in a brown/white slime. Consulted with manufacturer's rep about possible causes. Installed web grommet in place of RSV grommet. System may require more frequent servicing if source of slim buildup cannot be eliminated. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
07/27/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89331 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | 6.650000 | 3.090000 |  |  |  | 07/27/2023 | Pump Chamber | 7.000000 |  | 2419.600000 | 11.200000 |  |  | Will be sent separately | Inspected | Design & construction of system do not allow for sampling at the discharge point. Sample was taken from the pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
05/22/2023 | Alternative | RoutineScheduled | 171-05-0560 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | NA | [16 empty] | Inspected | Sludge level- 1" scum layer on top-10" sludge on bottom in Septic tank-- Pump tank has 6" of sludge, the pump and alarm are operational- Cleaned effluent filter, turned over peat moss in treatment tanks. Peat look in ok condition for age. Alarm is working, Peat was moist with no ponding, Added 1/2 2lb rootx treatment to the dbox below the peat pods to stop root intrusion- Float switches tested good- Pump counter at 106861 vs 106483 cycles last year 378 cycles in one year, pump run time 547.95 vs 537.92hr normal amount about 10 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
03/24/2023 | Alternative | Initial Visit | S-09-111-0151 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  |  | Trenches |  |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/24/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0385 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
11/09/2023 | Alternative | RoutineScheduled | 05-120-0220A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 750 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Effluent Screens","Level Sensor Operation","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation"] | YES | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | Dec 30 1899 11:00AM
11/17/2023 | Alternative | RoutineScheduled | 13-184-5001 | Scott | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination | [21 empty] | 3/22/2024 Property appears to be vacant, neighbor is owner's sister, there was a fire inside the home, and it is not livable. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/17/2023 | Alternative | RoutineScheduled | 2006-143-0156 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Advantex AX20 |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 12:00 AM
12/15/2023 | Alternative | RoutineScheduled | 02-113-378 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/15/2023 | 12:00 AM
07/12/2023 | Alternative | Routine/Scheduled | 550-STS-6437 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | a | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 10:50AM
08/28/2023 | Alternative | RoutineScheduled | 18-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 0.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.000000 | 6.000000 |  | 0.000000 | No effluent coming out Tested the tank | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/28/2023 | Dec 30 1899 2:00PM
05/26/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/03/2023 |  | RoutineScheduled | 179-10-0225-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Alarm call follow-up. System working its way out of high level after excess waster usage. Cleaned clogged Biotube filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
09/07/2023 | Alternative | Routine/Scheduled | 196-15-0027 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 0.000000 | [11 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 05:57 PM
12/21/2023 | Alternative | RoutineScheduled | 18-120-0502A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2000 | 1000 | 1000 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 11:30AM
06/29/2023 | Alternative | RoutineScheduled | 07-100-0689 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | REPLACED FIBER IN SYSTEM-EVERYTHING WORKING AS IT SHOULD. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/25/2023 | 02:20 PM
03/22/2023 |  | RoutineScheduled | 175-18-0401 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump" ,"Disinfection" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Recirculation Pump" ,"Disinfection" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Recirc pump intake was badly clogged again. Added a Simtech pump filter to provide some protection. Cleaned uv sleeve and replaced uv lamp. Brass check valve flapper for zone 1 (closer to the house) was stuck barely open so that the flush rate was decreased, and zone 2 was getting flushed each drip cycle. Replaced the check valve and retested to confirm repair. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
02/07/2023 |  | Initial Visit |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend keeping grade 1-2" below lids | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
03/06/2023 |  | RoutineScheduled | VAG408199 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Blue Ox |  |  | Gravity | Discharge | Chlorination |  | ["None"] | [] | [8 empty] | 03/21/2023 | Sample Chamber | 18.000000 |  |  | 7.900000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/21/2023 | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled | 04-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/19/2023 | 12:00 AM
06/05/2023 | Alternative | Follow-Up | C16-180-0090 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/26/2023 |  | Routine/Scheduled | 127-STS-33336 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Purasys |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/26/2023 | Jan 1 1900 1:53PM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90334 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
02/09/2023 |  | RoutineScheduled | 179-15-0168-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The inlet tee was partially clogged and has been cleaned out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
11/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | Dec 30 1899 2:02PM
04/29/2023 |  | RoutineScheduled | 133 04 0867 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Septic Tank Only |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | 5" of solids in septic tank. 2" of solids in pump tank. Tested alarm and pump floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 07:03 PM
02/27/2023 |  | RoutineScheduled | 099-19-0045 SPSA | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Alot of grease in the system and system showed signs of fabric softner usage went over do's and dont's with the homeowner. Recommend pumping out recirc tank during next years inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
10/30/2023 | Alternative | RoutineScheduled | 091-STS-337027 | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 3.000000 | 12000 | Septic Tank Only | Recirculating Sand Filter | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [7 empty] | 10/30/2023 | Pump Chamber | 8.700000 |  |  | 0.900000 |  |  | Attached to this report |  | The system did not need to be pumped. The effluent and spin filters were both pulled and cleaned. The sand filter was in good operating condition. The controls were operating as designed. There were no visible leaks in the drip field. The samples were within permitted limits. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | 09:10 PM
10/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Septic Tank-12"sludge 6"scum/ Microfast ATU-16"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Pump out required of the Septic-Microfast ATU Tank/ Blower air filter cleaned and blower is working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-784 ETM-57h 32m/ Pump2-753 ETM-55h 27m/ Peak-13/ High level-11/ No breakout or spongy areas on the LPD Pad Site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled | 2013-143-0011 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled | 07-197-A7 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection","BlowerCompressorAerator Operation"] |  |  | Pungent | Cloudy | 6.000000 | 2.000000 | [14 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0087 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Whitewater ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/13/2024 | 11:49 AM
11/14/2023 | Alternative | Routine/Scheduled | 800-STS-14289 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 2:19PM
03/28/2023 |  | RoutineScheduled | 18-137-0073 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["Effluent Screens","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/28/2023 | 12:00 AM
08/28/2023 | Alternative |  | 137-STS-23517 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan |  |  | Kristina | Lawwill | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/01/2023 | Alternative | Follow-Up | 101-15-0397 | Albemarle | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 |  |  | Pump | Pressure | Drip |  | 85.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/05/2023 | 10:00 AM
09/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 2000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/24/2023 |  | Routine/Scheduled | 550-STS-5876 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/24/2023 | Jan 1 1900 10:15AM
08/25/2023 | Alternative | Follow-Up Component Maintenance | 179-STS-92513 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pump out. Reassembled components and homeowner refilled tank back to proper water levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
08/30/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance | 182-17-0382 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Added media cleaner | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
07/25/2023 | Alternative |  | 195-Discharge-21118 Grassy Ridge Road | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/25/2023 |  | 2.540000 | [5 empty] | Will be sent separately |  | BOD: 2.54 TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/25/2023 | 12:00 AM
02/13/2023 | Alternative | Reportable Incident | 073-STS-101588 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Pad | UV | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Repair - VDH Permit 136-22-0267 Pumped empty existing septic tank - removed. Installed new 1500 gallon BioMicrobics FAST Processing Tank Installed new Norweco AT1500 UV Disinfection unit. Installed new pad / bed in area indicated. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/14/2023 | 07:15 AM
05/25/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 |  | Septic |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | LPD. 10" Of sludge. Minimal scum. 48" liquid depth. Cleaned the filter. Floats, alarm, and pump are operational. Field is dry and mowed.7410 Events and 355.49 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 10:45 AM
08/16/2023 | Alternative | Routine/Scheduled | 810-STS-3809 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | Dec 30 1899 12:00PM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/06/2023 | Alternative | Routine/Scheduled | 136-15-0010 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing tank - normal level - RSV, recirc pump, effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Absorption Bed - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 12:30 PM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 175-90-0082 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 | 2500 | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"SludgeScum Accumulation"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
07/31/2023 | Alternative | Reportable Incident Component Maintenance | 179-06-0324-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 2.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for demand dose panel in alarm due to bad connection on terminal strip. Corrected wire issue | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [7 empty] | 05/16/2023 | Sample Chamber | 10.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | Septic Tank-6"sludge 0"scum/ Microfast-0"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ UV-Light is faulty , need new sleeve and cord. To be addressed at a later date. Counts: Pump-831 ETM-150h 30m/ Peak-40 ETM-606h 4m/ Standard Off-3h 25m On-10m 46s Peak Off-2h 43m/ Z1-5.4 Z2-5.8/ Z35.9 Z45.8/ Watermeter-0064286.6/ No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/13/2023 | Alternative | Routine/Scheduled | 151-04-251 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - peatmoss in fair condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 01:00 PM
06/23/2023 | Alternative | Reportable Incident |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | AquaKlear |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Meeting onsite to discuss replacement of the Aquaklear treatment tank. Adding the needed blower and accesible lids on the septic and treatment tanks. System has been replaced with the same original brand unit Aquaklear and is now operational 8-15-23 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/30/2023 | 09:30 AM
03/03/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower connection was repaired. System appears to be functioning as designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
10/30/2023 | Alternative | Routine/Scheduled | 2007-143-0175 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Air filter cleaned. System appears to be operating normally. Etm 456.19, Ct. 382106 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 09:53 AM
12/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Septic Tank |  | Gravity | Gravity | Discharge | UV |  | ["Disinfection"] | ["Disinfection"] | NO | None | Clear | 7.990000 | 33.900000 |  |  |  | 01/22/2024 | Sample Chamber | [8 empty] | Septic Tank-4"sludge 0"scum/ No pump out needed/ No breakout or spongy areas on the sand filter bed/ Norweco UV-Light sleeve cleaned and working properly/ Air bubbler air pump functioning properly/ Discharge pipe and water is clear. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/09/2023 |  | Follow-Up | 179-10-0184-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pumpout of all tanks. Reassemble components and tanks were refilled back to proper level with a water truck. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
01/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS replaced septic pump. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
11/14/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | The effluent filter was very clogged and the liquid level was up 4-5 inches above the normal operating level. The septic and pump tanks should be pumped out soon. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 11:28 AM
12/05/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-848 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Peat moss is ok for now but getting to the end of its life span. Peat needs to be replaced in a year. Proposal to be sent. It is not recomended to have a shed on top of the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
04/21/2023 |  | Routine/Scheduled |  | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Post install service and inspection. Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - recirc pump, spray grid and media drapes serviced. Processing Tank - discharge - float sensors, pump and controls operating. U.V. bulb and housing serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 09:15 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was off at time of inspection. It was turned on and appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/12/2023 | Alternative | Routine/Scheduled | 151-06-0425 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1000 | Ecoflo |  | Gravity | Gravity | Pad |  |  | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | YES |  |  |  |  | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 06:14 PM
11/01/2023 | Alternative | Reportable Incident Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed WE20G05P4-21 pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
04/03/2023 |  | RoutineScheduled | 179-08-0194-SWT | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. System has averaged about 5 cycles a day since last inspection. Three out of 5 pods were saturated again. Observed standing water in the pod collection line - more water the further away from the exit point. The collection line has probably settled and is inhibiting drainage. Needs to be dug up, inspected and repaired. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
09/19/2023 | Alternative | RoutineScheduled | VAG408253 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | No discharge at this time | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/19/2023 | 12:00 AM
10/19/2023 | Alternative |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
06/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/26/2023 | 10:29 AM
08/15/2023 | Alternative | RoutineScheduled | 06-198-066 | Wythe | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ADVANTEX |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Distribution Pump Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Distribution Pump Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
01/05/2023 |  | Reportable Incident | 181-14-0008 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | The system did not need to be pumped. The blower was not working at the time of arrival so it was replaced with a new blower. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/25/2023 | 04:40 PM
03/05/2023 |  | Routine/Scheduled | 041-STS-260875 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/05/2023 | Jan 1 1900 9:30AM
03/29/2023 |  | RoutineScheduled |  | Page | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | leak in valve box | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/28/2023 | 02:17 PM
02/13/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | End caps repaired. System appears to be functioning as designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
04/04/2023 |  | RoutineScheduled | 175-18-0519 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Mound | UV |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 6"scum/ Microfast-18"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Due to sludge levels the Septic Microfast Tank REQUIRES PUMP OUT/ / Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-10148 ETM-1353h/ High-10/ Watermeter-029,167.6/ Zone1-7.8/ Zone2-7.3 On-8m Off-3h/ Level Override-10/ Dose 60gal./ UV-Light sleeve cleaned/ No breakout or spongy areas on the drip field and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/20/2023 |  | RoutineScheduled | 179-06-0241-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Sample box was half way full of water due to 8" of sludge in the bottom, vacuumed it out and box stared draining correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
08/29/2023 | Alternative | Routine/Scheduled | 04-142-0065 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | Dec 30 1899 7:45AM
06/12/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-1992 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/12/2023 | Dec 30 1899 1:00PM
10/23/2023 | Alternative |  | 125-STS-29522 | Nelson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
02/13/2023 | Alternative |  | 15-160-0093 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | Aquasafe |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | Dark Brown | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/18/2023 |  | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 8394.000000 | [] | [] |  |  |  | 6.970000 | 6.540000 | 32.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 08:45 AM
11/01/2023 | Alternative | RoutineScheduled | 181-00-0428 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only |  | Pump | Pressure | Trenches | Not Applicable |  | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | NA | [17 empty] | The system did not need to be pumped. The timer float was not operating correctly at the time of inspection so the float was replaced. The rest of the controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/27/2023 | 09:30 PM
11/30/2023 | Alternative | RoutineScheduled | 087-STS-6563 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | EZ Treat |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 12:00 AM
12/14/2023 | Alternative | RoutineScheduled Component Maintenance | 182-18-0093 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 12/14/2023 |  | 5.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal Recommend repairing riser that is egg shaped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 137-STS-25647 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
06/30/2023 | Alternative | Routine/Scheduled | 13-172-0057A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | EcoPod |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/30/2023 | Dec 30 1899 3:07PM
10/27/2023 | Alternative | Routine/Scheduled | 17-142-0128 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 500.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [17 empty] | Manifold was flushed. The recirculation pump had 6 overrides in the past 30 days | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | Dec 30 1899 12:40PM
12/18/2023 | Alternative | Reportable Incident | 151-14-0090 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the red light on and hears bubbling. Serviced system. Checked the panel and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The pump breaker was tripped - turned back on and everything worked properly. Pumped out the pump tank and bottom and top of the Clearstream tank. The timer is set to 3 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/18/2023 | 01:00 PM
07/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Montgomery | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - New River | Matthews Sanitation Services Llc | 1942001226 | Brian | Matthews | 1.000000 | 1000 | [7 empty] | [] | [] | [17 empty] | Pumped Out |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/25/2023 | 12:00 AM
05/25/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping this year. Recommend evaluating the manifold and repairing/replacing foam filters if necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 | Alternative | RoutineScheduled | SD-05-43 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 65.600000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09:45 AM
05/18/2023 |  | Initial Visit | 085-STS-34776 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - System Commissioning. Primary septic tank - effluent screen serviced. Processing Tank - REcirc - recirc pump, spray grid adjusted. Processing Tank - Discharge - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 12:30PM
10/13/2023 | Alternative | RoutineScheduled Component Maintenance | SD-07-401 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 3.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Observed effluent surfacing near ARV valve boxes in zone 2 (zone closer to parking lot) when running test cycles. 10/17/23 - dug up wet spot and replaced the zone check valve (zone 2) which was corroded and leaking externally. Also dug up and replaced the ARV valve box for zone 1 (front of church). The box had settled previously so that lid was pushed off by the ARV (and later hit by a lawn mower). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
09/01/2023 | Alternative | RoutineScheduled | 107-02-0782 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | ["None","Control Operation"] | ["None","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
12/06/2023 | Alternative |  | 07-192-160 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/06/2023 |  | 4.990000 | [5 empty] | Will be sent separately |  | BOD: 4.99 TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/06/2023 | 12:00 AM
11/09/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  |  |  | 6.760000 |  |  |  |  | 12/09/2023 |  | 27.000000 |  |  | 11.000000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 11:30 AM
05/08/2023 | Alternative | Routine/Scheduled | 166-07-407 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 5 modules - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 10:30 AM
07/03/2023 | Alternative | Routine/Scheduled | 228-18-0308 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear |  | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/03/2023 | Dec 30 1899 12:30PM
03/14/2023 | Alternative | RoutineScheduled | SD-14-09 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
10/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-13-0028 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/18/2023 | 08:36 AM
04/11/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced pressure gauge | This AOSS should now return to normal function after having provided the above state routine maintenance | 06/21/2023 | 03:35 PM
02/21/2023 | Alternative | RoutineScheduled | SD-14-50 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Cleaned air filter for air pump. Septic tank still needs pumped out. Owner to make arrangements. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/28/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | Dec 30 1899 2:50PM
01/10/2023 |  | RoutineScheduled | 177-STS-88982 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Effluent Screens" ,"Dispersal System Operation"] | ["Effluent Screens" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | There was effluent surfacing in the drip dispersal area due to broken drip tubing. We notified the installer & he plans to make repairs. Health Dept: 2/2/23 - MEBB EH Supervisor: Per conversation with Ed with EcoSeptix, as of 2/2/23, a second O&M visit was made (1/10/23) and issues observed. Ed stated that he has reached out to installer, Ray Perkins, and he plans to make repairs when weather is good. Will not send a second NOAV at this time. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | 07:17 AM
05/24/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 12:00 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lower line of the drainfield appears to possibly be hydraulically saturated and allowing effluent to seep perpendicular to the drainfield line. The distribution box lids were damaged by open space bush hogging. Recommended homeowner contact DSS to address the lid issue and the lower line. Recommend checking back in 4-6 months to reassess the lower line | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/01/2023 | Alternative | RoutineScheduled | 175-13-0332 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic / Ecopod ATU Treatment Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-2"sludge 0"scum/ Ecopod ATU-2"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-83911 ETM-9208 On-4m 20s Off-1h 55m/ Hand-86/ High-781/ Override-103/ Watermeter-0,873,152/ No breakout or spongy areas on the Delta Drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/06/2023 |  |  | 033-STS-91767 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Fuji | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/28/2023 | Alternative |  | 17-100-0507 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
06/20/2023 | Alternative | RoutineScheduled | 175-09-0030 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank #1-6"sludge 0"scum/ Septic Tank #2-3"sludge 0"scum/ EZ-Treat Recirc. Tank-3"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Recirc. pump intake cleaned and dosing correctly, media in good condition/ Counts: Pump #1-2384 ETM-172h 35m/ Pump #2-1379 ETM-2h 48m/ High-1965/ Power Fail-13/ No breakout or spongy areas on the drip field and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/19/2023 | Alternative | RoutineScheduled | C-05-111-0016 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Delta DF 50 Whitewater |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Sludge levels- 2-4" Scum and sludge 24" sludge in septic tank- In whitewater 3-4" scum on surface and trace sludge on bottom of tank. Good aeration and Clean Airfilter, checked blower alarm, System is fully operational. May want to get both the scum layer pumped in the white water and the septic tank pump later this year. Need a new 4" white screw cap lid, it is aged and about to break. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
10/04/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | Dec 30 1899 9:00AM
04/11/2023 | Alternative | Follow-Up Component Maintenance | 175-03-0761 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | NA | Musty | [14 empty] | Will be sent separately | Inspected | Tank pumped by Powell's Plumbing. Tank had an exorbitant amount of feminine products and wipes. During the tank cleaning, several diffusers were found to be torn or not working correctly. All diffusers were replaced and a flush valve was added for future maintenance to assist in the removal of buildup in the manifold. A PVC spring check valve was installed at the manifold inlet to prevent backflow of water into blower and housing during a high level event. Ballast blocks were removed and PVC support stands installed to allow for 360 degree aeration. The pump was lowered to put the base 12" off the bottom of the tank. Replaced worn gasket in camlock. Cleaned the air pre-filter. Observed thin areas in the fiberglass manways. Need to be reinforced to preserve manway integrity. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
10/12/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Puraflo |  | Pump | Gravity | Trenches |  | 600.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 10:16 AM
01/31/2023 |  | RoutineScheduled | 179-11-0048-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Disinfection" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Disinfection"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | A follow-up visit is scheduled for May. At that time, the septic tank & Advantex RT tank will be pumped. We also plan to install a new UV cord and lamp and install a vent on the septic tank. The spin filter will also be cleaned during this visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
03/10/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","Dispersal System Operation","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/14/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | McKim Septic & Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | [18 empty] | Zone 2 air release vales replaced and pipeing fixed. All new buckets were installed | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/28/2023 | Dec 30 1899 3:20PM
06/02/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
08/11/2023 | Alternative | Pump-Out Only |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Fuji |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Fuji Clean - pump out of trash tank and pump tank only. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 06:30 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
04/08/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Sulphitic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
02/02/2023 |  | RoutineScheduled | 177-STS-88667 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0234 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
05/08/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  | 450 | Norweco Drip |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | 12:00 AM
08/05/2023 | Alternative | RoutineScheduled | 2130-09-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | UV | 250.000000 | ["Control Operation","Disinfection","Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Disinfection","Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NA | Musty | Clear | 7.400000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/01/2023 |  | RoutineScheduled | 179-STS-89674 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump" ,"Auxiliary Filter" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Auxiliary Filter" ,"Recirculation Pump" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The UV bulb alert light was on. We recommend replacing the UV bulb. We also recommend replacing the air release valve and housing for the lower drip dispersal zone, and the air release valve housing for the upper zone. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. No measurable sludge in primary septic tank confirms that tank was pumped out last week. Water starting to accumulate in the headworks vault due to the sump pump not running. No power to junction box in tank, needs further diagnosis. Low level count in drip panel has increased to 500, will need diagnosis if count continues to increase. In the past 14 days, system has pumped an average of only 738.6 gals/day at 333.5 gals/cycle (avg.) for a total of 10,341 gallons. These numbers may be low due to reporting period including 2 weekends when not as much water is used. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 175-11-0248 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 10:33 AM
04/13/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation","BlowerCompressorAerator Operation"] | ["Level Sensor Operation","BlowerCompressorAerator Operation"] | NA | [7 empty] | 04/13/2023 | Sample Chamber | 23.000000 | [5 empty] | Attached to this report |  | Septic Tank-3"sludge 0"scum/ Microfast-0"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Off Float is faulty and replaced during inspection/ Controls, pumps, floats and alarms now functioning properly/ Counts: Pump1-164 ETM-5h 24m/ Pump2-156 ETM-5h 8m/ Peak-10/ High-7/ No breakout or spongy areas on the drainfield area. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
04/04/2023 | Alternative | RoutineScheduled | 061-16-256 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 1.000000 | 1500 | MircoFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation"] | NA | [7 empty] | 04/04/2023 | Sample Chamber | 17.000000 | [7 empty] | Sample was grabbed from in let of D- Box | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 08:00 AM
06/14/2023 | Alternative | Reportable Incident | -STS-15903 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | [17 empty] | Replaced 50 gpm Orenco pump, WE20 discharge pump, 2 check valves, 2 schedule 80 unions. Re-plumbed the piping for resirc pumps so you can access them. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 7:00AM
12/06/2023 | Alternative | RoutineScheduled Component Maintenance | 175-19-0119 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Control Operation"] | ["Recirculation Pump" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | On site for annual inspection and to investigate high level alarm in septic/recirc tank. Recirc pump would run but at low amps and not moving any water. Cleaned very dirty pump intake, removed built-in check valve, and verified proper voltage to the pump - still not working. Installed new StayRite recirc pump and a Simtech stainless steel pump screen. Verified good spray pattern into EZ-Treat pod and then completed rest of inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
12/12/2023 | Alternative | Routine/Scheduled | 136-06-0704 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal level 11 in of sludge 2 in of solids Pulled and cleaned filter however it is aged No signs of infiltration Discharge/Pump Tank Condition of above Component Notes for above Component Normal level Tested floats and pump all working as should Pump and floats have met there life expectancy All plumbing intact and pump moving water properly No signs of infiltration Peat Moss Condition of above Component Notes for above Component Tipping bucket and dispersal trays intact Peat moss completely broken down into mud and has standing water Control Panel Outlet box Condition of above Component Notes for above Component 120 volt at the outlet Piggybacked pump and floats Distribution Box Condition of above Component Notes for above Component Normal level 6 lines all intact and taking water properly Speed balancers intact and functional Drain Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:54 PM
10/13/2023 | Alternative | RoutineScheduled Component Maintenance | 177-14-0288-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
09/19/2023 | Alternative | RoutineScheduled | 105-18-0106 Discharge | Appomattox | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Septic Tank | Advantex | Gravity | Gravity | Discharge |  | 350.000000 | ["Effluent Screens"] | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/19/2023 | 10:30 AM
02/20/2023 |  | RoutineScheduled | 175-15-0282 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
04/03/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS repaired break in tubing. System should return to proper function. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/01/2023 |  | Routine/Scheduled | 11-137-0112 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | The treatment tank needs pumping | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/01/2023 | Jan 1 1900 1:56PM
02/28/2023 |  | RoutineScheduled | 175-02-0713 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
05/11/2023 |  | RoutineScheduled | 175-02-0762 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Advantex Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Recirculation Pump"] | ["Attached Growth Medium","Recirculation Pump"] | NA | [17 empty] | Septic Tank-6"sludge 0"scum/ Recirc. Tank-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump-267197 ETM-028399 Override-251878 ETM-003667/ Recirc cnt-960939 ETM-473355/ Recirc pump intake and media cleaned/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/21/2023 | Alternative | Routine/Scheduled | R-10-111-0016 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 11:00AM
01/12/2023 |  | RoutineScheduled | SWP-05-482 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 2 bottom lines were not getting any water due to a roots pushing pipes out of dbox. Replaced section of pipe on each line to be able to connect to dbox. Cut both roots and added root destroyer. Tree to close to dbox advice owner to cut tree down. Recommend to cut magnolia tree to close to pureflow pod. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 03:56 PM
03/29/2023 |  | RoutineScheduled | 175-15-0344 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ Recirc.-2"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Recirc pump intake cleaned/ EZ-Treat media in good condition, spray nozzles clean/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump-7672 ETM-1244h 29m EZ-Treat On-2m 30s Off-12m/ Watermeter-0,716,798.2/ Zone1 -4.6gpm/ Zone2-5.0gpm/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/17/2023 |  | RoutineScheduled | 177-17-0202-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Puraflo peat needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | Dec 30 1899 2:02PM
11/03/2023 | Alternative | RoutineScheduled | 107-16-0386 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | Advantex AX20RT |  | Gravity | Pressure | Drip | Not Applicable |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | Musty | Clear | 5.500000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/12/2023 | 10:00 AM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0478 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
01/11/2023 | Alternative | RoutineScheduled | 047-18-336 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank & aerobic treatment unit due to sludge accumulation in the tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator is not functioning. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
03/28/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
06/20/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-2654 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/20/2023 | Dec 30 1899 2:00PM
09/15/2023 | Alternative | RoutineScheduled | 061-16-097 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 1.000000 | 1500 | MicroFast |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/18/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled | 13-197-048 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/16/2023 | Alternative |  | 101-13-0422 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Shirley | Rennick | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0184-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. treatment crystal clear. System most likely will need pumping next year due to sludge levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
04/10/2023 |  | Reportable Incident |  | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | System discovered to have a failed control panel - Friday 04/07. Commonwealth Waste Solutions umped processing tank and pump tank empty for storage and repair. Installed new MVP S1 DM control panel - restored programming. Processing tank refilled with fresh water for re-start. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/11/2023 | Jan 1 1900 6:30AM
06/30/2023 | Alternative | Reportable Incident | 175-01-0891 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Distribution Pump Operation"] | ["Dispersal System Operation"] | [18 empty] | Service call only: Replaced faulty Zoeller N-161 Pump. Counts- 017179 ETM-0041113 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/21/2023 | Alternative | Reportable Incident | 159-18-0148 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Advanced Septic |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | AOSS - Initial Visit - Alarm Event - Churchview Septic reported as primary service provider - having issues getting them to come out. Found system in alarm condition due to failed diaphragms on compressor. - Rebuilt compressor on property - restored to proper operation. Offered Service Agreement. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/22/2023 | 09:30 AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
11/13/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 1.000000 | 1530 | Advantex RT |  | Pump | Pressure | Drip | Not Applicable | 125.000000 | ["Distribution Pump Operation","Effluent Screens"] | ["Control Operation","Distribution Pump Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | replaced pressure gauge and valve on discharge return line. redirected flow back to avoid hitting floats | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/14/2023 | 06:00 PM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator motor broke PVC fittings inside the blower housing. ATU was not receiving aeration. Homeowner has contacted someone for repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/04/2023 | 06:02 AM
07/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/18/2023 | Dec 30 1899 8:25AM
03/28/2023 |  | Routine/Scheduled | 550-STS-6636 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Jan 1 1900 9:30AM
11/02/2023 | Alternative | Routine/Scheduled | C093-11-0187 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 11:20AM
03/30/2023 | Alternative | Pump-Out Only | 18-177-1049 | Pulaski | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Aquasafe | [6 empty] | [] | [] | [17 empty] | Pumped Out | - blower is not working - left message for customer to proceed with inspection and repair, does not appear customer is wanting to proceed at this time | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/11/2023 | 12:00 AM
05/15/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 RT |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens","Control Operation"] | NA | [16 empty] | Inspected | Septic Tank minimal scum and 6-8 in sludge, Recirculation zone trace of scum 6"sludge and discharge 5-12" sludge trace, Cleaned effluent filter, cleaned drip filter, discharge pressure good on drainfield. Flushed both valves. Discharge pump 54.8 hours and 803 cycles Recirc Pump run time 762.3 hours and 56,560 cycles. Check all all 6 floats and all respond to the panel. System is operational. Alarm history not available. it is connected to monitoring last years report of minutes run time for pumps was an eror and it was in hours. All looks operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
09/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump","Other"] | ["Recirculation Pump","Other"] | YES | [17 empty] | Septic Tank EZ-Treat Recirculation Tank-16"sludge 2"scum ( Requires Pump Out) Pump Tank-3"sludge ( May require pump out next year) Cleaned the intake of the recirculation pump and all the spray heads in the EZ-Treat Module/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump-91805 ETM-059011/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | SD 87-738 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
01/09/2023 |  | RoutineScheduled | {FIPSCode}-STS-19857 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | PKIE-8X7KQS | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Required pumping of primary tank and a follow up inspection once completed Replaced cracked spin filter | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/23/2023 | 06:57 AM
12/01/2023 | Alternative | Routine/Scheduled | 036-STS-33869 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Outlet tee appears to be intact. Not due for pump out -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. -Aeration: Water level normal. Flushed and cleaned weir. Not due for pump out -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drip Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 9:01AM
01/03/2023 |  |  | 2007-143-0211 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Best One | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out | Replaced Blower | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/01/2023 | 12:00 AM
05/03/2023 |  | RoutineScheduled | 109-STS-32036 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 12:00 AM
09/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 2000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-15027 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | Chlorination |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | Musty | Clear | 8.000000 | 14.100000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 11/15/2023 | 02:02 PM
07/18/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | [9 empty] | Auxiliary Filter | Auxiliary Filter |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 10:30AM
05/12/2023 | Alternative | Routine/Scheduled | 136-06-0236 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 01:20 PM
10/19/2023 | Alternative | RoutineScheduled | 12-100-0214 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 2.000000 | 500 | AQUA SAFE |  | Pump |  | Mound | UV | 900.000000 | [] | [] | NA | [17 empty] | SLUDGE JUDGE OF SEPTIC TANK REVEALED 3-4" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:50 PM
10/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0241 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 10:33 AM
12/06/2023 | Alternative | Routine/Scheduled | 093-06-0224 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Not due for pump out. Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy RSV (Recirculating Splitter Valve) Condition of above Component Notes for above Component Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge pump has exceeded life expectancy. Discharge pump plumbing has exceeded life expectancy. Discharge floats have exceeded life expectancy. Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy Distribution Box Condition of above Component Notes for above Component Water level normal. Structural integrity of distribution box appears to be intact Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 10:24AM
07/07/2023 | Alternative | Follow-Up Component Maintenance | 175-03-0441 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new blower RBH2-067-1 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
02/10/2023 |  |  | 05-142-0218 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [18 empty] | Replaced the peat moss 3/22/23 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/14/2023 | 12:00 AM
02/26/2023 |  | RoutineScheduled | 113-16-062 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [8 empty] | 1686.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
04/06/2023 | Alternative | Routine/Scheduled | S 800-18-0031 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the red light and aerator not working. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The septic tank needs additional risers on it to be properly inspected in the future. The timer is set to 3 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/06/2023 | Dec 30 1899 11:30AM
01/05/2023 | Alternative | Routine/Scheduled | 157-01-129 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream, cleaned the filter in the aerator, and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | 02:00 PM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | SD-06-77 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. Some slime, spoke to customer about Do's and don'ts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
08/15/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 | Microfast Drip |  | Pump | Pressure | Drip | Not Applicable | 600.000000 | ["None"] | ["Auxiliary Filter","Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
11/01/2023 | Alternative | Reportable Incident Component Maintenance | 179-17-0074-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system alarming due to lack of maintanance. Completed routine inspection. pump tank needs to be pumped out due to sludge levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
06/20/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 750 | Sandfilter, Recirculating |  | Pump | Gravity | Trenches |  | 300.000000 | Septic Tank Baffles | Septic Tank Baffles | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/25/2023 | 02:43 PM
04/24/2023 |  | Routine/Scheduled | 234-18-164 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  |  | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [14 empty] | Pumped Out | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | Jan 1 1900 8:00PM
07/31/2023 | Alternative | Initial Visit | 147-18-0043 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 |  | AquaKlear |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/27/2023 |  | RoutineScheduled | 12-184-060 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ATL |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:00 AM
06/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | NA | Musty | Clear | 7.000000 |  |  | 1.600000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/12/2023 | 12:00 AM
10/02/2023 | Alternative | RoutineScheduled | 16-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/02/2023 | 12:00 AM
05/05/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Microfast blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
04/05/2023 |  | RoutineScheduled | 132-18-0117 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
05/02/2023 |  | RoutineScheduled | 107-04-0673 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation","BlowerCompressorAerator Operation"] | ["Dispersal System Operation","BlowerCompressorAerator Operation"] | YES | [17 empty] | The system did not need to be pumped. The pressure and blower pipes were broke outside the pump tank and were dug up and repaired. The discharge pump was pulled and sprayed off. The blower and spin filters were both cleaned. The controls were operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/24/2023 | 09:40 PM
02/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | UV light bulb and cord were replaced and are working at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/10/2023 |  | RoutineScheduled | 17-197-023 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | EZ Treat |  | Pump | Pressure | Discharge | UV | 200.000000 | ["Attached Growth Medium","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Attached Growth Medium","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/10/2023 | 12:00 AM
01/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS replaced septic pump. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/02/2023 | Alternative | RoutineScheduled | 05-160-0156 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1000 gallon precast | Fast | na | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | ["Other"] | NA | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 11:35 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | Norweco Singulair ATU | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/05/2023 |  | RoutineScheduled | 2132-10-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear |  | 12.800000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 02/02/2023 | 11:08 AM
12/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 12/20/2023 |  | 9.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
04/24/2023 |  | Routine/Scheduled | 234-16-207 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced recirculation pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | Jan 1 1900 8:30AM
10/04/2023 | Alternative | RoutineScheduled | 166-09-270 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/21/2023 |  | Reportable Incident | 234-17-0332 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/21/2023 | Jan 1 1900 8:00AM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-62 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media still looks good. HL-20, SECONDARY COUNTS-65, 0VERRIDE-15. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
12/14/2023 | Alternative | RoutineScheduled | 05-113-076 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 12:00 AM
07/14/2023 | Alternative |  | 033-07-0221-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
06/26/2023 | Alternative |  | SWP-04-259 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-91612 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Septic tank is accumulating hard grease and tampons, left copy of Do's and don'ts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
03/13/2023 |  | RoutineScheduled |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith |  |  | EcoPod | none | Gravity | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/19/2023 | 05:47 PM
05/01/2023 | Alternative | Pump-Out Only | 88-160-0363 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2500 gal approximately | [7 empty] | [] | [] | [17 empty] | Pumped Out | Pumping & Cleaning Septic Tank (1500 gallons) Pump and Clean Pump Tank/Chamber ( 1000 gallons) - pump chamber is cracked but is holding wastewater at this time - pump chamber will need to be replaced/upgraded when it fails to hold wastewater | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 12:00 AM
07/12/2023 | Alternative | Reportable Incident | 093-14-0106 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced pump and timer enable float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/12/2023 | Dec 30 1899 11:43AM
10/13/2023 | Alternative | RoutineScheduled Component Maintenance | 196-06-163 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
03/21/2023 |  | Reportable Incident | 234-18-390 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  | Pressure |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/21/2023 | Jan 1 1900 3:00PM
06/20/2023 | Alternative | Reportable Incident | NYII-B9RNK3 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/20/2023 | Dec 30 1899 3:00PM
08/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Other"] | NA | [7 empty] | 08/31/2023 | Pump Chamber | 94.000000 | [5 empty] | Will be sent separately |  | 5 year BOD sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 5:00PM
04/03/2023 |  | RoutineScheduled | 132-07-0143 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Drip | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
01/10/2023 |  | RoutineScheduled | SWP-03-39 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Annual inspection. Effluent filter was extremely dirty/clogged. Peat had a typical amount of ponding for these units, went away after raking the peat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
05/24/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None |  | 7.600000 | [14 empty] | System is currently not in use, client asked us to check it out to make sure it would be functional. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | 09:00 AM
02/22/2023 | Alternative | RoutineScheduled | 121-STS-13378 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001094 | David | King | 1.000000 | 1000 | Delta E50 EcoPod |  | Gravity | Gravity | Discharge | UV | 75.000000 | ["Disinfection"] | ["Disinfection"] | NA | [17 empty] | Cleaned UV light, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/02/2023 | 12:00 AM
03/08/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
11/01/2023 | Alternative | Routine/Scheduled | 14-142-0130 | Hanover | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Manifold flushed. Dbox is full of roots and will need to be dug up and roots removed and sealed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/01/2023 | Dec 30 1899 1:16PM
01/09/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-77598 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 75.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 05:52 PM
04/25/2023 |  | RoutineScheduled |  | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | 2" leak at camlock due to settling of pipe. Let us know if want us to come and repair. Thanks | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
03/14/2023 |  | RoutineScheduled | 132-07-0167 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 01:05 PM
11/30/2023 | Alternative | RoutineScheduled | 05-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/15/2023 |  | RoutineScheduled | 175-15-0036 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast blower needs replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/13/2023 | 11:23 AM
10/13/2023 | Alternative | Initial Visit | 800-STS-13899 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs to be pumped and when doing so pump the trash out of the Clearstream tank. The timer is set to 2 minutes every 2 hours. Did not take sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | Dec 30 1899 3:30PM
08/22/2023 | Alternative | RoutineScheduled | 175-10-0047 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 2"scum/ Ecopod ATU Tank-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out required at this time/ Air blower & capacitor is faulty and requires replacement/ Sand turned in the filter/ UV-Light sleeve cleaned and functioning properly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-8819 ETM-699h 26m/ High counts-93/ Pump timer settings- On-4m 46s Off-4h 48m. Returned on 11/17/2023 to replace the blower & capacitor- System now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/18/2023 | Alternative | RoutineScheduled | BHAR-ATSMUW | Prince Edward | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 2.000000 | 2500 | Septic | Microfast | Gravity | Gravity | Discharge | UV | 450.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Disinfection","SludgeScum Accumulation","Septic Tank Baffles","Control Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 05/18/2023 | Dec 30 1899 10:00AM
08/28/2023 | Alternative | RoutineScheduled | 10-125-158 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 6 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/28/2023 | 12:00 AM
06/06/2023 |  | RoutineScheduled | 175-16-0433 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Recirculation Pump"] | ["Recirculation Pump"] | [18 empty] | Service call only: Replaced faulty Sta-Rite Step-20 pump. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/10/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-2015 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 9:35AM
04/20/2023 |  | RoutineScheduled | 101-14-0256 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Pressure | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/23/2023 | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled | 157-12-0011 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Eljen |  | Gravity | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation","Dispersal System Operation"] | ["Distribution Pump Operation","Dispersal System Operation"] | [18 empty] | Roots in dbox and headers removed roots system still draining slow. Checked pad and found root intrusion between graven and Eljen pad. Pump piping broke in tank. Repair piping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:00 AM
04/27/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Jan 1 1900 12:48PM
07/05/2023 | Alternative | Reportable Incident | C 800-14-0108 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The timer is set to 4 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | Dec 30 1899 10:00AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-13-0550 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
05/24/2023 | Alternative | Reportable Incident Component Maintenance | 099-13-0082-SWP | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite to look at wet spots in dripfield. Inspected the entire system. Inlet riser leaks. Proposal to be sent to flush drip field and sel inlet riser.Supply ARV was full of sludge and pump intake was completely clogged not allowing the field flush to work properly. This was caused by the use of scent beads. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:08 AM
07/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0210-SPWT | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation"] | ["Recirculation Pump" ,"Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Cleaned sheets to correct minor bridging. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
07/14/2023 | Alternative | Follow-Up | 550-STS-6486 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 5.000000 |  | 1.000000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. Replaced the UV light bulb and replaced the UV light cord. The pressure switch on the aerator is not hooked up - needs to be addressed and/or fixed. The septic tank needs additional risers on it to be properly inspected in the future. The timer is set to 4 minutes every 1 hour. Took BOD and Fecal samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/14/2023 | Dec 30 1899 9:45AM
05/03/2023 | Alternative | Routine/Scheduled | -STS-15912 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Drip | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | Dec 30 1899 1:15PM
02/02/2023 | Alternative |  | 151-08-0169 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Ecoflo |  | Pump |  | Pad | Not Applicable |  | ["Other"] | ["Other"] | YES | [17 empty] | Overgrowth over top of Ecoflo cannot check pete moss. No effluent surfacing on ground. Need to get this cleared. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 12:00 AM
03/06/2023 | Alternative | RoutineScheduled | 154-96-0226 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [17 empty] | Septic Tank-6"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Interior control panel, pumps, floats and alarm are functioning properly/ No counts or etm on the panel box/ No breakout or spongy areas on the LPD Trenches and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/26/2023 | Alternative | RoutineScheduled | 13-142-0321 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | The effluent filter was partially clogged and was cleaned. The tee weir in the Clearatream aerobic tank was cleaned.There is about 8" of scum in clarifying chamber. This tank needs to be pumped out and refilled before being put back into service. The compressor filter was cleaned. The high water float activated the alarm properly when tested. The system is functioning but may not be treating as well as it should be, which may lead to drain field failure in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Dec 30 1899 11:48AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/21/2023 | Alternative |  | -STS-92486 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/03/2023 |  | RoutineScheduled | 179-STS-89429 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. inlet pipe on septic tank settled a little but still flowing good will keep an eye on it. Leak on grommet was sealed by installer. Fence still there but there is no signs of damage above ground. All 5 trenches look like they are getting same amount of water but still recommend to camera snake headers. Blower 2.93 amps. Will send proposal for camera snaking headers. Grease building up in septic tank spoke to customer about it and she said she's going to be more careful with that. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
01/27/2023 |  | Reportable Incident | SWP-04-165 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in high level due to failed pump. Replaced pump and added a inline check valve. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/25/2023 | Alternative | RoutineScheduled | SD-07-186 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | [9 empty] | [] | [] | [18 empty] | Repair | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 08:45 AM
05/15/2023 |  | RoutineScheduled | {FIPSCode}-STS-11298 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | 6.800000 |  |  | 1.400000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/16/2023 | 12:00 AM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired air supply | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
05/04/2023 |  | RoutineScheduled | 08-118-0062 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Clearstream |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The panel is having issues. Troubleshooting and repair is scheduled. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
10/22/2023 | Alternative | RoutineScheduled | SD-89-475 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | Singulair | Gravity | Pressure | Discharge | Chlorination |  | [] | [] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/24/2023 | 08:15 AM
03/10/2023 |  | RoutineScheduled | 06-197-A6 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/10/2023 | 12:00 AM
07/28/2023 | Alternative |  | 033-06-0135-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
02/27/2023 |  | Reportable Incident | 234-17-433 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/27/2023 | Jan 1 1900 9:00AM
08/17/2023 | Alternative | RoutineScheduled | 107-99-0806 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | LP |  |  |  |  | Not Applicable |  | ["Septic Tank Baffles","Other"] | ["Septic Tank Baffles"] | [18 empty] | recommend lid (Rockingham) be replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 12:00 AM
05/24/2023 | Alternative | Routine/Scheduled | 150-10-0063 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine service. Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - intact - at grade. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 11:30 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-10-0178 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend to pump all tanks due to high sludge level | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Airblower was not on when we arrived. Air blower has no power getting to it. No one was home when we were inspecting. Need to go back and investigate if breaker in house is off | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
04/21/2023 |  | Routine/Scheduled | 228-08-0957A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/21/2023 | Jan 1 1900 8:00AM
03/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | peat fiber is low and badley broken down. Peat fiber needs replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/24/2023 |  | RoutineScheduled | 08-183-181 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Septic Tank Baffles","Auxiliary Filter","Control Operation","Effluent Screens","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Disinfection","BlowerCompressorAerator Operation","Attached Growth Medium","Control Operation","Auxiliary Filter","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/24/2023 | 12:00 AM
06/09/2023 | Alternative | Reportable Incident | 234-14-417 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/09/2023 | Dec 30 1899 1:00PM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-12-0145-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | There are roots growing in around the top seam of the septic/ATU tank and around the risers where they connect to the tank. We recommend excavating by machine & resealing the tank. We also recommend treating the aerobic treatment unit with lye and pumping both tanks afterwards at the same time. We also recommend mowing the drainfield area and maintaining it in a mowed condition. Finally, we recommend removing the trees and bushes near the tanks to prevent future root infiltration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/29/2023 | Alternative | Routine/Scheduled |  | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating - pump basin fractured! BioFilter - peatmoss has ponding, compacted and requires replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/06/2023 | 07:30 AM
02/17/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | Dispersal System Operation | Dispersal System Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/20/2023 | 12:49 PM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
05/24/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Best1 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic tank 1-2" scum layer and 24-28" sludge layer, treatment unit has a trace, dishcharge has a trace of sludge good aeration. Alarm is good.. Timer is good and BLower motor still operational. Cleaned effluent filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/15/2023 |  |  | 185-STS-15925 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/15/2023 |  | 4.500000 |  |  | 2.100000 |  |  | Will be sent separately |  | BOD: 4.50 TSS: 2.10 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/15/2023 | 12:00 AM
07/03/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-53 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | ["SludgeScum Accumulation" ,"Septic Tank Baffles" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Timer float failed. Replaced float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
05/11/2023 | Alternative | RoutineScheduled | 104-14-0091 | Amherst | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service, Inc | 1942001028 | Penny | Taylor | 1.000000 | 1250 | Septic Tank | Eco Pod | Gravity | Gravity | Trenches | Not Applicable | 350.000000 | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens","SludgeScum Accumulation","Septic Tank Baffles"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/11/2023 | 09:30 AM
12/08/2023 | Alternative | Follow-Up | 09-197-A4 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity |  | Discharge | Chlorination | [9 empty] | 1.000000 | [11 empty] | Tablets are now installed | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12:00 AM
11/20/2023 | Alternative | RoutineScheduled | 2009-143-0137 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/07/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.480000 | [14 empty] | Blower not operational | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/13/2023 | 11:30 AM
11/09/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | [14 empty] | Pumped Out | Replaced recirc pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | Dec 30 1899 9:00AM
07/14/2023 | Alternative | Routine/Scheduled | NYII-BD5K76 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | Dec 30 1899 10:20AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/12/2023 |  | RoutineScheduled |  | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 4.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
06/06/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001527 | Jacob | Hott | 1.000000 | 1875 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/12/2023 | Alternative | RoutineScheduled | 06-142-0038 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/13/2023 | Alternative | Reportable Incident | S 800-13-0243 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner due to some issues with the downstairs toilet. Serviced system. Checked the pump, panel, and floats (ok). Changed the diffuser in the Clearstream and changed the filter in the aerator. The inlet tee was stopped up with grease. The Clearstream tank should be pumped and cleaned and when doing so pump the crust and grease off the top of the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | Dec 30 1899 11:45AM
02/16/2023 |  | Routine/Scheduled | 03-120-0734AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | System "chirping" - owner reports had system pumped by "others". Processing Tank - RSV, recirc pump & effluent screen serviced. - effluent screen 100% clogged, causing low level alarms when pump is activated. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/20/2023 | Jan 1 1900 7:30AM
01/26/2023 |  | RoutineScheduled | 033-STS-88575 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
07/05/2023 | Alternative | RoutineScheduled | 05-142-0027 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
02/02/2023 |  | RoutineScheduled | 179-STS-90038 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. fix problem with transducers bracket. Control panel needs new door due to broken hinges. Pump has slow down to 30 gallons per minute. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
11/03/2023 | Alternative | RoutineScheduled | 99-197-A6 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] |  |  | None | Clear | 6.000000 | 5.000000 |  | 0.000000 | [11 empty] | Lids to both tablets are missing weeds are growing over them and falling into chambers. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/10/2023 |  | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired Discharge Middle Float at time of inspection | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
02/02/2023 |  | Pump-Out Only | 18-160-0153 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 gal | Aquasafe | [6 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 12:00 AM
08/22/2023 | Alternative | RoutineScheduled | 179-06-0225-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-3 | 0-0 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 5.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 12:00 PM
07/26/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 177-17-0017-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [5 empty] | 07/11/2023 |  | 10.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Found recirc pump intake due to sludge level, cleaned. Found discharge pump intake clogged, cleaned. Drip field has few wet areas, recommend bleach flush to help restore dozing. Recommend to install sim-tech filters on both pumps to keep intakes from clogging. Recirc tank needs pump out due to sludge on pump side. Outstanding proposal for sealing leaks on riser. Will send new proposal for all the work needed. Customer was getting alarms due to alarm float in recirc tank got loose in bracket and was causing alarms, set it back in place. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
12/06/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/25/2023 | Alternative | RoutineScheduled | SD-99-215 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Flow rate has dropped 5 gpm since last cleaning & balancing of laterals. This is a relatively small drop. Recommend flushing laterals and disassembling/ cleaning the 2 globe valves before it gets any worse. Septic tank has several cracks visible above the water level, and potentially more below the water level. In addition, the concrete above the water line has some bad spalling. The outlet pipe does not appear to be properly sealed any more. Recommend replace the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
01/18/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 04:47 PM
04/10/2023 |  | Routine/Scheduled | 12-172-0099A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/10/2023 | Jan 1 1900 11:04AM
01/24/2023 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 03:40 PM
07/26/2023 | Alternative | RoutineScheduled | SD-12-389 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic / Ecopod ATU Treatment Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 07/26/2023 | Sample Chamber | 48.000000 | [5 empty] | Attached to this report |  | Septic Tank-6"sludge 3"scum/ Ecopod ATU-14"sludge 0"scum/ Pump Tank-6"sludge / Pump out required in all Tanks / Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-23269 ETM-3209h/ High level-45/ Watermeter-10924080/ Drip rate-6.7/ 35 gal./ On-7m 15s Off-1h 53m/ No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/05/2023 | Alternative | Routine/Scheduled | 05-142-0345 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | Dec 30 1899 2:58PM
02/14/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0073 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
04/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Anua and pump tank need pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
07/26/2023 | Alternative | Routine/Scheduled | 08-160-0096 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 68.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 02:00 PM
01/18/2023 |  | Routine/Scheduled | 04-172-0163A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | Jan 1 1900 7:00AM
06/27/2023 | Alternative | RoutineScheduled | 093-11-0021 | Isle of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Environmental Services of Virginia | 1942001182 | Steve | Haley | 1.000000 | 450 | CS NC 600 /DRIP |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Other"] | ["Effluent Screens","Other"] | YES | Musty | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
10/26/2023 | Alternative | Routine/Scheduled | 147-07-0151 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal level 4 in of sludge less than 1 in of solids No signs of infiltration -Recirculation Tank: Was in high level when arrived on site due to float wire had pulled out of wire nut Pumped down to normal level 9 in of suspended solids Pulled and cleaned pump Tested floats and pump all working as should Pulled and cleaned bio tube filter All plumbing intact and pump moving water properly No signs of infiltration -RSV (Recirculating Splitter Valve): Male slide is intact Pulled disassembled and cleaned Working as should -Discharge/Pump Tank: Normal level 4 in of suspended solids Tested floats and pump all working as should Pulled and cleaned pump Pump housing intact All plumbing intact and pump moving water properly No signs of infiltration -Media Sheets: Brushed and flushed laterals Flushed module until water ran clear Sprayed media sheets clean Module intact and components properly working -Control Panel 1 Recirc panel: 120 volts coming in All visual and audible alarms functioning properly Recirc pump pulled 10.7 amps All components properly working -Control Panel 2 Discharge panel: 120 volts coming in All visual and audible alarms functioning properly Discharge pump pulled 10.8 amps All components working properly -Drip Field: Pulled and cleaned spin filter No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | Dec 30 1899 8:03AM
09/12/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Cloverleaf Environmental Consulting, Inc | 1942001135 | Robert | Charnley |  |  | Advantex AX-20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/03/2023 | Alternative |  | 099-STS-92493 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89966 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [5 empty] | 07/26/2023 |  | 3.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Broken lid on pump tank riser (outlet). Broken J-box on pump tank. Spoke to customer and he said some one is coming to replace both soon, parts have been ordered. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
06/15/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Multi-Flo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
12/12/2023 | Alternative | Routine/Scheduled | 166-08-110 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Advanced Septic |  | Gravity | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 05:11 PM
03/07/2023 | Alternative |  | 101-08-0093 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Travis | Henderson | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92341 | Stafford | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Effluent Screens"] | ["Disinfection" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Risers need sealing. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 11/15/2023 | 02:02 PM
07/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001763 | Jessica | Young | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/02/2023 | 12:20 PM
02/06/2023 |  | Routine/Scheduled | 234-16-156 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 10:40AM
11/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Whitewater ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
07/26/2023 | Alternative |  | 185-STS-17318 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 |  | 8.950000 |  |  | 5.730000 |  |  | Will be sent separately |  | BOD: 8.95 TSS: 5.73 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/26/2023 | 12:00 AM
01/25/2023 | Alternative | RoutineScheduled | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 01/25/2023 |  | 13.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
10/20/2023 | Alternative | Reportable Incident | 151-15-0034 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | -Advantex Treatment Unit Engineered Textile Media Filter Cleaning - includes use of a specialized wanding tool -Install 6 floats | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 01:36 PM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/23/2023 |  | RoutineScheduled | 065-STS-32283 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:00 AM
05/30/2023 |  |  | 18-125-131 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/30/2023 |  |  |  |  | 2.500000 |  |  | Will be sent separately |  | BOD: BDL TSS: 2.50 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/30/2023 | 12:00 AM
10/25/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 7.800000 |  |  |  |  | 10/25/2023 |  | 3.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 02:30 PM
04/03/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 04/03/2023 |  | 78.000000 | [5 empty] | Will be sent separately | Inspected | Solution added to media Drip filter was clogged | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
07/28/2023 | Alternative | Routine/Scheduled | 228-17-0018 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced aerator, UV bulb and diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | Dec 30 1899 10:51AM
04/28/2023 |  | Pump-Out Only |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 01:49 PM
11/21/2023 | Alternative | RoutineScheduled | 03-192-073 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/21/2023 | 12:00 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/26/2023 | Alternative | RoutineScheduled | 153-STS-19029 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-3"sludge 2"scum/ Microfast-3"sludge 0"scum but the media is clogging and need a chemical cleaning and pump out / Pump Tank-0"sludge 0"scum/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-1970 ETM-319h 30m/ High level-14/ Watermeter-0,118,717.4/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/18/2023 | Alternative | RoutineScheduled | 157-03-118 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Maintenance Team | 1942001039 | Corey | Braxton |  |  | Advantex |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Effluent Screens","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 12:00 AM
08/20/2023 | Alternative | Routine/Scheduled | 041-STS-260164 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/20/2023 | Dec 30 1899 11:00AM
07/25/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | Dec 30 1899 1:44PM
08/08/2023 | Alternative | Routine/Scheduled | 800-11-0200 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 9:25AM
09/25/2023 | Alternative | RoutineScheduled | 159-15-0078 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | 12:00 AM
06/01/2023 | Alternative | Routine/Scheduled | 147-14-0087 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Changed the diffuser in the Clearstream and changed the filter in the aerator. The Clearstream needs to be pumped out as well as the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Dec 30 1899 1:00PM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance | SD-10-335 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter"] | ["Level Sensor Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. The low/level count in the drip panel had increased by 2. During inspection, the drip panel started an auto drip cycle. As a test, the timer float and then the RO float were pulled up (LED's turned off). The cycle continued until control power was turned off. This suggests that either the PLC is corrupted, or the timer and RO floats are failing intermittently. Low level count at 509 after all testing. In the past 21 days, system pumped an average of 1,128.8 gals/ day at 269.3 gals/ cycle (avg.) for a total of 23,706 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 09:40 AM
05/27/2023 | Alternative | RoutineScheduled | 019-STS-24847 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of solids in the septic tank. 12" of solids in recirculation tank. 6" of solids in discharge pump tank. Cleaned recirculation pump solids basket filter. Flushed both treatment unit's spray manifolds. Cleaned discharge pump solids basket filter. Tested floats, pumps and alarm. May need to be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 07:03 PM
10/17/2023 | Alternative | Routine/Scheduled | 07-192-205 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 17.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | Dec 30 1899 4:45PM
02/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | An inspection of the conventional gravity septic system was done. The septic tank inlet lid was dug up it was 34" under the ground. The septic tank was at the proper working level. A sludge judge was done and the tank only had 4" of sludge. The inlet and outlet T's are pvc. The sewer line was camera snaked and was clear. The conveyance line was camera snaked and was also clear. The 10 port concrete d-box was dug up it was 8" under the ground. It will need replaced. It is badly broken and deuterated. All 7 header lines were camera snaked and other than some sludge on the bottom of the pipes they were clear. The drain field was probed and was dry. At time of inspection the septic system was not in working condition. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
01/16/2023 |  | RoutineScheduled | 2018-143-0129 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton |  |  | Norweco Singulair |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Control Operation","Effluent Screens","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 12:00 AM
03/31/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Peat fiber needs replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
12/04/2023 | Alternative | Initial Visit | SD-13-41 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [15 empty] | As stated in 12/4/23 Report from AOSE. 1. Plant check: No alarms, tank levels normal 2. Sludge depth: 12" Scum: .25" 3. Check blower: 120v clean air filter 4. The diffuser for the Clearstream was in the wrong place. I took it out and repositioned it. 5. The high level float was bad. Replaced the float 6. Check the control panel and alarms 7. Walked over the drain field: all ok 8. I recommended that the system be pumped 9. System passed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | 08:00 AM
05/11/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Whitewater |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Yearly inspection, Septic Tank 3-4" scum, 10" sludge, try to minimize fat oil and grease in the septic. Treatment unit 1-2" scum and Trace of sludge, good aeration, cleaned air filter-very Dirty-Discharge Pump operational, Blower Alarm and Pump Alarm tested good, Drainfield in TALL Grass- owner cuts it over - System was pumped 2 years ago- | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/25/2023 |  | Follow-Up | 099-STS-89867 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank pumped out 2 days prior by others. Degraded peat was removed by hand and new peat was installed. Peat was purchased from Driller Services. Degraded peat was disposed at Spotsylvania Refuse. Distrbution box is cracked and needs to be replaced. Proposal to be sent to homeowner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
09/25/2023 | Alternative | RoutineScheduled | 08-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/25/2023 | 12:00 AM
02/14/2023 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 01:13 PM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 182-13-0293 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 09/28/2023 |  | 11.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample Normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
04/17/2023 |  | RoutineScheduled | 177-STS-90335 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
07/05/2023 | Alternative | Routine/Scheduled | 03-143-0199 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - Four Modules - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/07/2023 | 07:30 AM
12/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/25/2023 | Alternative | Follow-Up | 98-160-0344 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | 05-31-23 Completed inspection 06-23-23 serviced both tanks, pump work 07-10-23 Pump Replacement 07-25-23 Follow up on system to ensure functionality | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 12:00 AM
02/20/2023 |  | Reportable Incident | SWP-05-349 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | [9 empty] | ["Distribution Pump Operation","Level Sensor Operation"] | ["Distribution Pump Operation","Level Sensor Operation"] | YES | [17 empty] | peplaced N140 Zoeller pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 PM
08/19/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 6" of accumulated solids in septic tank. 4" of solids in discharge pump tank. Flushed treatment unit spray manifold. Cleaned recirculation pump basket filter. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 07:03 PM
04/14/2023 |  | Routine/Scheduled | 2001-143-0073 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/14/2023 | 09:58 AM
08/10/2023 | Alternative | Initial Visit | 157-16-0049 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the red light being on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The pressure switch wire was disconnected in the panel. Replaced the UV light bulb. The UV was wired to the incoming power - causing it to stay on 24/7 - wired it up through the pump float. Could not check the drainfield or mound - it was raining at the time of service. The timer is set to 5 minutes every 2 hours. Did not take samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/10/2023 | 02:15 PM
01/16/2023 |  | RoutineScheduled | 2018-143-0129 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton |  |  | Norweco Singulair |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","BlowerCompressorAerator Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 12:00 AM
03/29/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/11/2023 | 01:03 PM
09/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 2.000000 | 2750 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/14/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 11:15AM
02/28/2023 | Alternative | Initial Visit | 157-04-073 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - Real Estate Inspection. Primary septic tank - at grade minor fractures in top - effluent screen serviced. Pump Basin - plastic - float sensors, pump and controls operating. BioFilter - peatmoss in poor condition - raked /turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 10:45 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/04/2023 |  | Routine/Scheduled | 151-19-009 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:55 PM
03/20/2023 |  | Follow-Up | 177-13-0027-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pump out. Reassembled components and tank was refilled with a water truck. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
03/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced 2 gauges | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
05/15/2023 | Alternative | Routine/Scheduled | 093-18-0024 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | Dec 30 1899 11:59AM
02/20/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
10/30/2023 | Alternative |  | 033-09-0107-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/22/2023 | Alternative | RoutineScheduled | 001-STS-92986 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJI CELAN CEN 5 |  | Pump | Pressure | Pad | UV | 300.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 3-4" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | 02:25 PM
06/23/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-92539 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | SP-01-453 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Pre-sale inspection. (Septic tank was pumped out earlier today by Marshall's Septic.) Outlet end of septic tank and inlet end of pump tank are covered by a raised garden bed. Recommend remove that garden bed. The septic tank wedge lids are not watertight and need to be sealed. As a better solution, it is recommended that plastic risers to grade be added to each end of the septic tank. This would make the lids watertight and facilitate inspections and pump-outs. The pump tank plastic riser joint and conduit penetration also need to be re-sealed. The control panel alarm horn did not sound during testing. The flow meter in the hydraulic unit had been removed years ago (based on low meter reading) and replaced with a straight pipe. Installed a new flow meter today in order to complete the inspection. No effluent was dosed in first test cycle. Diagnosed and repaired 5 broken/ rotten solenoid wire connections. A leak at the backwash valve solenoid valve #1 needs to be repaired (plastic 6mm tee). Zone 2 drip rate was initially very high. Observed effluent surfacing in zone 2. Dug up and repaired a drip tubing loop connection. Continued testing. Both zones running a little higher than design, but no further surfacing seen. Recommend removing brush/briars/leaves that are covering the the manifold end of the dripfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
01/26/2023 |  | Routine/Scheduled | 01-120-0618A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - no riser access installed. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump tAnk - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | Jan 1 1900 7:00AM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["Disinfection"] | ["None"] | YES | None | Clear | [14 empty] | Inspected | Needs Alarm Bulb Audible Alarm Top off 5 Peat Pods Pumping Needed ( Customer Declined ) | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/01/2023 | 12:00 AM
06/15/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | replaced all floats and weights | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
01/20/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.510000 |  | 30.000000 |  |  | 01/20/2023 |  | 9.000000 |  |  | 4.900000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:00 AM
08/24/2023 | Alternative | Reportable Incident | 033-13-0044-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | [7 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] |  | None | Clear | [14 empty] | Inspected | replaced air compressor | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 10:00 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Drip panel audible alarm is intermittent. Recommend replacing it. Visual is still functional. Blower motor sounds odd but is functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-01-0761 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Peat needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | 02:41 PM
10/23/2023 | Alternative | RoutineScheduled | SD-07-85 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | eco-flo | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | None | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 08:40 AM
05/19/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
02/03/2023 | Alternative | RoutineScheduled | 154-04-0168 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1250 | 1-1 | 1-0 0-0 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 2.000000 | [7 empty] | 3.000000 |  |  |  | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 10:00 AM
03/14/2023 |  | Routine/Scheduled | {FIPSCode}-STS-5576 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Jan 1 1900 11:35AM
09/30/2023 | Alternative |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | See Attachment | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
05/10/2023 | Alternative | RoutineScheduled | 08-160-0027 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 |  |  | 2.000000 | 2000gal | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Septic | Discolored | [15 empty] | blower is functional, however it is making a high-pitched noise, may need to be replaced in the future | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
02/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | Dec 30 1899 11:23AM
08/22/2023 | Alternative | Follow-Up |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | Dec 30 1899 9:00AM
10/04/2023 | Alternative | RoutineScheduled | 03-197-151 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | [12 empty] | None | Clear | 6.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/05/2023 | Alternative | RoutineScheduled | C03-180-0270 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | [9 empty] | [] | [] | [18 empty] | - replaced airline from blower inside of tank onsite | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | Dec 30 1899 5:45PM
09/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Pad | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:00PM
04/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The septic/atu anua tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
06/20/2023 | Alternative | RoutineScheduled | 2005-143-0186 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
05/10/2023 | Alternative | RoutineScheduled | 13-120-0089A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Distribution Pump Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | Pungent | Dark Brown | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
01/06/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 11:30 AM
03/03/2023 | Alternative | Reportable Incident | 159-01-056 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 2000 | Clearstream |  | Pump | Pressure | Trenches | Not Applicable | 1500.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Both dosing / flow equalization pumps have failed - pulling high amperage and tripping breakers. Discharge pumps pulling high amperage and tripping breakers. One compressor appears to be failing / working intermittently. Customer given quote for repair and for routine REQUIRED service. Customer again refused service agreement. Only wanted pumpout to get the RESTAURANT through until Tuesday (03/07/2023). Pumped Septic Tank, Flow Equalization Tank and pump tank empty. Skimmed Clearstream units. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/07/2023 | 08:00 AM
06/03/2023 | Alternative | Routine/Scheduled | 041-STS-260750 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | Dec 30 1899 10:30AM
09/07/2023 | Alternative | Pump-Out Only |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 2.000000 | [8 empty] | ["Other"] | [] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
11/09/2023 | Alternative | Routine/Scheduled | 19-142-0063 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the control panel in alarm condition due to a faulted UV. I reset breakers inside control panel and UV breaker felt weak/ tripped. UV system appeared to be functioning properly after breaker was reset. Checked and confirmed power lead for UV bulb is intact and in good condition. Noted discoloration at ends of UV bulb but no definitive signs of burn out. Checked and confirmed UV bulb is functioning | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 2:18PM
01/21/2023 |  | Routine/Scheduled | 149-STS-10589 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/21/2023 | Jan 1 1900 9:30AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-26167 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Blower was turned off upon arrival. Turned blower back on and it is operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
01/09/2023 |  | RoutineScheduled | 121-STS-11907 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1000 | AS 500 |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | ["Other"] | NA | None | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 12:30 PM
03/27/2023 |  | RoutineScheduled | 08-184-5006 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/27/2023 | 12:00 AM
11/09/2023 | Alternative | Follow-Up | SWP-05-36 | King George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | Assure Plumbing & Septic LLC | 1942001502 | Wayne | Fishel | 1.000000 | 1500 | 1500 |  | Pump |  | Trenches | Not Applicable |  | [] | ["Other"] |  | Musty | Clear | [5 empty] | 11/09/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/24/2023 | 07:00 AM
07/11/2023 | Alternative | RoutineScheduled | 03-142-0155 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/02/2023 | Alternative | RoutineScheduled | VAG401044 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | None | Clear | [15 empty] | The system was not actively discharging at time of inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/29/2023 | 08:55 PM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced valve box | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
07/27/2023 | Alternative | RoutineScheduled | 085-STS-34366 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 |  | PuraSYS SBR |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0999 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
06/26/2023 | Alternative |  | 04-192-109 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/26/2023 |  | 6.830000 |  |  | 3.100000 |  |  | Will be sent separately |  | BOD: 6.83 TSS: 3.10 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/26/2023 | 12:00 AM
05/20/2023 |  | RoutineScheduled | -STS-20164 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Septic Tank Baffles"] | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Septic Tank Baffles"] | YES | Musty | Clear | 7.200000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/22/2023 | 12:00 AM
05/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | Septic Tank-10"sludge 4"scum/ Microfast-12"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time but may need pump out of the Septic- Microfast Tank next year/ UV-Light bulb is faulty and requires replacement/ Controls, pump, floats and alarms functioning properly/ Blower air filter cleaned and working correctly/ Counts: Pump-2668 ETM-595h 34m/ Peak-8/ High-13/ Watermeter-0,192,466.8/ On-14m 55s Off-3h/ No breakout or spongy areas on the drip field and dosing correctly. Returned on 6/8/2023 to replace the UV bulb, now working properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/02/2023 | Alternative | RoutineScheduled | SD-12-393 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
02/06/2023 |  | Routine/Scheduled | 234-14-417 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 2:15PM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408093 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Pad | Chlorination |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | rec pull weeds and add mulch to et bed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Primary tank pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
02/21/2023 | Alternative | RoutineScheduled | SD-14-98 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic / Ecopod ATU Treatment Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","Dispersal System Operation"] | NA | [17 empty] | Septic Tank-3"sludge 0"scum/ Ecopod-0"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Redundant off and timer enable floats are faulty and require replacement/ Watermeter is faulty and also require replacement. Counts: Pump-26596 ETM-1203h 51m On-5m 2s Off-2h/ No breakout or spongy areas on the drip field/ Blower air filter cleaned and blower working correctly. Returned on 4/18/2023 for repairs: Replaced the watermeter and the on & off floats. Controls, floats , pump and alarms now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/15/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-5384 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced aerator, pump on/off float and alarm float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/15/2023 | Dec 30 1899 3:45PM
03/14/2023 |  | RoutineScheduled | SP-05-532 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The drainfield area is overgrown. This area should be bush hogged and maintained in a mowed condition to prevent roots from growing into the drainfield lines. The pump line has been insulated where it is exposed. This should be covered with soil. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/20/2023 |  | Routine/Scheduled | 01-172-0353A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/21/2023 | Jan 1 1900 7:30AM
04/08/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel |  |  |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
01/20/2023 | Alternative | Reportable Incident | 157-04-091 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Maintenance Installed new access riser on pump tank. Installed new plumbing kit, and controls. Replaced Textile Media with new. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/23/2023 | 08:30 AM
04/22/2023 | Alternative | RoutineScheduled | 107-14-0324 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
10/27/2023 | Alternative | RoutineScheduled | 085-STS-34483 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2000 | PURAFLOW 4 PODS |  | Pump | Gravity | Mound | Not Applicable |  | [] | ["Auxiliary Filter"] | NA | Musty | Clear | [14 empty] | Inspected | EFFLUENT FILTER CLEANED SLUDGE/SCUM ACCUMULATION - SEPTIC TANK 6", PUMP STATION 2" PEAT MOSS LIGHTLY SATURATED | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | Dec 30 1899 1:00PM
06/22/2023 | Alternative | Reportable Incident Component Maintenance | SP-05-606 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in a high level alarm due to tripped pump breaker inside the house possibly caused by a power surge. Turned breaker back on and tested the system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
05/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens" ,"Dispersal System Operation"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Puraflo peat in poor condition. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Dec 30 1899 12:05PM
05/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-12"sludge 1"scum/ Pump Tank- 2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-024507 ETM-0204063/ Pump2-024242 ETM- 0362957/ Turned the peat in all 6 Puraflo Modules and peat is in good condition/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/13/2023 |  | RoutineScheduled | 177-09-0023-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | The sample chamber lid should be replaced. The peat is aging but is still providing treatment at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/30/2023 | Alternative |  | 139-00-0242 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Ted | Norris | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | 04-197-176 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ADVANTEX |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Distribution Pump Operation","Recirculation Pump","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","Control Operation","Dispersal System Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 12:00 AM
08/08/2023 | Alternative | Routine/Scheduled | 228-11-0654 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 9:40AM
10/27/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 1.000000 | 1060 | re-circulating sand filter | n/a | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Attached Growth Medium","Control Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | The entire system is in compliance with the health department regulations and approved plans. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | 05:00 PM
03/27/2023 | Alternative | RoutineScheduled | 033-STS-90101 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1500 | 2-2 1-0 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 4.000000 | [11 empty] | Inspected | system functioning properly *Address was incorrect, but found the owner in the Caroline Land records. Updated address accordingly. MWEBB 8/7/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 11:00 AM
03/13/2023 |  | RoutineScheduled | 99-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/13/2023 | 12:00 AM
07/20/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Advantex | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 3' liquid depth avg. of 12" of sludge 3" of scum, 12" loose in outlet. could use pumping. field dry, floats , alarms working, everything looks good. D pump 3696 cycles 246 hr 37 min R pump 114611 cycles, 1527 hrs 52 min | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 02:00 PM
05/01/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 |  |  | Pump | Pressure | Trenches |  | 600.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 11:38 AM
08/18/2023 | Alternative | Reportable Incident Component Maintenance | 179-STS-90067 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in a low level alarm due to failed enable float. Replaced float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0122 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | UV unit needs ballast, chord & glass housing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
11/27/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.380000 | [14 empty] | Recommended having system pumped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 139-05-0177 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Please keep drainfield mowed and around valve box clear | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
04/25/2023 |  |  | 16-113-061 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/25/2023 |  | 2.960000 | [5 empty] | Will be sent separately |  | BOD: 2.96 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 12:00 AM
01/26/2023 |  | RoutineScheduled | 179-16-0028-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Clearstream | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
06/20/2023 | Alternative | Routine/Scheduled | 196-18-0119 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 04:25 PM
02/06/2023 |  | RoutineScheduled | 003-STS-30251 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
09/01/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
10/06/2023 | Alternative |  | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed. On the far side of the mounds there is a small hole/depression. No effluent presented when cycling the system. It appears to be mole/vole burrow possibly? Advised homeowner to monitor and notify us if anything changes/. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/01/2023 | Alternative | RoutineScheduled | C-122-08-0051 | Craig | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | BioMicrobics Microfast 0.5 |  | Pump | Gravity | Trenches | Not Applicable | 250.000000 | ["None"] | ["None"] | NA | [17 empty] | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/03/2023 | 12:00 AM
06/19/2023 |  | RoutineScheduled | 182-09-0320 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | FAST 0.5 |  | Gravity | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 03:40 PM
10/04/2023 | Alternative | RoutineScheduled |  | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | Aqua aerobics |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
10/19/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | Dec 30 1899 12:05PM
04/04/2023 |  |  | 2010-143-0084 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2300 | 1000 | 1300 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter","Effluent Screens","Level Sensor Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | YES | None | Clear | 8.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 11:30 AM
01/03/2023 |  |  | 10-192-121 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/03/2023 |  | 4.040000 |  |  | 1.100000 |  |  | Will be sent separately |  | BOD: 4.04 TSS: 1.10 E.Coli: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/03/2023 | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | Dec 30 1899 5:20PM
11/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/27/2023 | Alternative | RoutineScheduled | SD-13-391 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 2000 | septic | Solar | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 07:15 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/02/2023 |  |  | 027-STS-17360 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/02/2023 |  | 2.570000 | [5 empty] | Will be sent separately |  | BOD: 2.57 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2023 | 12:00 AM
02/21/2023 |  | RoutineScheduled | 033-STS-88810 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | 182-07-0282 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | fixed zone valve leak | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
03/20/2023 |  | Routine/Scheduled | 06-120-0770A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine service. Processing Tank - recirc pump, RSV and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/21/2023 | Jan 1 1900 7:30AM
10/09/2023 | Alternative | Reportable Incident Component Maintenance | 175-12-0071 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Random alarms, outside panel only (none from indoor panel). The 5th yellow led on control panel motherboard was dimly lit as compared to the 1st led. Used test meter to confirm that the high level float in the discharge tank (identified by #5 led) was stuck partially on, enough to cause the random alarms. Float was at least a foot above the effluent. Replaced the high level float and verified proper voltage. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
08/29/2023 | Alternative | Reportable Incident | S-13-111-0126 | Botetourt | This AOSS should now return to normal function after having provided the above state routine maintenance. Other conventional maintenance performed | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Biomicrobics Micro-Fast |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Initial Visit - Blower motor had failed and owner called for replacement. We replace the unit and confirmed good aeration and the alarm stopped sounds. cleaned blower airfilter. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/30/2023 | Dec 30 1899 9:30AM
05/10/2023 |  | Routine/Scheduled | 2010-143-0125 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Air filter cleaned. Weir cleaned. System appears to be operating normally. Tank will need to be pumped out at next visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 09:40 AM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend keeping equipment off lower area of the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/02/2023 | Alternative | RoutineScheduled | 101-05-0204 | Albemarle | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | MICROFAST .5 |  | Pump | Pressure | Drip | Not Applicable |  | ["Other"] | ["Auxiliary Filter","Effluent Screens","Dispersal System Operation"] | YES | Septic | Clear | [14 empty] | Inspected | AERATOR AMPERAGE, 3A. DISTRIBUTION PUMP AMPERAGE, 7.5A SLUDGE/SCUM ACCUMULATION - SEPTIC 20", **TANK SHOULD BE PUMPED** ATU - 2" SLUDGE/SCUM ***BOTTOM 1/3 OF DRIP FIELD HEAVILY SATURATED, POSSIBLE CONSTANT WATER SOURCE COMING FROM HOUSE. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/02/2023 | 02:30 PM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 177-12-0299-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Drainfield looks nice and even. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
04/12/2023 | Alternative |  | 18-100-0472 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/13/2023 |  | RoutineScheduled | 93-160-0227 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 3000 | LPD |  | Pump | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Septic | Dark Brown | [15 empty] | All valves were opened one full turn more than original adjustments - at first calibration system pumped 4.5 inches in two minutes minimum and at second calibration on a secondary visit system ran very close to the same - all valves were open 1.5 times more and we want to recheck the system in 30-60 days. Other notes: - it is possible that drainfield is stopped up and need to be cleaned out in the future - 1 1/4in galvanized pipe and sand was used to mark and help locate all nine drainfield ends on the house side of the drainfield for future visits - valves were insulated at this time - may recommend adding some dirt onto a portion of the drainfield in the future - new user friendly manhole risers are recommended for the septic tank and pump chamber - replaced all nine globe valves - calibrated and time the system which included locating/excavating then end of all nine drainlines - repaired broken header line | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 12:00 AM
02/03/2023 | Alternative | RoutineScheduled | SD-04-063 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Drip | Not Applicable | 750.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
12/12/2023 | Alternative | Routine/Scheduled | 166-07-538 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 05:19 PM
03/27/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Routine yearly visit . Septic tank 4" scum, Sludge level-8-14"-- TOO Much Grease, - arranged pump out with foutz after our visit and owner refilled with water. Inlet Tee blocked by solid grease & T.P.(broke up blockage). Please reduce scum(FOG- Fat Oil Grease) in spectic tank to owner. No scum in treatment and a 10" of sludge in Recirc tank and 16" sludge trace in Discharge zone. Media looked good, spray pattern was good, Cleaned eflfuent filter. All Floats switched tested good. Pump opperational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 09:30 AM
03/07/2023 |  | RoutineScheduled | 181-09-0152 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | MicroFast | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped, however last year a septic tank was installed in front of the treatment tank. The bacteria and sludge that had built up on the media filter has fallen off so the treatment tank will be pumped next year. The effluent and blower filters were both cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 10:10 AM
05/12/2023 |  | RoutineScheduled | 177-STS-87476 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92341 | Stafford | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 12/01/2023 | 10:33 AM
11/29/2023 | Alternative | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Gravity | Discharge | Not Applicable |  | ["None"] | [] | [18 empty] | no discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/29/2023 | 12:00 AM
09/01/2023 | Alternative | Reportable Incident Component Maintenance | SWP-04-379 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for recirc panel and discharge panel alarming. Recirc panel was alarming due to a bad wire connection in the junction box repaired wire connection. Discharge panel alarming due to failed pump. Replaced failed pump. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/02/2023 | 05:18 AM
09/29/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 1.000000 | 1500 | Orenco Advantex AX20 |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["Control Operation","Dispersal System Operation","Effluent Screens","Auxiliary Filter"] | ["Control Operation","Dispersal System Operation","Effluent Screens","Auxiliary Filter"] | YES | [16 empty] | Inspected | Measured 6" scum and 3" solids at effluent end of septic tank-does not require a pumpout; cleaned sepitc tank effluent filter; cleaned Advantex recirculation pump screen and pump vault filter; flushed drip system laterals and cleaned spin filter; set drip system return at 15 psi; Advantex pump: 11.82 amps; drip system pump: 10.85 amps | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/26/2023 | 12:00 AM
04/04/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | d-box was parged and is in working condition at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
01/13/2023 |  | Routine/Scheduled | 18-174-0013 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/13/2023 | Jan 1 1900 4:19PM
07/13/2023 | Alternative | RoutineScheduled Component Maintenance | 179-18-0413-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
11/09/2023 | Alternative | Routine/Scheduled | SD-86-232 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  | 450.000000 | None | None | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 12:06 PM
06/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/21/2023 | Alternative | Routine/Scheduled | 228-17-0216 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced aerator, diffuser & UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | Dec 30 1899 11:10AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | SD-13-210 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The exposed section of the blower airline is in good condition now, but may need to be replaced in the future due to weathering. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
06/26/2023 | Alternative |  | 021-STS-35879 | Bland | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/26/2023 |  | 2.350000 |  |  | 2.700000 |  |  | Will be sent separately |  | BOD: 2.35 TSS: 2.70 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/26/2023 | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled | 07-113-124 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/15/2023 | 12:00 AM
10/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["Distribution Pump Operation","BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank- 6"sludge 3"scum/ Microfast ATU-4"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Found the pump is faulty and was replaced (Zoeller N-98) Controls, pump, floats and alarms are now functioning properly/ Blower air filter cleaned and blower working correctly/ Counts: Pump1-488 ETM-32h 5m/ Pump2-463 ETM-30h 59m/ Peak-9/ High level-7/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/24/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | Dec 30 1899 12:05PM
01/04/2023 |  | RoutineScheduled | 175-09-0507 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/24/2023 | 08:34 AM
09/01/2023 | Alternative | Routine/Scheduled | 228-12-0301 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | Dec 30 1899 9:40AM
12/06/2023 | Alternative | Routine/Scheduled | 159-03-024 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Structural integrity of tank appears intact. Found no signs of infiltration. Inlet and outlet tees appears intact. Pulled and Cleaned filter . Filter is discontinued model Discharge/Pump Tank Condition of above Component Notes for above Component Normal level All floats and pump are functioning properly but are aged 3 sections of pump chamber have dirt/ water infiltration 2 sections integrity have been compromised by inlet pipe hole being cut into side wall allowing them to start to close in on it self Dirt/ water intrusion around inlet pipe Uf Wires for pump come through side of riser and have dirt/ water infiltration Aeration Condition of above Component Notes for above Component Water level normal. Checked air pump is functioning properly. Customer rebuilt air pump last year it. Pulled and cleaned weir and diffuser. Diffuser is 85% clogged Air Pump/Blower Condition of above Component Notes for above Component 120v Air pressure sensor functioning properly Pulled and cleaned air filter Customer rebuilt air pump last year. Air pump pulling 1.3amps Drain Field Condition of above Component Notes for above Component No signs of surfacing Unable to locate distribution box | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 10:00 AM
04/13/2023 |  | RoutineScheduled | 101-13-0167 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | 12:00 AM
03/03/2023 | Alternative | RoutineScheduled | 139-06-0041 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
01/30/2023 |  | RoutineScheduled | 001-STS-92303 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJI CLEAN CEN 5 |  | Pump | Pressure | Mound | UV |  | [] | [] | [18 empty] | EVERYTHING WORKING AS IT SHOULD. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/31/2023 | 12:00 AM
08/29/2023 | Alternative | Routine/Scheduled | 234-17-440 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 10:30AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | NA | [7 empty] | 12/13/2023 |  | 10.000000 | [5 empty] | Will be sent separately | Inspected | Replaced buzzer and alarm float Lab sample normal | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
06/20/2023 | Alternative | RoutineScheduled | 162-04-0216 | Nelson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Dispersal System Operation","Septic Tank Baffles"] | ["Attached Growth Medium","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
08/08/2023 | Alternative | Routine/Scheduled | 154-17-0263 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Purasys |  | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Septic tank and treatment tank pumped out and refilled. Propeller replaced on aerator. System should return to normal operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/09/2023 | 07:36 AM
02/01/2023 |  | RoutineScheduled | 153-STS-19106 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast .5 | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | NA | [17 empty] | Septic -8"sludge 2"scum/ Microfast-2"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-1235 ETM-213h 40m On-10m 50s Off-8h/ Cleaned hydraulic unit filters/ 1 Zone American Drip- No breakout or spongy areas and dosing properly/ Watermeter-0095706.3 High level-13 Zone dose counts-1116 Flush-68/ 6gpm | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance | 175-08-0100 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] |  | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | Second quarter routine inspection. Blower is locked up, needs replaced. Blower appears to have been offline for a few months. Mechanical manway has been damaged and poorly repaired - recommend replace. Timer float switch is not working and other floats are mercury type which do poorly in an SBR such as this Aquarobic SBR model - recommend replace all float switches. The inside alarm panel is upside down and mounted tight up against a wall so that the door can't be opened. The pump was replaced in May of 2021. The gate valve and camlock were removed and the pump hard-piped in place. Why? This means the piping will need to be cut, from inside the tank, to service the pump. That operator also drilled a large weep hole in the pump piping. Because this system is an SBR, the effluent needs to be quiescent prior to pumping. The spray from the weep hole during a pump cycle pretty much negates the 3 hours of settling prior to the scheduled pump cycle. Owner declined repairs. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/08/2023 | 06:43 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | SD-11-168 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Evergreen trees and rose bush make access to tank lids difficult. Trees are practially growing on top of the tank and now roots have begun to penetrate the top seam of the tank. Recommend trees be removed. Observed a soft/ soggy area near the drip manifold. Nothing surfaced during the test cycle. Will check again next year. Replaced the air filter for the compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
05/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance | 154-08-0212 | Louisa | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity |  | UV |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Disinfection" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Disinfection" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | UV light was not working on arrival. This is the third time this has happened in the last 12 months. UV panel has been returned to the manufacturer for evaluation. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
06/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Attached Growth Medium","SludgeScum Accumulation"] | [] | [8 empty] | 06/01/2023 | Sample Chamber | 63.000000 | [5 empty] | Attached to this report |  | Sample Results Only/ Report on 1/13/2023 stated system needed pump out and spray of the Microfast Media. Sample taken on 6/1/2023 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/03/2023 | Alternative | RoutineScheduled | SD-15-15 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Reset all "R" counts to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/10/2023 | 05:56 AM
08/08/2023 | Alternative | Routine/Scheduled | PPIE-A6SRL5 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Microfast |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 12:44PM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-470 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:26 AM
06/13/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced (4) control floats. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/20/2023 | Dec 30 1899 12:57PM
10/11/2023 | Alternative | Reportable Incident Component Maintenance | 175-07-0311 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm in both tanks, started in discharge pump tank. Replaced original discharge pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
04/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
03/14/2023 | Alternative | Initial Visit | 800-STS-14821 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 16.000000 |  | 4.000000 | [5 empty] | Owner called due to an alarm - no noise - red light on. Serviced system. Checked the floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the pump (new serial # 2207-139414) and replaced the relay in the control panel. Wired pump through the pump float. The timer is set to 2.5 minutes every 3 hours. Took initial BOD and Fecal samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/14/2023 | Dec 30 1899 1:45PM
09/19/2023 | Alternative | RoutineScheduled | -STS-20534 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 09/19/2023 | Sample Chamber | 21.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Microfast-2"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarm are functioning properly/ Counts: Pump-173 ETM-324/ No breakout or spongy arears on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/10/2023 |  | RoutineScheduled | 179-18-0337-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Alarm call by owner. Cleaned clogged pumps & filter to restore normal flow of water. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 12:00 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0257-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex RT tank, with our staff present to assist, due to sludge accumulation in the tank. We also recommend installing a new Advantex vent kit. We also removed grass roots that are growing into the top of the Advantex module. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/14/2023 |  | Routine/Scheduled | 550-STS-6597 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Jan 1 1900 2:35PM
02/06/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | timer and bottom float replaced | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | 182-15-0302 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 07/25/2023 |  | 20.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
05/15/2023 |  | RoutineScheduled | {FIPSCode}-STS-5057 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
03/13/2023 |  | Routine/Scheduled | 04-118-0029 | Charles City | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Discharge | Chlorination | 750.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [5 empty] | 03/13/2023 | Sample Chamber | [8 empty] | Routine Service - Laboratory Sampling Conducted. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Modules (2) - media drapes & spray grids serviced. Chlorination Unit - free flowing, no tablets present! Discharge point - free of debris - no signage present. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 03/14/2023 | Jan 1 1900 7:15AM
03/07/2023 | Alternative | Initial Visit | 093-STS-14886 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 16.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. The timer was set at 3 seconds every 2 seconds changed it to 3 minutes every 2 hours. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | Dec 30 1899 2:15PM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/10/2023 |  | Reportable Incident | 234-18-388 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/10/2023 | Jan 1 1900 11:30AM
07/28/2023 | Alternative |  | SP-04-393 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
03/28/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | pumped by Greens | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
09/25/2023 | Alternative | RoutineScheduled | 166-18-0004 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/21/2023 |  | Routine/Scheduled | 550-STS-6590 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 12:45PM
09/19/2023 | Alternative | RoutineScheduled | 179-STS-92055 | Stafford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Level Sensor Operation","Recirculation Pump"] | ["Level Sensor Operation","Recirculation Pump"] | NO | [7 empty] | 09/19/2023 | Sample Chamber | 20.000000 | [5 empty] | Attached to this report |  | Septic Tank-3"sludge 2"scum/ Recirculation Tank-0" sludge / Pump Tank-0"sludge/ No pump out needed at this time/ Found alarm float was faulty and replaced during inspection/ Controls, pump, floats and alarms now functioning properly/ Recirculation pump intake cleaned/ Counts: Pump-1018 ETM-157h 26m/ High -156838/ Peak-15 ETM-10h 33m/ Watermeter-41985.02/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable | 750.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | Dec 30 1899 3:05PM
08/02/2023 | Alternative | Routine/Scheduled | 16-163-0068 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/02/2023 | Dec 30 1899 9:48AM
06/12/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [9 empty] | Level Sensor Operation | Level Sensor Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 12:24 PM
03/30/2023 | Alternative | Reportable Incident | 073-STS-105720 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced failing distribution box with new. Replaced terracotta conveyance line with new 4" PVC. Spliced Dbox to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 06:30 AM
06/30/2023 | Alternative | Reportable Incident | 128-14-0067 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Compressor failed. Replaced compressor | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The lids were not screwed in. Hardware was replaced at the time of inspection. Blower was replaced by others. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-09-0141 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | blower hot will check air supply and add 4" riser completed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
11/02/2023 | Alternative | Routine/Scheduled | S102-08-0010 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 4:00PM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
10/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 2000 | Septic | micro fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled | SD-09-140 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Puraflo | Pump | Gravity | Trenches |  |  | [] | ["Control Operation","Distribution Pump Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 0 scum, 8" of sludge. Cleaned filter, Peat moss is in good shape, alarms, pump is working. field is dry. had a bad float, All floats were replaced and are working now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 09:15 AM
12/07/2023 | Alternative | Follow-Up Component Maintenance |  | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [9 empty] | 16.000000 | 0.030000 | 1.000000 | 10.000000 |  |  | Will be sent separately | Inspected | SAMPLING/TESTING RESULTS ONLY Dissolved Oxygen: 8.06 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
08/10/2023 | Alternative | Follow-Up Component Maintenance | 177-12-0094-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Follow up. Replaced riser for spider valve. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
12/20/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | [8 empty] | 600.000000 | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend evaluating distribution box later this year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/13/2023 | Alternative | RoutineScheduled | 2006-143-0055 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Control Operation","BlowerCompressorAerator Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/17/2023 | Alternative | Reportable Incident | 166-06-191 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | [18 empty] | Maintenance - upgraded Biomicrobics control panel with new. Upgraded / replaced rotary compressor with new. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 10:30 AM
08/10/2023 | Alternative | RoutineScheduled | 107-17-0337 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
06/05/2023 | Alternative | Routine/Scheduled | 136-04-817 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | last documented service by Millers was 10/14/2020! Processing Tank - RSV, recirc pump and effluent screen serviced - effluent screen heavily clogged causing low level alarm events. Treatment Module - media sheets have bridging present - spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 07:30 AM
11/07/2023 | Alternative | RoutineScheduled | 06-113-241 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 10 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/07/2023 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90143 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [5 empty] | 10/30/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 107-19-0062 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | ["Control Operation" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 09/21/2023 |  | 15.000000 | [5 empty] | Will be sent separately | Inspected | Pumped primary tank Lab sample Normal | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
05/16/2023 | Alternative |  | 12-197-A3 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/16/2023 | [7 empty] | Will be sent separately |  | BOD: BDL TSS; BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
07/28/2023 | Alternative | RoutineScheduled |  | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 AM
05/04/2023 |  | Routine/Scheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  | 450.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | 01:27 PM
02/23/2023 | Alternative | Routine/Scheduled | unknown | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 2.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Effluent Screens","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Effluent Screens","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/23/2023 | Dec 30 1899 10:54AM
04/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | Dec 30 1899 6:20PM
07/05/2023 | Alternative | Reportable Incident | 151-13-0055 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | N/A | [16 empty] | Pumped Out | AOSS - Repair - VDH Permit Replaced pump tank with new Infiltrator IM1060 poly tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/07/2023 | 07:30 AM
07/27/2023 | Alternative |  | 03-197-A3 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/27/2023 |  | 11.700000 |  |  | 4.700000 |  |  | Will be sent separately |  | BOD: 11.7 TSS: 4.70 DC | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 12:00 AM
01/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
11/14/2023 | Alternative | RoutineScheduled | 019-STS-24961 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [17 empty] | Inspected | Routine inspection yearly inspection. 1"+ scum and 8-12" sludge in septic tank, 8" trace sludge in recirc zone, 8-10" sludge in discharge zone. System is operational. Alarm tested good. Flotas responding on control panel, Media is clean. Good spray. Cleaned effluent filter. a few alarms/alerts in history for high use- internet connected with monitoring. recircpump 801.4hrs and 67,221 cycles and discharge pump has 260.8 hrs and 2873 cycles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
05/10/2023 |  | RoutineScheduled | 099-10-0066-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Panel inside garage. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
06/16/2023 | Alternative | RoutineScheduled | 175-12-0099 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 10"scum/ Microfast-18"sludge / Pump Tank-2"sludge/ Pump out required on the Septic- Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: 3735 ETM-44587/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | UV light is not functioning as designed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
12/14/2023 | Alternative | Routine/Scheduled | 800-STS-15024 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 1:40PM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | EcoPod | EcoPod | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/17/2023 | Alternative | Routine/Scheduled | 147-07-0160 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/17/2023 | Dec 30 1899 12:17PM
02/01/2023 |  | RoutineScheduled | 033-STS-90062 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 90-Day Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
10/10/2023 | Alternative |  | 179-12-0050-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
01/24/2023 |  | RoutineScheduled | 08-192-132 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/24/2023 | 12:00 AM
12/27/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-17712 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
11/14/2023 | Alternative | Routine/Scheduled | 175-STS-15036 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 3:05PM
10/24/2023 | Alternative | RoutineScheduled | 177-17-0140-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | MicroFAST |  | Pump | Gravity |  |  | 42.460000 | [] | ["Effluent Screens","SludgeScum Accumulation","Control Operation"] | YES | Sulphitic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 03:00 PM
04/18/2023 |  |  | 05-142-0115A | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 12:00 AM
08/11/2023 | Alternative | RoutineScheduled | 171-13-0180 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Aquaklear |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Replaced the blower motor, Blower motor control/alarm box and and the septic tank riser on septic tank. All appear good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 09:30 AM
01/23/2023 |  |  | SP-04-642 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | 175-19-0017 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
03/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0243-ST | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Disinfection"] | ["Auxiliary Filter" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. System was very dirty due to lack of maintanance. Septic tank was in high level due to clogged filter. Wanded sheets. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
05/09/2023 |  | Pump-Out Only | 10-118-0017 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Pumpout of trash tank and processing tank as recommended during last service visit. Refilled with fresh water for system re-start. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Jan 1 1900 12:15PM
12/07/2023 | Alternative | Routine/Scheduled | 228-04-0270 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | Dec 30 1899 11:00AM
12/27/2023 | Alternative | RoutineScheduled | 165-STS-333930 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | E-Z Treat |  |  | Pressure | Drip | Not Applicable |  | ["None"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
12/11/2023 | Alternative | RoutineScheduled | 135-STS-24665 | Nottoway | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Piedmont | Septic Pro of Virginia | 1942001780 | Eric | Tambourine | 1.000000 | 750 gallons | FujiClean CEN5 | Norweco 1500AT UV | Pump | Pressure | Pad | UV | 300.000000 | ["Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [5 empty] | 11/15/2023 | Pump Chamber | 41.700000 |  | 1.000000 |  |  |  | Attached to this report | Pumped Out | BOD was slightly higher than permitted limits, but the system was only fully operational for 45 days. Fecal was below detection limits. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/11/2023 | 12:00 AM
04/24/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
11/13/2023 | Alternative |  | 154-05-0507 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Tony | Hamilton | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/27/2023 | Alternative | RoutineScheduled | SD-12-370 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | McKim Septic & Pumping | 1942001330 | Michelle | McKim | 1.000000 | 1250 |  |  | Gravity | Gravity | Trenches | UV |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/28/2023 | 03:30 PM
07/21/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | septic | Fast | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 4" of scum & avg 10" of sludge in inlet of tank, 10" of loose sediment and sludge in fast. 2' of loose in pump tank. could use a pumping, has a thick scum layer and is hard to get a accurate reading. Blower, alarms, pump working, field is dry Flushed the spin filter cleaned blower filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 02:00 PM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
07/19/2023 | Alternative | Routine/Scheduled | 550-STS-6896 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 10:20AM
09/08/2023 | Alternative | RoutineScheduled Component Maintenance | SP-04-280 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Fluffed media with pitchfork and was nice and dry. Media showing its age but still ok, will check next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
04/24/2023 |  | RoutineScheduled | 133 16 0039 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Septic zone under 2"scum, 6" sludge- Recirc zone 8" sludge, Discharge zone trace scum and 10" sludge -Effluent filter cleaned- spray manifold-has good even spray- media is clean. Checked Floats and alarm all operational. Ran system in test mode. All is functional; It is noted that the soil level around the lids and tank are flush with the level of the lids. Extensive Maple tree Roots were found growing into and onto the media. We notified theowner the tree and roots need removl. Recirc pump 872 hours and 84544 cycles, Discharge pump 16.5hours and 700 cycles. start up 9/17/17 2075 Days trended in compunter memory. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
01/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Trash tank level was high due to filter being clogged. Cleaned filter and level returned to normal. Recommend pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/24/2023 |  |  | {FIPSCode}-STS-78480 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/17/2023 |  | Reportable Incident | 177-08-0023-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | High level alarm. Replaced blown pilot fuse. Contactor blocked internally (swollen insulation around the coil), prevented it from pulling in the contacts and thus causing fuse to blow. Replaced contactor. Pump amp draw well within limits. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
10/20/2023 | Alternative | Routine/Scheduled | 166-06-564 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Noted signs of groundwater infiltration within septic tank riser -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Noted signs of groundwater infiltration within discharge riser. Discharge pump plumbing has exceeded life expectancy -Peat Moss: Raked and tilled peat moss. Peat moss is in good condition. -Drain Field: Found no signs of surfacing on dispersal area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 01:48 PM
09/01/2023 | Alternative | RoutineScheduled | 175-12-0266 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Clearstream ATU | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Septic Tank-6"sludge 2"scum/ ATU-4"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, floats, pump and alarms are functioning properly/ Counts: Pump-17603 ETM-1379h On-4m 17s Off-2h 20m/ High counts-17/ Watermeter-0,525,320/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/14/2023 | Alternative | Routine/Scheduled | 136-07-0088 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Real Estate Inspection Primary septic tank pumped empty, inspected, effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 PM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/16/2023 |  | RoutineScheduled | 15-120-0493A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 12:00 AM
05/23/2023 | Alternative | RoutineScheduled | Sd-02-803 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Replaced air filter for the air compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
03/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/05/2023 | Alternative | Routine/Scheduled | 136-07-0029 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: - Septic Tank: Normal level 2 in of sludge less than 1 in of solids Pulled and cleaned filter No signs of infiltration -Discharge/Pump Tank: Normal level 2 in of suspended solids Pulled and tested floats all functioning Plumbing and splice box intact Pump working and moving water properly No signs of infiltration - Aeration: Normal level 5 in of suspended solids Tested float functioning properly Pulled and cleaned diffuser Moving air as it should -Air Pump/Blower: 120 volts coming in Pulled and cleaned filter air pressure sensor intact and properly working -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Pump pulled 9.14 amps Air pump pulled .93 amps -Distribution Box: Normal level 5 lines intact and taking water properly No signs of infiltration - Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 08:30 AM
01/11/2023 | Alternative | Initial Visit | 073-STS-93195 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Intitial Visit Residence 2 years old - unknown if required 180 day sampling event occurred. - Sampling due 2026 Trash Tank - normal level Aeration Tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2023 | 07:45 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The aerator was not functioning and was replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance | 179-09-0078-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001053 | Ed | Scott | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Upon arrival, the pump tank was in low level due to a bad transducer. The bottom of the control panel is cracked. This will allow moisture into the control panel and could harm it's operation. These should be replaced as soon as possible. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance | 175-90-0354 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 02:30 PM
05/15/2023 |  | RoutineScheduled | 175-05-0878 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Floats need replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-19018 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
05/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | J&G Septic Service |  | James | Kleindl | 2.000000 | 3000 | mircofast |  | Gravity | Pressure | Drip | UV |  | ["None"] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Dec 30 1899 12:00AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/13/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:45 AM
12/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0197-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Recomend we pump out recirc tank during next years inspection. System showed alot of history for high level alarms recently. Recommend having a plumber look at the toliets to make sure they are not running. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Keep area around system mowed and maintained | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
06/26/2023 | Alternative | Reportable Incident | 115-STS-95147 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Fuji |  | Pump | Pressure | Drip | UV | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [17 empty] | Alarm event - fuji air compressor failed - replaced and restored operation. Replaced leaking access riser on Fuji Clean treatment system. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/27/2023 | 06:30 AM
05/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | EcoPod | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | pump tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
08/07/2023 | Alternative | Routine/Scheduled | 234-17-384 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 11:10AM
10/18/2023 | Alternative | Pump-Out Only | 14-160-0165 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Aquasafe | [6 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | 12:00 AM
08/20/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/20/2023 | Dec 30 1899 10:30AM
06/27/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Whitewater ATU |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 08:54 AM
07/05/2023 | Alternative | Reportable Incident Component Maintenance | SP-04-552 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to bad wire connections in the recirc tank junction box. Fixed wire connections. Infiltration on all tanks. Rods for sheets are broke and sheets are laying in the bottom of the unit. Proposal to be sent to repair the system. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/13/2023 | 10:41 AM
05/01/2023 |  |  | 133 08 0035 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001144 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | ["None"] | ["None"] | YES | None | Clear | [5 empty] | 05/08/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 12:00 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance | SD-14-73 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | A new alarm horn was installed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | SD-12-15 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0011-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Replaced zone 2 check valve. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
11/01/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-71503 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: Arrived onsite, found panel in alarm. Verified voltage. Hooked up Bluetooth and went through programming and verified it was working. Recirc was in low level. Customer has been out of town for a few days. orenco told me to reset trend data and adjust floats which I did. Put water back in the system to get it to normal operating level. Going to see if the changes work | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 10:11 AM
06/26/2023 | Alternative | Routine/Scheduled | 234-13-425 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | Replaced diffuser and UV ballast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | Dec 30 1899 12:45PM
04/10/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation"] | NA | [7 empty] | 04/10/2023 |  | 17.000000 | [5 empty] | Will be sent separately | Inspected | Repaired timer float Recommend keep grass back from system and to have easier access for future pumpings Homeowner states have found valve box in drainfield | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
03/08/2023 | Alternative | Initial Visit | 104-09-0201R | Amherst | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central |  | 1942001044 | Melvin | Collins | 1.000000 | 500 | Best 1 |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Other"] | ["Other"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/14/2023 | 04:00 PM
09/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Pods need unclogged. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/29/2023 | Dec 30 1899 4:50PM
05/16/2023 | Alternative |  | 14-100-0361 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
02/07/2023 | Alternative | Routine/Scheduled | 166-04-069 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. BioFilter - patch is intact - peatmoss in fair condition - raked / turned. Pump Basin - float sensors, pump and controls operating - basin shows bulging, but no fractures. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 07:00 AM
06/27/2023 | Alternative | Routine/Scheduled | 11-120-0314A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/27/2023 | Dec 30 1899 10:26AM
10/09/2023 | Alternative | Reportable Incident | 128-12-069 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | -Pump out: Pumped and Refilled 2500 Gallons from Septic, Aeration, and Pump Tanks -Repair: -Installation of a time-dose Control Panel | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/20/2023 | 01:16 PM
03/06/2023 |  | RoutineScheduled | 08-197-A9 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Aquaclear / Clean Machine |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 6 Chlorine 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/06/2023 | 12:00 AM
04/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/15/2023 | Alternative | RoutineScheduled | 165-STS-333460 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Lower line appears to show signs of nitrification outside of the trench area. There are no signs of wet or soggy areas though. Recommend rebalancing D-Box and checking header connection to ensure that effluent isn't bleeding down to lower line. Camera headers if necessary. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
01/13/2023 | Alternative | Routine/Scheduled | 136-05-0352 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - plastic - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 12:15 PM
02/13/2023 | Alternative | RoutineScheduled | 05-100-0935 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | [17 empty] | Pumped Out | PUMPED SEPTIC. INSTALLED A NEW N-53 SEWAGE EFFLUENT PUMP. REPLACED PEAT. EVERYTHING WORKING AS IT SHOULD. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/28/2023 | 02:50 PM
09/27/2023 | Alternative | RoutineScheduled | 195-STS-26515 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Pungent | Cloudy | 6.000000 | 0.000000 |  | 0.000000 | [11 empty] | System needs work. No DO and no tablets | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-91695 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"Dispersal System Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Dial flow needed adjustment, done. Treatment crystal clear. Blower3.19 amps. Couple spots with darker green grass on bottom line but not soft or water above ground. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
01/18/2023 |  | RoutineScheduled | SWP-05-39 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | All tanks pumped by Marshall's Septic Services today. Alarm activated 1/31/23. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/28/2023 | Alternative | RoutineScheduled | 154-03-0415 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 1.000000 | 1000 | Eco-Flow |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge/Scum Accumulation - Septic Tank 4" Peat Moss looks Recently Replaced No Power at the time of inspection - unable to check floats and pump - effluent at the appropriate levels | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 12:00 PM
04/18/2023 |  | RoutineScheduled | 179-15-0285-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Owners said they get septic odors near the tank fairly often. Treatment looks good, no perceptible odor today. Tank does not need pumped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
02/20/2023 |  | Routine/Scheduled | 234-17-131 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | Jan 1 1900 9:25AM
01/24/2023 | Alternative | RoutineScheduled | 171-15-0163 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | BioCoir |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Grease Trap - 3" crust, 6" in bottom, very little separation. Septic Tank - 6" crust, 24" solids in bottom. Treatment Tank - 12" solids in bottom. Clear effluent. Grease trap needs to be pumped. Both aerators operational. Cleaned grease trap filter. Advised owner to have septic tank and grease trap pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 07:03 PM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Some of the lines are slightly wet in the gravel. No surfacing effluent. Recommend checking back in a few months. Advised homeowner to monitor water usage and notify us if there is any change in the field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/17/2023 | Alternative | Routine/Scheduled | 075-STS-32891 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/17/2023 | Dec 30 1899 2:51PM
12/12/2023 | Alternative | RoutineScheduled | 085-STS-31805 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Carrington Pump & Irrigation | 1942001121 | John | Carrington | 2.000000 |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
03/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Dec 30 1899 12:26PM
09/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | UV |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [7 empty] | 09/26/2023 | Sample Chamber | 5.000000 |  | 130.000000 |  |  |  | Attached to this report |  | Septic Tank-2" sludge 0"scum/ EZ-Treat Recirculation Tank-2"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Recirc. pump intake cleaned/ Controls, pumps, floats and alarms are functioning properly/ Recirculation Counts: Pump-0021652 ETM-0103410/ Drip Pump Tank Counts: Pump-758 ETM-152h 23m On-12m 32s Off-2h 40m/ Peak-7/ High-15/ No breakout or spongy areas on the drip field and dosing properly/ Watermeter-0,056,429.1 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as preventative maintenance. Blower bearing noise observed. The "blower running" light (green) was burnt out, replacement assembly out of stock. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
06/29/2023 | Alternative |  | 139-13-0058 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Jim and Gwendolyn | Zimmermann | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/06/2023 | Alternative | RoutineScheduled | 179-13-0071 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, checked sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
01/27/2023 |  | RoutineScheduled | 099-11-0042-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/24/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | LP |  |  | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 12:00 AM
07/17/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | 1 | [6 empty] | [] | [] | NA | [17 empty] | Pumping Only | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled | 16-160-0025 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | Aquasafe |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [] | NA | Septic | Dark Brown | [14 empty] | Inspected | - riser needs to be installed for maintenance purposes | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | 12:00 AM
08/08/2023 | Alternative | Routine/Scheduled | 234-15-46 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | Replaced aerator and diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 3:30PM
02/23/2023 |  | Reportable Incident | 177-16-0268-SR | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity |  | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed UV bulb shutting the system down. Replaced UV bulb. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 04/04/2023 | 04:51 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/14/2023 |  | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | None | None | Pump | Pressure | Trenches | Not Applicable | 600.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS Dispersal ONLY - Routine Service Primary septic tank - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Control panel and wiring have "issues" but is functioning. Absorption fields no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 PM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance | SD-02-480 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 06:25 AM
10/02/2023 | Alternative | Routine/Scheduled | 15-142-0251 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/02/2023 | Dec 30 1899 4:31PM
05/03/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/09/2023 | Alternative | RoutineScheduled | 2129-10-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | UV | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.900000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/12/2023 | 12:00 AM
07/13/2023 | Alternative | Reportable Incident | 157-11-0201 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 3.000000 | 3000 | Clearstream | Clearstream | Pump | Gravity | Mound |  | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Cottage Treatment System Alarming - found compressor failure - diaphragm failure - repaired compressor onsite. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 07:00 AM
03/16/2023 | Alternative | RoutineScheduled | 159-09-116 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled | SD-11-01 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 500 | Multi-Flo |  | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Cloudy | [14 empty] | Pumped Out |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/16/2023 | 09:10 AM
05/19/2023 |  | RoutineScheduled |  | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Pressure gauge replaced | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
02/08/2023 |  | RoutineScheduled | 04-183-348 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Fast |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/08/2023 | 12:00 AM
03/28/2023 |  | RoutineScheduled | 181-09-0013 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | The system did not need to be pumped. The blower and spin filters were cleaned. The controls were operating as designed. There were no visible leaks in the drip field. The drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 11:00 AM
04/10/2023 |  | RoutineScheduled | 175-05-0076 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
12/15/2023 | Alternative | RoutineScheduled | SP-05-92 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-4 | 0-0 | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 7.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 01:00 PM
01/16/2023 |  | RoutineScheduled | 03-125-239 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 12:00 AM
04/17/2023 |  |  | 06-192-065 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/17/2023 |  | 13.600000 |  |  | 12.000000 |  |  | Will be sent separately |  | BOD: 13.6 TSS: 12.0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:00 AM
06/23/2023 | Alternative | Reportable Incident | SD-13-184 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | compressor failed. rebuilt compressor | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 06:01 AM
03/07/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/03/2023 | 11:24 AM
08/25/2023 | Alternative | Routine/Scheduled | 07-120-0630A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/25/2023 | Dec 30 1899 11:53AM
08/11/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Norweco Singulair ATU |  | Pump | Pressure | Drip |  | 300.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/13/2023 | 09:52 AM
05/22/2023 | Alternative | Routine/Scheduled | 04-174-0173 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Trash Tank - normal level - recommend pumpout. Aeration tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Dec 30 1899 7:30AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | Dec 30 1899 12:05PM
05/16/2023 | Alternative |  | 05-197-A3 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/16/2023 |  | 6.150000 | [5 empty] | Will be sent separately |  | BOD: 6.15 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
01/23/2023 | Alternative | RoutineScheduled | VAG408371 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [17 empty] | Pumped Out | no discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/12/2023 | 12:00 AM
09/29/2023 | Alternative | Pump-Out Only Pump-Out Only | SD-12-381 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Other"] | NA | [16 empty] | Pumped Out |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/10/2023 | 10:00 AM
01/16/2023 |  | Routine/Scheduled | 550-STS-6596 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 |  |  |  | 01/24/2023 |  | 24.000000 |  | 2600.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 8:30AM
09/28/2023 | Alternative | Routine/Scheduled | 136-05-0615 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level, 4in of sludge and less than 1in of solids. Pulled and cleaned filter. -Discharge/Pump Tank: Found at normal level, tested floats and pump all working as they should. Pumped chamber down found bulging but no cracks. -Peat Moss: Tipping bucket and trays are in working order. Raked out peat on both sides. Some roots. But peat still has life left. -Control Panel: 120 volts, audio and visual alarms working as they should. Pump pulled 7.6 amps. -Drain Field: No signs of surfacing in drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 09:12 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The panel is having issues. Troubleshooting and repair is scheduled. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
11/14/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 1.000000 | 1250 | Micro-fast bio microbics |  | Pump | Pressure | Drip | Not Applicable | 125.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation"] | YES | Musty | Cloudy | [15 empty] | system has been pumped out by others | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/21/2023 | 08:00 PM
01/19/2023 | Alternative | Routine/Scheduled | 136-08-0059 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine service. Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 07:15 AM
03/21/2023 |  | RoutineScheduled | SWP-03-683 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Observed heavily corroded brass check valve leaking externally, replaced it. Small roots growing in at wedge lids on both tanks. Owner says never any alarms. Recommend add riser to inlet end of septic tank, and reseal wedge lid at inlet end of pump tank. Peat is old but still working because owners don't use much water. Small pockets of water in each of the pods went away after raking the peat. Might need replaced next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
08/01/2023 | Alternative |  | 10-113-117 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/01/2023 |  | 5.110000 |  |  | 2.200000 |  |  | Will be sent separately |  | BOD: 5.11 TSS: 2.20 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/01/2023 | 12:00 AM
05/08/2023 |  | Routine/Scheduled | 08-163-0078 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Jan 1 1900 10:45AM
01/30/2023 |  | Routine/Scheduled | 234-18-339 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | Jan 1 1900 1:05PM
01/06/2023 |  | RoutineScheduled | 181-10-0056 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 4.000000 | 4000 | Ecopod | Biomicrobics MicroFAST | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. Effluent screen checked and cleaned. Panel boxes all functioning properly. No apparent leaks in system or drain field area. Pumps were functioning properly. Lids were properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:55 PM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0518 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
05/15/2023 |  | RoutineScheduled | 2121-12-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU |  | Pump | Gravity | Discharge | UV | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Level Sensor Operation"] | YES | Musty | Clear | 7.400000 |  |  |  |  | 05/25/2023 | Sample Chamber | 10.000000 |  | 1.000000 | 4.600000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/07/2023 | 12:00 AM
02/16/2023 |  | Routine/Scheduled | 09-142-0218 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Bionest |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration tAnk - recirc pump serviced - sprayed down media - mixing present - compressor serviced. Pump tAnk - float sensors, pump and controls operating. DBox - intact - 2 absorption lateral headers have roots present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | Jan 1 1900 7:45AM
05/19/2023 |  | Reportable Incident |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 2.000000 | 2500 | Whitewater ATU to drip |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [16 empty] | Inspected | Initial visit of an exhisting system. Septic tank at main house, No Access, Pump tank good pump runs good and alarm is good. Pumps to guest house. Guest house sepitc tank minimal scum and 6" sludge, treatment tank whitewater, 2" scum layer on top and trace sludge on bottom, Good aeration, Pump tank, 12" sludge, Located the pressure bell which was flooded and removed to reset, Owner will reinstall to get it functioning again, Needs to run or repair exhisting hose line for pressure bell and make it accessible for future maintananice. Pump run and all of sysytem if operational at this time after the air line repaird by owner. Owner runs pump in manual until it will return to auto mode. pump run time 2792 hrs 32 min, 49,968 cycles, override cycle 1669, high alarm 164, | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | 09:30 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-60912 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the sheets in your Advantex module and pumping the tank afterwards (no later than next years inspection). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
10/04/2023 | Alternative | RoutineScheduled | SD-12-330 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 50.000000 | [] | ["SludgeScum Accumulation","Dispersal System Operation"] | YES | Sulphitic | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 10:00 AM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
01/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Freedom Plumbers Corp | 1944002095 | Richard (Ricky) | Salinas | 2.000000 |  |  |  | Gravity | Gravity | Pad | Not Applicable | 360.000000 | ["Attached Growth Medium","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation","Attached Growth Medium"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | Dec 30 1899 12:00PM
06/15/2023 | Alternative | Routine/Scheduled | R-16-111-0087 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | Jan 1 1900 12:00PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-259 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend adding a 12" concrete riser to the septic Tank to improve access to the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
09/19/2023 | Alternative | RoutineScheduled | 12-197-099 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation","Recirculation Pump"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation","Recirculation Pump"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 12:00 AM
05/08/2023 | Alternative | RoutineScheduled | 133-STS-96436 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 015-STS-334434 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 12/07/2023 |  | 26.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
06/13/2023 | Alternative | RoutineScheduled | 154-12-0223 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge/Scum - Septic 6", Treatment 6", Pump Tank 6" Recirculation Pump 11.5A, Discharge Pump 11.15A Crack in Pump Station Lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 02:00 PM
11/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | Dec 30 1899 10:33AM
03/03/2023 |  | RoutineScheduled | 2017-95-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Discharge | Chlorination |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO |  |  | 7.000000 |  |  |  | E.coli-2420 MPN/100mL | 03/08/2023 | Sample Chamber | 18.000000 |  |  | 5.000000 |  |  | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Pump Tank-3"sludge 0"scum/ No pump out needed at this time/ Sand filters in good condition , no ponding and sand turned/ Controls, floats, pump, alarms, and aerator functioning properly/ Pump Counts: 050314 On- 6m Off-1h 30m/ Chlorine & Dechlor. tablet levels are good , no bridging/ Discharge point clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/07/2023 | Alternative | Routine/Scheduled | 196-12-165 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | 04:41 PM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank full. Pump appears to be functioning on hand but not under control of the panel. Homeowner is scheduled for pumping and repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
11/04/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | Modified Extended Aeration |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Total flow to drain fields October 2023 - 132,290 gallons. Average 3,780 gallons per day. All aspects of the system are operational. Wasting of settled mixed liquor from the clarifier to the digester and decanting of supernatant from digester are occurring regularly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 07:03 PM
05/15/2023 | Alternative | RoutineScheduled | 2008-01-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | Musty | Clear | 7.100000 |  |  | 2.000000 |  | 06/01/2023 | Sample Chamber | 28.000000 |  |  | 7.600000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/11/2023 | 12:00 AM
01/02/2023 | Alternative | Routine/Scheduled | 136 03 717 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | 08:15 AM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Media ponding may consider replacing media | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
11/11/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 4000 | EZ Treat Filter |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | 3rd Quarter 2023 inspection. First inspection since start-up. Grease Trap - First section - skim crust, 2" on bottom. Second section - skim crust, 12" on bottom. Septic Tank - First section - 3" crust, 6" on bottom Second Section - skim crust, 18" on bottom FEQ Tank - Low level, adjusted timers so that the pumps did not empty the tank on each cycle. Recirculation Tank - First section - 0" crust, 0" on bottom Second section - o" crust, 1" on bottom Discharge Pump Tank - First section - 0" crust, 0" on bottom Second section - 0" crust, 2" on bottom. Cleaned Filters on grease trap and septic tank. All treatment unit spray nozzles spraying unclogged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 07:03 PM
06/06/2023 | Alternative | RoutineScheduled | 061-16-398 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Fittings in hydraulic unit are leaking. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
10/09/2023 | Alternative | RoutineScheduled | 182-08-0018 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","BlowerCompressorAerator Operation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","BlowerCompressorAerator Operation"] | [18 empty] | FAST dug off and cleaned. Air line cleared | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/09/2023 | 12:00 AM
03/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Prince William | Ace Contracting Services, Inc | 1942001120 | Lawrence | Fellenz Jr. |  |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 03:09 AM
06/21/2023 | Alternative | RoutineScheduled Component Maintenance | 177-12-0076-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Disinfection" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Disinfection" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 38psi. Ax20-RT unit needs to be pumped due to sludge. Small roots on wedge lid in septic tank but no water infiltrating, inspection done while raining. Both air release valves have broken valve covers. Will send price for pumping tank and repairs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
10/30/2023 | Alternative | RoutineScheduled | 159-STS-95859 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/15/2023 | Alternative | Routine/Scheduled | 15-120-0320AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. Riser is not properly sealed to septic tank -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. -Media Sheet: Cleaned media sheets. Checked and confirmed spray pattern is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 2:14PM
07/10/2023 | Alternative | Routine/Scheduled | 228-05-0158 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None |  | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 11:30AM
01/30/2023 |  | Initial Visit | 053-STS-10397 | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 6.500000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and cleaned the diffuser in the Clearstream and cleaned the filter in the aerator. There is visible wetness on the drainfield - most likely from rain - once it dries need to keep an eye on it. The timer was set to 2 minutes every 3 hours = 260 gallons per day change it to 3.5 minutes every 3 hours = 445 gallons per day. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | Jan 1 1900 12:30PM
06/30/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 01:59 PM
12/12/2023 | Alternative | RoutineScheduled | 182-06-0198 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Best 1 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | Septic and pump tank needs to be pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Service call only: Replaced Jet Uv-Light cord and sleeve. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/17/2023 | 12:02 PM
08/24/2023 | Alternative | Routine/Scheduled | 166-14-208 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 05:45 PM
06/02/2023 | Alternative | Pump-Out Only | 234-16-58 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | Dec 30 1899 2:00PM
11/01/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 9:20AM
03/07/2023 | Alternative | RoutineScheduled | 061-STS-21344 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Grass in dripfield has gotten tall again and needs cut. High level count at 11 (after testing). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
05/15/2023 | Alternative | RoutineScheduled | 109-07-0338 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation","None"] | ["Distribution Pump Operation","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge levels- minimal scum and 5" Sludge trace in Septic tank. Tank was pumped after my visit in 2020 , Septic tank ar normal level, Peat still looks new and shows some age, the level in lower and could add some new peat atop the exhisitng to extend the life, No roots observed in Peat, In general good condition for age, has had little use. We may arrange later this summer to add peat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 05:30 PM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/07/2023 | Alternative | Routine/Scheduled | 041-STS-261222 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | Dec 30 1899 10:30AM
08/31/2023 | Alternative | Reportable Incident |  | York | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Control Operation | Control Operation | N/A | [16 empty] | Pumped Out | System reported backing up into residence - found discharge tank flooded, control panel fried by probable lightning strike. New controls ordered, Septic tank pumped and pump tank for storage | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/06/2023 | Dec 30 1899 10:45AM
08/09/2023 | Alternative | Routine/Scheduled | 550-STS-6852 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 2:10PM
04/26/2023 | Alternative | Routine/Scheduled | 175-06-0268 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Cajun Aire ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Dec 30 1899 3:12PM
03/22/2023 | Alternative |  | 101-18-0539 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Ronald | Wilcox | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0067-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Replaced damaged (possibly from weed-wacking) Advantex vent cap and cleaned dirt and grass that were collecting inside the vent pipe. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
04/21/2023 |  | RoutineScheduled | 14-118-0015 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Pressure | Drip | UV |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Distribution Pump Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/21/2023 | 12:00 AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0201-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
12/06/2023 | Alternative | RoutineScheduled | 041-STS-260323 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["Effluent Screens","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
05/17/2023 |  | RoutineScheduled | 2035-12-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Discolored | 6.800000 | 19.700000 |  | 0.000000 |  | 05/17/2023 |  | 10.000000 |  | 1.800000 | 137.000000 |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
12/20/2023 | Alternative | Initial Visit |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Fixed the grade on the pipe in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes 20 seconds every 3 hours 57 minutes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | Dec 30 1899 10:30AM
04/20/2023 |  | RoutineScheduled | 101-17-0618 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Pressure | Mound | Not Applicable | 900.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/23/2023 | 12:00 AM
12/15/2023 | Alternative | RoutineScheduled | 11-160-0106 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 2.000000 | 2500 | Delta DF60 |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Auxiliary Filter"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Auxiliary Filter"] | YES | [17 empty] | Cleaned Effluent screens; replaced blower, pump and relay; system is working correctly after repairs. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/18/2023 | 12:00 AM
01/16/2023 |  | Routine/Scheduled | 2006-143-0359 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Microfast |  | Pump | Gravity | Trenches |  | -2.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | The Microfast tank needs pumping pumping | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/16/2023 | 01:53 PM
04/24/2023 |  | RoutineScheduled | 07-113-154 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 5 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/24/2023 | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled | 109-14-0120 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge level-scum under 1" and 8" Sludge in Septic tank. 4" Sludge in treatment, 6" sludge in Pump tank.Repairs 2 leaks found in the drain field, Noticed the pressure gauge is reading 870psi on pump cycles and a blockage may exhist inside the drip lines. Nothing located. Cleaned Effluent filter and spin filter, confirmed both solenoid control valves are opening automatically and flushed both. Good aeration noted in treatment tank. Pump cycle count 5532 vs 4817 last year - 715 cycles since last visit , ETM( time) 17099 min vs 15088 Min last year = 2011 min or 33.5 hours since last visit. 44 HLA-high alarm, secondary county 732, Power failure 80, Pump run test 70 psi vs 50 psi last year on drip drainfield. system is operational but high pressure may cause more leaks or line breaks to develop until we address/discover the reason for high pressure. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
04/07/2023 | Alternative | Reportable Incident | 800-11-0117 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/07/2023 | Dec 30 1899 9:00AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
01/06/2023 | Alternative | RoutineScheduled | 061-STS-21826 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 3.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Valve box lid is missing for the ARV in front of the church. Box needs dug up and raised about 3" so lid does not contact the top of the ARV. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
09/22/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | Dec 30 1899 10:10AM
02/07/2023 |  | Routine/Scheduled | 2015-143-0169 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the UV light bulb. Changed the filter in the aerator and changed the mesh screen in the spinfilter. Installed a rebuild kit on the aerator. The aerator should be raised. The sludge is thick in the bottom of the Clearstream tank. Need a valve box and red caps for the vacuum breakers. The timer is set to 18 minutes every .75 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 01:30 PM
03/30/2023 |  | RoutineScheduled | 179-15-0063-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 2-3 0-4 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 9.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 09:00 AM
01/20/2023 | Alternative | RoutineScheduled | 103-STS-96017 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | VAG408008 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | no discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/30/2023 | 12:00 AM
12/06/2023 | Alternative |  | 195-STS-26515 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | [33 empty] | No tablets smells bad 1 DO | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | 12:00 AM
03/07/2023 |  | RoutineScheduled | 08-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
11/02/2023 | Alternative | Routine/Scheduled | 166-12-109 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 05:03 PM
10/18/2023 | Alternative | RoutineScheduled | S-06-111-0068 | Botetourt | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Dispersal System Operation","Distribution Pump Operation"] | ["Auxiliary Filter","Distribution Pump Operation"] | NO | [16 empty] | Pumped Out | The system was pumped and cleaned. The discharge pump was not working at the time of the inspection so the pump was pulled and replaced. The blower filter and spin clean filter were both pulled and cleaned. The drip field was not operating as designed at the time of inspection. The bottom zone of the two zone drain field was not taking any effluent so the header pipes were dug up and inspected. The drip lines were determined to be clogged with sludge. The spinner in the zone valve was removed to the system would work without dead heading the pump. The drip lines will be repaired as soon as the paper work is completed with a PE. The controls were operating as designed. The lids were secured. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/27/2023 | Dec 30 1899 8:30PM
02/01/2023 |  |  | {FIPSCode}-STS-79644 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | LPD | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
04/25/2023 |  |  | 085-STS-31723 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 139-08-0060 | Greene | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced discharge pump Media is ponding and needs replacement | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/06/2023 | 03:05 PM
05/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [5 empty] | 05/25/2023 |  | 18.000000 |  | 49.000000 |  |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
02/10/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-6"sludge 0"scum/ Microfast-2"sludge 0"scum/ Blower air filter cleaned and blower working properly including the alarm/ Sample box water clear with no odor/ No breakout or spongy areas on the drainfield and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/14/2023 | Alternative | Reportable Incident | 147-16-0125 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Mound | Not Applicable |  | ["Other"] | ["Other"] | YES | None | Clear | [14 empty] | Pumped Out | Pumped septic tank to allow field to dry out. Will have to add more topsoil around the edge of mound to stop water from seeping out. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/15/2023 |  |  | {FIPSCode}-STS-68407 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
12/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 9:30AM
03/15/2023 |  | Routine/Scheduled | 10-163-0022 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Air filter cleaned. System appears to be operating normally. Clearstream panel is not working correctly and needs to be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 2:26PM
10/19/2023 | Alternative | RoutineScheduled | 06-163-0244 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Best |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | 12:00 AM
08/08/2023 | Alternative | Routine/Scheduled | 228-12-0024 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 10:05AM
10/10/2023 | Alternative | Routine/Scheduled | 09-172-0207A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/10/2023 | Dec 30 1899 1:04PM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
09/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 2"scum/ Microfast-8"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-333 ETM-15h 41m/ Pump2-339 ETM-10h 53m/ Peak-5/ High-5 On-2m 52s Off-10h/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/31/2023 |  | RoutineScheduled | SP-05-359 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | The EZ Seet riser lid on the Septic Tank is damaged and should be replaced. We also recommend pumping the Advantex Recirculation Tank due to scum & sludge accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
07/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
04/19/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Jan 1 1900 12:48PM
03/27/2023 | Alternative | Routine/Scheduled | 157-10-0255 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash tank - normal level Aeration Tank - normal level - mixing present , compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 09:00 AM
04/18/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 10:41 AM
11/06/2023 | Alternative | Reportable Incident | 124-STS-2379 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, Mike Walker had already pumped out the station. Checked and confirmed floats are functioning properly. Checked pump and found it was not receiving power due to tripped residential breaker. I reset the breaker and confirmed the pump had failed. Pump was pulling about 50 amps. Checked and found that pump is under warranty. Informed homeowner of my findings and turned discharge breaker off inside control panel. Checked timers and counters inside panel. At this time, it has been about 333 days since install of pump/ control panel. Average pump cycles per day is about 43.5. Average time per time is about 130.4 minutes. Average run time per cycle is about 3 minutes. Checked with warehouse and they stated we do not have the exact pump in stock. Notified them to order it and that it's a p5. Informed homeowner that we need to order it and should be able to replace it before the end of the week. * Arrived for pump out of grinder station for Service Expert repairs * Pumped 110 gallons from grinder station Installation of new Liberty Grinder Pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/13/2023 | 09:47 AM
07/07/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 2.000000 | [8 empty] | [] | [] | [17 empty] | Pumped Out | Pumped both tanks | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | 12:00 AM
05/02/2023 |  | Routine/Scheduled | 234-12-33 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Jan 1 1900 1:20PM
03/15/2023 |  | Routine/Scheduled | 234-14-405 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 11:25AM
04/18/2023 | Alternative | RoutineScheduled | 06-100-0624 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | REPLACED PEAT. EVERYTHING WORKING AS IT SHOULD. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/30/2023 | 12:45 PM
01/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
11/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","Level Sensor Operation"] | ["Disinfection","Level Sensor Operation"] | NO | [7 empty] | 11/21/2023 | Sample Chamber | 11.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | BOD sample is in the permitted limits but the Fecal is not. We have cleaned the UV-Light sleeve and the light is now working correctly/ Septic Tank-3"sludge 0"scum/ EZ-Treat recirculation tank-0"sludge / Pump tank-0"sludge / No pump out is needed at this time/ Recirc. pump intake was cleaned/ Found the enable float was faulty and replaced during inspection/ Controls, pumps, floats and alarms are now functioning properly/ Counts: Drip Pump-2032 ETM-467h 20m/ Peak-15 ETM-111h 7m/ High-24/ No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/28/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [18 empty] | Baffle filter was clogged causing backup | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/28/2023 | 12:00 AM
03/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/14/2023 | Alternative | Reportable Incident Component Maintenance | 179-STS-86831 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Two part septic tank was pumped out prior to my visit. Onsite for system in alarm due to failed recirc pump. Replaced step 30 pump with a step 20 per Ez-treat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
08/10/2023 | Alternative | Follow-Up Component Maintenance | 177-STS-92270 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Follow up. Wire wheeled riser joint and sealed it with E6100 on septic tank inlet riser. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/15/2023 |  | RoutineScheduled | 00-125-011 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens","Control Operation","Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/15/2023 | 12:00 AM
01/05/2023 |  | RoutineScheduled | 05-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 2 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/05/2023 | 12:00 AM
09/22/2023 | Alternative | Reportable Incident | 109-03-0112 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Called due to control panel failure -replaced the control panel and system returned to normal operation | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/30/2023 | 09:30 AM
01/10/2023 |  | RoutineScheduled | 177-STS-87918 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Trees have been recently planted on/near the end of the drainfield lines. The homeowner is contacting the landscaper to remove the trees and an installer to assess and repair the lines in the appropriate manner. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
08/02/2023 | Alternative | Routine/Scheduled |  | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 07:00 AM
05/12/2023 | Alternative | RoutineScheduled | S-09-111-0048 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Biomicrobics Micro-Fast |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Routine Inspection Visit - Scum 3-4" layer on top 20" sludge layer on bottom- Fast treatment side port 20" sludge- Sample port has 24 in sludge- No smell this year. Good aeration, cleaned blower airfilter, | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
02/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic/ Microfast | Pump Tank/ EZ-Treat Recirculation Tank | Pump | Gravity | Discharge |  |  | ["BlowerCompressorAerator Operation","Recirculation Pump"] | ["Recirculation Pump","BlowerCompressorAerator Operation"] |  |  |  | 6.300000 |  |  |  | E.coli-488MPN/100mL | 02/22/2023 | Sample Chamber | 11.000000 |  | 79.000000 | 10.000000 |  |  | Attached to this report |  | Septic Tank-8"sludge 2"scum/ .75 Microfast ATU-6"sludge 2"scum/ EZ-Treat Recirculation Tank with ratio box-3"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ UV-Light sleeve cleaned and light working/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-55590 ETM-2168h 19m/ Pump2-55545 ETM-2166h 38m/ Peak-15/ High-15/ Discharge point water is clear and odor good. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/24/2023 |  | RoutineScheduled | 027-STS-17695 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/24/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [17 empty] | Septic Tank-8"sludge 3"scum/ Pump Tank-1"sludge/ No pump out needed at this time/ Puraflo Peat turned and in good condition, no ponding/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-15350 ETM-14324/ Pump2-15376 ETM-14288/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance | 175-10-0081 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Bio Barrier | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Inspection with Sampling | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
08/09/2023 | Alternative | Routine/Scheduled | 234-18-339 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 8:40AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | Best 1 | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was turned off and the blower connection to the air line had separated. It was connected and should return to proper function | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/25/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-89867 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
12/14/2023 | Alternative | RoutineScheduled | 06-184-5005 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/02/2023 | Alternative | RoutineScheduled Component Maintenance | 177-16-0101-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | The psi gauge in the drip dispersal system is not working and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 113-STS-22131 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | There was evidence of effluent surfacing previously, but no effluence was coming to the surface at the time of this inspection. We strongly recommend removing the leaves and dead grass from the dispersal area, reseeding where necessary and maintaining it in a mowed condition. We also recommend repairing the cracked plumbing in the pump tank and excavating by hand and resealing the pump tank riser. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
09/08/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-4720 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets added 12 - Bio Max tablets added | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/08/2023 | 12:00 AM
05/09/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Multiflo FTB |  | Gravity | Gravity | Trenches |  | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/21/2023 | 12:57 PM
01/10/2023 |  | RoutineScheduled | 175-00-0320 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | 6.800000 | 12.200000 | [11 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
01/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 10"scum/ Microfast-12"sludge/ Pump Tank-2"sludge/ (ALL TANKS REQUIRE PUMP OUT AND CHEMICAL CLEANING DUE TO ISSUES WITH WATER QUALITY, GREY COLOR) Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-782 ETM-37h 31m/ Pump2-720 ETM-36h 44m/ Peak-20/ High-14/ No breakout or spongy areas on the drainfield. Returned on 4/14/2023 for the chemical cleaning. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/27/2023 |  | RoutineScheduled | 03-125-034 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:00 AM
04/29/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. Flushed treatment unit spray manifold. Cleaned recirculation pump solids basket filter. Cleaned drip manifold spin filter. 0" of solids in discharge pump tank. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 07:03 PM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-288 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
09/25/2023 | Alternative | RoutineScheduled | 103-STS-102083 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system checked - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
03/13/2023 |  | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Mound |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/14/2023 | 11:13 AM
01/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2024 | 12:23 PM
07/11/2023 | Alternative | RoutineScheduled | 109-10-0286 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20 RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Alarm operational - sounds intermittent. Replace circuit board battery and reporgrammed. Tested floats all good. Ran in test mode, Good! | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/30/2023 | 09:30 AM
11/28/2023 | Alternative | Routine/Scheduled | 157-03-037 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal Level 6" of sludge and 1" of solids Riser below grade -Discharge/Pump Tank: Normal Level 3" of suspended solids All floats and pump are functioning properly however they are Aged Plumbing is aged Riser below grade -Peat Moss: Mound is blowing out Inspection port holding 18-20" of water 2 of 4 Peat moss are in fair condition Other two are ponding -Control Panel: 120v to panel All audible and visual alarms are functioning properly Pump pulled 7.19amps Panel is Aged | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/12/2023 | 02:01 PM
12/14/2023 | Alternative | RoutineScheduled | 91-184-5002 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump 1 of 2 is not functioning at this time. Homeowner is reaching out to get pump replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/02/2023 | Alternative | Reportable Incident | 150-06-379 | King William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation |  | N/A | [17 empty] | Weekend Alarm - owner reportedly hit the blower housing and broke air line plumbing - technician replaced broken airline, but still NO air reaching the treatment system. Follow-up Required. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/07/2023 | 08:30 AM
02/13/2023 |  |  | R04-180-0239 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 |  | Biogator |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] |  | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | 12:00 AM
08/04/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89328 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media has filamentus bacteria but not clogged. Treatment is crystal clear. Blower 2.79 amps. HL- 4, LL-13, OVERRIDE 0. "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
07/19/2023 | Alternative | Routine/Scheduled | 057-STS-94186 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Pressure | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - GeoMat Low Pressure Pad. Primary septic tank - normal level - effluent screen serviced (4" slip-in) - Customer requests modification to larger cannister style effluent screen. Pump Tank - float sensors, pump and controls operating. GeoMat Pad - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 07:00 AM
11/10/2023 | Alternative | RoutineScheduled | 2016-143-0117 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 250 | ClearStream |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [6 empty] | Aerator diaphragm replaced | [9 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 03:40 PM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance | 179-19-0044-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The vent cap for the Advantex module should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
09/26/2023 | Alternative | Routine/Scheduled | 02-172-0752AR | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [21 empty] | -6.000000 |  |  | 1.300000 |  |  |  |  | BOD and TSS Samples taken | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 12:24PM
04/03/2023 | Alternative | Routine/Scheduled | 093-13-0059 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Dec 30 1899 2:40PM
03/31/2023 |  | Routine/Scheduled | 085-STS-33999 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level Trash Tank - normal level Aeration Tank - mixing present - Aspirator(s) (2) - serviced. Clarifier - effluent screen serviced. Pump tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Jan 1 1900 8:00AM
05/01/2023 |  | Routine/Scheduled | 03-120-0349AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Jan 1 1900 7:15AM
01/06/2023 |  | RoutineScheduled | 05-100-0009 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | Everything is working properly and peat looks good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2023 | 01:10 PM
05/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/04/2023 |  | Routine/Scheduled | 03-163-0076 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Routine service. Processing tank pumped empty and serviced. RSV, recirc pump & effluent screen serviced. Processing tank refilled for re-start. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 7:45AM
03/10/2023 |  | RoutineScheduled | 132-18-0057 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/12/2023 | 12:00 AM
03/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/08/2023 |  | RoutineScheduled | 153-STS-20259 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
05/01/2023 |  | Routine/Scheduled | 196-14-0140 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - at grade - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 07:00 AM
03/03/2023 |  | RoutineScheduled | 175-05-0899 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs timer enable float. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | 12:26 PM
11/29/2023 | Alternative | RoutineScheduled | 06-184-5006 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Pungent | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/15/2023 |  | RoutineScheduled | 127-STS-31878 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:00 AM
07/13/2023 | Alternative | Routine/Scheduled | 166-17-0070 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank Pumped | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2500 | [9 empty] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 05:05 PM
01/13/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.510000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/13/2023 | 12:00 AM
12/11/2023 | Alternative | Routine/Scheduled | 093-12-0091 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | Dec 30 1899 12:41PM
05/19/2023 |  |  | 2014-143-0148 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 AM
01/24/2023 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced MicroFast blower & installed Norewco uv unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
05/16/2023 | Alternative | RoutineScheduled | 121-STS-12467 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 3.000000 |  | Aquasafe |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [] | NO | Septic | Dark Brown | [5 empty] | 02/22/2022 | Pump Chamber | [7 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-02-725 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-336760 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 07/05/2023 |  | 229.000000 | [5 empty] | Will be sent separately | Inspected | Replaced Uv Light | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
06/26/2023 | Alternative | Reportable Incident Component Maintenance | 175-15-0176 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Customer called because blower was not running, found blower dead so we replaced it. New blower pulling 2.74 amps. New blower seems to get hot quick possibly due to remote vent being so far from tank and being the wrong diameter. Customer is going to remove remote vent and install a charcoal filter instead. Annual will be done in 3 weeks and sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/28/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | Jan 1 1900 7:20PM
05/22/2023 | Alternative | RoutineScheduled | 11-173-009 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Puraflo | Pump | Gravity | Pad | Not Applicable | 350.000000 | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | 12:00 AM
10/20/2023 | Alternative |  | 19-142-0048 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2250 | 1250 | 1000 | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 11:00AM
05/03/2023 |  | Routine/Scheduled | 15-120-0478AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/03/2023 | Jan 1 1900 8:42AM
05/08/2023 |  |  | 2006-143-0177 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
12/19/2023 | Alternative | Routine/Scheduled | 800-08-0293 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 10:45AM
08/30/2023 | Alternative | RoutineScheduled Component Maintenance | SD-02-814 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Sanitary tee missing from inlet end of septic tank. The tee is required by VA code (12VAC5-610-815). A repair proposal to install the tee, as well as an inlet riser, will be provided to the owner. A large butterfly bush growing on top of the septic tank needs to be removed. There is also an evergreen growing close to the pods that is recommended to be removed. Replaced rotten brass check valve (leaking externally) for the pump closer to the hose. Pump was removed for this repair and verified to be an N98 from 2003. Plans called for duplex N140's. Total float separation was just 12" apart, with the override float set between the timer and high level floats. The override float had failed stuck on, so the pumps were kicking on any time the timer float closed (because of the way the panel had been wired). Replaced all 3 floats with proper spacing and the override float set as the highest float. The prior setup would have masked infiltration or a running toilet. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
01/24/2023 |  | Routine/Scheduled | 550-STS-6479 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 1:15PM
11/16/2023 | Alternative |  | 027-STS-17798 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/16/2023 |  | 8.140000 |  |  | 2.500000 |  |  | Will be sent separately |  | BOD: 8.14 TSS: 2.50 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/16/2023 | 12:00 AM
03/17/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Little scum, 3" of sludge, nothing in pump tank, pump, alarm, floats are all operational, LPD field looks good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 09:00 AM
11/21/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. -Aeration: Water level normal. Checked and confirmed aeration within tank. -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly -Drip Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 03:43 PM
01/18/2023 | Alternative |  | 150-97-240 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected | Replaced norweco agitator 1/20/23 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/03/2023 | 12:00 AM
10/09/2023 | Alternative | Pump-Out Only | 136-17-0096 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Pumped and refilled 1500 gallons from septic, aeration, and pump tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:59 PM
10/02/2023 | Alternative | Follow-Up Component Maintenance | SP-04-552 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed inlet & outlet risers. Resealed pump tank outlet riser. Re-plumbed discharge piping for easy access and installed blocks under pump. Installed new wire and conduit for recirc and discharge. Reset pod with proper fall. Corrected badly sagging sewer line. Installed proper float tree in discharge. Repaired crushes in headers. Checked discharge rate. Cut off lines 3 & 4 due to saturation, will return in 6 months to reevaluate. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/01/2023 | 06:08 AM
09/08/2023 | Alternative | Routine/Scheduled | 228-17-0058 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 9:35AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/09/2023 | Alternative | Follow-Up Component Maintenance | 061-STS-21231 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Disinfection"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Installed Jet retro UV kit. Removed uf power cable and ran individual strand wires in 3/4" conduit. Used 1/2" liquid-tite flexible conduit inside pump tank riser to connect incoming power to the Jet control box. Left enough slack to facilitate uv maintenance. Removed power uf cable for air compressor. Dug ditch, installed individual wires in conduit to power the compressor and also ran 2 wires to make the pressure switch active. Simulated failures to ensure both of these alarms functioned properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
08/05/2023 | Alternative | RoutineScheduled | -STS-20164 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | NA | Musty | Clear | 6.700000 |  |  | 2.200000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-338831 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 05/24/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
12/08/2023 | Alternative | Routine/Scheduled | 075-STS-32839 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty |  | -3.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 10:30AM
12/05/2023 | Alternative |  |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/05/2023 |  | 2.360000 |  |  | 1.400000 |  |  | Will be sent separately |  | BOD: 2.36 TSS: 1.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
05/10/2023 | Alternative | RoutineScheduled | 115-13-0049 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Septic | Presby | Gravity | Gravity | Pad | Not Applicable | 600.000000 | ["Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 09:00 AM
04/21/2023 |  | Reportable Incident |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 300.000000 | ["Attached Growth Medium","Control Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Peatmoss Biofilter changeout. Septic tank pumped for storage and drying. Removed spent biofilter media and replaced with new. Upgraded control panel, float sensors, and plumbing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 09:30 AM
02/23/2023 |  |  |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST | [6 empty] | ["Distribution Pump Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out | replaced pump and repaired pump line | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/16/2023 | 12:00 AM
03/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | E294 effluent pump needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Dec 30 1899 12:05PM
04/03/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 04/03/2023 |  | 62.000000 | [5 empty] | Will be sent separately | Inspected | filter clog was able to clean | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
09/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 2"scum/ Microfast-6"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-3102 ETM-95h 16m/ Pump2-3084 ETM-94h 51m/ Peak-68/ High-18 On-2m 22s Off-6h/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/30/2023 | Alternative | Routine/Scheduled | 041-STS-257977 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/30/2023 | Dec 30 1899 8:45AM
06/06/2023 | Alternative | Pump-Out Only | 234-15-469 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | Dec 30 1899 2:00PM
11/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-0373-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
05/09/2023 |  | RoutineScheduled | 175-02-0377 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
05/22/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip |  | 300.000000 | ["Auxiliary Filter","Dispersal System Operation"] | Auxiliary Filter | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/08/2023 | 10:07 AM
10/23/2023 | Alternative | RoutineScheduled | 182-13-0191 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | 12:00 AM
12/05/2023 | Alternative | RoutineScheduled | 182-01-0232 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Level Sensor Operation","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Level Sensor Operation"] | [18 empty] | Reattached floats to float tree. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/05/2023 | 12:00 AM
12/05/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [16 empty] | Pumped Out | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/05/2023 | Dec 30 1899 11:00AM
03/31/2023 |  | Reportable Incident | 234-17-361 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Jan 1 1900 2:30PM
12/07/2023 | Alternative | RoutineScheduled | 182-08-0212 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Replaced pressure gauge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | 12:00 AM
06/07/2023 | Alternative | RoutineScheduled |  | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 |  | MicroFAST |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | address does not exist | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled | 105-04-0162 | Appomattox | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Eco Flo | Gravity | Gravity | Trenches | Not Applicable | 350.000000 | ["Effluent Screens"] | ["Attached Growth Medium","Effluent Screens","Control Operation","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 09:00 AM
08/08/2023 | Alternative | Routine/Scheduled | 810-STS-3895 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 9:15AM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Filter element for blower canister filter replaced and air pre-filter cleaned as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
01/31/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [8 empty] | 606.000000 | [] | [] | [8 empty] | 01/10/2023 | Sample Tap | 7.000000 |  |  | 6.000000 | 90.050000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 12:00 AM
01/12/2023 |  | RoutineScheduled | 033-07-0347-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Dispersal System Operation"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend clearing the drainfield and maintaining in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
03/20/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS repaired air release valve and cleaned Advantex spray heads. Effluent pump had failed. The system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/26/2023 |  | Routine/Scheduled | 136-15-0216 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - mixing present - compressor servcied. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 08:00 AM
12/14/2023 | Alternative | RoutineScheduled Component Maintenance | VAG401599 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Multiflo FTB | none | Gravity | Gravity |  | Chlorination |  | ["Attached Growth Medium"] |  | NA | [15 empty] | Will be sent separately | Inspected | Media is clogged needs replacement No tablets present and needs repair to feeders | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/15/2024 | 10:39 AM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Cleaned the air pre-filter as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
01/23/2023 | Alternative | Routine/Scheduled | 136-14-0229 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | [19 empty] | Pumped Out | System pumped as recommended during initial service visit. Aeration tank refilled with fresh water for re-start. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 08:15 AM
02/01/2023 |  |  | 01-192-354 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 02/01/2023 | [7 empty] | Will be sent separately |  | BOD: BDL TSS: BDL SV | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/01/2023 | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled | SD-08-009 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | [9 empty] | [] | [] | [18 empty] | Repair | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:20 PM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/18/2023 | Alternative |  | {FIPSCode}-STS-23623 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/18/2023 |  | 5.540000 |  |  | 10.300000 |  |  | Will be sent separately |  | BOD: 5.54 TSS: 10.3 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
08/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 3.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
12/14/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-24121 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.500000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/18/2023 | Alternative | Reportable Incident |  | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. Effluent filter installed or maintained | Pending Review | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Septic zone minimal scum & 6" sludge- Recirc zone 4" sludge- system pumped prior by foutz0 , Bio filter cleaned, RSV cleaned, Flushed and brushed sprayer manifold, sprayed off media, No alarms since jan 2018, Ran system in test mode, flushed system, 3 floats functional functional. Found a broken recirlation line next to the tank leaking effluent on ground. scheduled to repair for the next day- | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/21/2023 | 09:30 AM
04/05/2023 |  | Pump-Out Only |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Power off at residence over weekend - owners not present - leaking toilet fixture has flooded system. Power restored - pumped pump tank empty so as to not hydraulically overload absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | Jan 1 1900 6:45AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-01158-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
10/27/2023 | Alternative | RoutineScheduled | SD-06-23 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | PuraFlo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["SludgeScum Accumulation","Control Operation","Effluent Screens"] | YES | Sulphitic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 12:00 AM
09/05/2023 | Alternative | Reportable Incident | 228-05-0605 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/05/2023 | Dec 30 1899 5:30PM
08/12/2023 | Alternative | RoutineScheduled | 019-STS-24440 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. 0" of solids in recirculation portion of treatment unit. 12"of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 07:03 PM
04/13/2023 |  | Initial Visit |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  |  |  | Gravity | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out | adjusted level of air line | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:00 AM
05/16/2023 | Alternative |  | 07-197-A4 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/16/2023 |  |  |  |  | 1.500000 |  |  | Will be sent separately |  | BOD: BDL TSS: 1.50 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
01/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/09/2023 | Alternative | RoutineScheduled | 08-160-0285 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 |  | Ecoflo (peat moss) |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation","SludgeScum Accumulation"] | [] | YES | Septic | Dark Brown | [14 empty] | Pumped Out | - tipping tray in peatmoss/pretreatment tank is cracked and not functioning properly | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/17/2023 | 12:00 AM
01/06/2023 |  | Routine/Scheduled | 800-04-0294 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing tank - RSV, recirc pump & effluent screen serviced. Treatment module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 9:15AM
01/25/2023 | Alternative | RoutineScheduled | 154-01-0052 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump Station #2: Staff replaced the light on the panel. Pump Station #4: PSI gauge needs to be replaced. Pump Station #5: Replaced 2 PSI gauges. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
04/12/2023 |  | Routine/Scheduled | 128-14-0022 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the panel (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | 08:00 AM
09/01/2023 | Alternative | Routine/Scheduled | 11-120-0018A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine service Trash Tank - normal level Aeration tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 8:00AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
04/22/2023 |  | Initial Visit | 067-STS-38843 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Control Operation"] | ["Control Operation"] | NA | [17 empty] | Initial startup inspection visit. Programmed recirculation pump timers. Tested floats, pumps and alarm. Verified that all aspects of the installation were complete and functional. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 07:03 PM
05/11/2023 |  |  | 087-STS-6715 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [18 empty] | Replaced peat moss with coconut husk media | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/12/2023 | 12:00 AM
10/25/2023 | Alternative | RoutineScheduled | 171-05-0682 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 2.000000 | 2200 | Mircofast |  | Pump | Pressure | Trenches |  | 530.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/31/2023 | 03:00 PM
05/11/2023 |  |  | 18-142-0369 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | Solids compartment needs to be pumped and the aeration tank needs to be skimmed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
08/14/2023 | Alternative |  | 11-125-158 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/14/2023 |  |  |  |  | 1.800000 |  |  | Will be sent separately |  | TSS: 1.80 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 12:00 AM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | Dec 30 1899 10:33AM
10/27/2023 | Alternative | RoutineScheduled Component Maintenance | 107-05-0323 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend removing bush near system and installing riser and pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
04/14/2023 | Alternative | Routine/Scheduled | C 800-13-0056 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | Dec 30 1899 2:37PM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88857 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Replaced UV bulb and failed low level float in discharge tank. Parts provided by the home owner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
09/29/2023 | Alternative | RoutineScheduled | 001-STS-92319 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJICLEAN CEN 5 |  | Pump | Pressure | Mound | UV | 450.000000 | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | PUMPED SEPTIC TANK-EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 11:50 AM
10/13/2023 | Alternative | Routine/Scheduled | 06-142-0542 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Due for pump out. Refill is required for proper operation and to prevent damage to components. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. Due for pump out. Refill is required for proper operation and to prevent damage to components -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 8:49AM
02/01/2023 | Alternative | Routine/Scheduled | 157-16-0042 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Delta Environmental Products, UC Series |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | 09:00 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn |  |  | Whitewater ATU | Whitewater ATU | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/29/2024 | 10:23 AM
05/04/2023 | Alternative | Routine/Scheduled | 12-160-0044 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 11:30 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower failed. New blower was installed and appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/16/2023 |  | Routine/Scheduled | 550-STS-6781 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 1:53PM
03/23/2023 |  | Routine/Scheduled | 2002-143-0227 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tnak - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump a nd controls operating. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/28/2023 | 06:45 AM
01/11/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator was not functioning upon arrival. It was replaced and is functioning as designed at this time. The effluent filter was very clogged and causing a high-level in the septic tank and possibly coming out the riser. Filter was cleaned and the lever returned to normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/15/2023 | Alternative | RoutineScheduled | 109-19-0184 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 3000 | EcoPod |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | 2nd Quarter 2023 inspection. Grease trap, First section - 1" crust, 12" of solids on bottom, Second section - 0" crust, 12" of solids on bottom. Septic Tank -skim crust, 12" of solids on bottom. EQ tank - 0" crust, 12" of solids on bottom. Denitrification tank- 0" crust, 0" of solids on bottom. Treatment Unit - 0" crust, 10" of solids on bottom. Clarifier - 1" crust, 14" of solids on bottom. Discharge tank - 0" crust, 10" of solids on bottom. Meter Reading - 273390, 46,880 gallons since 3-25-2023. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 07:03 PM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-13-0447 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | Dec 30 1899 2:30PM
02/07/2023 | Alternative | Pump-Out Only | 136-07-0245 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Repairs conducted to discrepancies noted during previous service visit. Processing tank pumped empty and serviced. RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes removed - installed new media drapes, bars, hangers and locking mechanism for AX lid. Replaced discharge plumbing kit, float sensors, and pump. System refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 07:30 AM
02/10/2023 | Alternative |  | 154-19-0141 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Racheal | LaBonte | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/29/2023 | Alternative | Routine/Scheduled | 234-13-294 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 11:15AM
08/29/2023 | Alternative | RoutineScheduled | 08-113-245 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 7 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/29/2023 | 12:00 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/12/2023 | Alternative | RoutineScheduled | 107-99-0102 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | LP |  |  | Pressure | Trenches | Not Applicable |  | ["None"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
04/17/2023 |  | Routine/Scheduled |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | Level Sensor Operation | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Intermittent high level alarms - alarm station located in crawlspace. Septic tank - normal level - effluent screen serviced. Pump Basin - on/off float sensor intermittently failing - ordered replacement. BioFilter - peatmoss in fair condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | 07:30 AM
05/03/2023 |  | Routine/Scheduled | 01-120-0209A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - recommend pumpout. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - fractured at bottom - requires replacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | Jan 1 1900 6:30AM
05/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [5 empty] | 05/09/2023 |  | 17.000000 |  | 110.000000 |  |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/07/2023 | Alternative | RoutineScheduled | 061-17-493 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 3"scum/ Microfast ATU-3"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower functioning correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-1545 ETM-172h 3m On-6m 54s Off-11h 53m/ Peakcounts-0/ High counts-20/ No breakout or spongy areas on the drainfield and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/06/2023 | Alternative | RoutineScheduled | SD-14-421 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | UV |  | ["Recirculation Pump" ,"Disinfection" ,"Level Sensor Operation" ,"Control Operation"] | ["Recirculation Pump" ,"Disinfection" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Replaced the UV lamp and rinsed out the housing. Two of the tubes in the biotube filter are broke loose from the top of the filter assembly. Not affecting performance of filter yet. Will continue to monitor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
01/30/2023 | Alternative | Reportable Incident | 103-STS-103122 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | COSS - Maintenance - GMP2018-02 Churchview Septic pumped system at beginning of last week - not able to clear clog in line. Appears that sewer line is cast iron - when jetted, removed dirt and other debris. 01/30/2023 - excavated and replaced building sewer (Cast Iron) to septic tank with 4" PVC - Installed clean out at foundation - replaced inlet "T" - reparged septic tank to seal. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/31/2023 | 07:00 AM
01/05/2023 |  | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 1.000000 | 1500 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/06/2023 |  | Routine/Scheduled | 093-06-0329 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Gravity |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 9:58PM
05/04/2023 |  |  | 03-125-300 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/04/2023 |  | 3.780000 |  |  | 7.400000 |  |  | Will be sent separately |  | BOD: 3.78 TSS: 7.40 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/04/2023 | 12:00 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/24/2023 | Alternative | Reportable Incident |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Confined space entry Septic tank pumped empty - reparged seams installed new access risers on inlet and outlet. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 02:30 PM
06/08/2023 |  |  | 127-STS-33209 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Purasys |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Recirculation Pump","Level Sensor Operation","Distribution Pump Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 12:00 AM
04/25/2023 |  | Reportable Incident | 175-19-0119 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Alarm reported, but no alarm on. Possible high level alarm in recirc tank due to clogged intake on recirc pump. Cleaned intake and reinstalled pump. No other problems found. System is limited to 270 gals/day. Recommend installing Simtech pump screen for the recirc pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/10/2023 | 05:56 AM
06/03/2023 | Alternative | RoutineScheduled | 067-STS-38876 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Raised recirculation pump float switches to insure proper recirculation rates. 6" of accumulated solids in septic tank. 0" of solids in discharge pump tank. Cleaned recirculation pump basket filter. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 07:03 PM
02/22/2023 |  | RoutineScheduled | 027-STS-17361 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/22/2023 | 12:00 AM
08/08/2023 | Alternative | Routine/Scheduled | 228-18-0109 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 8:10AM
06/16/2023 | Alternative | RoutineScheduled | 175-08-0406 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank to Pump Tank to Puraflo Modules | Discharge pump tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [17 empty] | Septic Tank-4"sludge 1"scum/Puraflo Pump Tank -1"sludge/ Discharge pump tank-2"sludge/ No pump out needed at this time/ Puraflo peat turned in all 5 modules and is in good condition at this time/ Controls, pumps, floats and alarms are functioning properly/ Counts: Puraflo Pump- 28465 ETM-594860/ Discharge Pump- 6785 ETM-79940/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/28/2023 | Alternative |  | 139-05-0116 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Denis | Torres | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/02/2023 |  | RoutineScheduled | 04-125-163 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/02/2023 | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled | VAG408329 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.660000 |  |  |  |  | 10/03/2023 |  | 14.000000 |  |  | 9.000000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/13/2023 | 04:50 PM
02/07/2023 |  | Routine/Scheduled | 199-04-0549 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - Peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | Jan 1 1900 8:45AM
08/04/2023 | Alternative | RoutineScheduled | 175-18-0282 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | UV |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | Septic Tank-10"sludge 4"scum/ Microfast-14"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ Pump out highly recommended on the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-002843 ETM-0003243 On-1m 33s Off-6h 42m/ No breakout or spongy areas on the drainfield and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 |  |  | 03-163-0221 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 4.000000 |  | Advantex |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation","Recirculation Pump"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 12:00 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/27/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.380000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 02:30 PM
12/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Virginia Beach | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 12:00 AM
01/27/2023 |  | Routine/Scheduled | 093-03-0312 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Cajun Aire ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | Jan 1 1900 1:05PM
09/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  | 1500Gal |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 2:45PM
07/05/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-2052 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | [9 empty] | ["None"] | [] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 12:00 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 4.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Audible alarm for DF pump was not functioning. It was replaced at time of inspection. 3 Spray heads on the EZ treat unit were clogged. Lines were flushed and nozzles were replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/25/2023 |  |  | 05-125-003 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/25/2023 |  | 18.300000 |  |  | 22.000000 |  |  | Will be sent separately |  | BOD: 18.3 TSS: 22.0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 12:00 AM
12/27/2023 | Alternative | RoutineScheduled | 10-160-0092 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [7 empty] | 12/27/2023 | Sample Tap | [6 empty] | Will be sent separately | Inspected | - recommend riser installation for adequate maintenance access - recommend tank be pumped/cleaned -two 4in caps need to be replaced on outlet line | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/21/2023 | Dec 30 1899 1:30PM
08/09/2023 | Alternative | Routine/Scheduled | 234-17-322 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 8:15AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/12/2023 | Alternative | Routine/Scheduled | 19-172-0074AR | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | Dec 30 1899 11:09AM
03/10/2023 |  | RoutineScheduled | 132-18-0056 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/12/2023 | 12:00 AM
05/01/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | 2 shocks and brackets repaired rsv repair and media hanger repaired Installed surge arrestor | This AOSS should now return to normal function after having provided the above state routine maintenance | 06/21/2023 | 03:35 PM
05/09/2023 |  | Follow-Up | 177-10-0189-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 05/09/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
04/04/2023 |  | RoutineScheduled | 175-03-0208 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | 07:20 PM
12/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 6.800000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/12/2023 | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89165 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump" ,"Dispersal System Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
06/15/2023 | Alternative | Initial Visit | 11-120-0344A | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - Service Provider = Madison Environmental Owner requested 2nd Opinion Trash Tank - normal level Aeration Tank - normal level - mixing present - aspirator serviced. Clarifier - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Absorption field - mulitple areas of surfacing noted. Laterals used Infiltrator Chambers. Several units are damaged. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/22/2023 | Dec 30 1899 7:00AM
02/14/2023 |  | Routine/Scheduled | 2007-143-0089 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | PremierTech, EFX | PremierTech, EFX | Pump | Gravity | Trenches | Not Applicable | 750.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Biofilter #1 - tank has a fracture present - peatmoss ponding - raked / turned. Biofilter #2 - peatmoss in good condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 10:45 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/13/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0313 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Removed roots from surge box. D-box is buried, not inspected. In the past 30 days, system averaged 9.7 distribution cycles per day at 1.3 minutes per cycle. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
02/27/2023 |  | RoutineScheduled | 09-125-077 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/27/2023 | 12:00 AM
06/05/2023 | Alternative | RoutineScheduled | 139-00-0271 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 11:35 AM
05/15/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Pressure | Drip |  | 450.000000 | ["Attached Growth Medium","Control Operation","Effluent Screens"] | Effluent Screens | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/19/2023 | 10:37 AM
11/14/2023 | Alternative | Pump-Out Only |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [8 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | Dec 30 1899 9:00AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/05/2023 |  | RoutineScheduled | 04-100-0785 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1250 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | EVERYTHING WORKING PROPERLY. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | 12:30 PM
05/04/2023 | Alternative | Routine/Scheduled | 136-07-0239 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tnak - normal level - effluent screen serviced. BioFilter - peatmoss in good condition - raked / turned. Pump Basin - float sensors, and controls operating - Pump replaced - failed. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 07:00 AM
02/09/2023 |  | RoutineScheduled | 177-STS-90175 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
10/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
04/03/2023 |  | RoutineScheduled | 133 04 1026 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | BioWheel |  | Pump | Gravity | Trenches |  |  | ["None"] | [] | NA | [7 empty] | 03/22/2023 | Pump Chamber | 0.000000 |  |  | 1.800000 | 6.300000 |  | Will be sent separately |  | Monthly Report. Total flow for month of March 2023 - 62,890 gallons. Average daily flow - 2,029 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 07:03 PM
05/24/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 3000 | anua (puraflo) |  | Pump | Gravity | Trenches | Not Applicable | 100.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [15 empty] | System is operational and in general conformance with the health department and approved plans. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 11:00 AM
06/23/2023 | Alternative | Routine/Scheduled | 136-99-0583 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls operating. DBox - plastic - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | 01:00 PM
11/02/2023 | Alternative | Routine/Scheduled | 085-STS-32325 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/02/2023 | Dec 30 1899 12:15PM
10/11/2023 | Alternative | RoutineScheduled | 153-STS-19007 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ EZ-Treat Recirculation Tank-4"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Recirc. Pump intake cleaned/ Counts: Recirc Pump-0090223 ETM-0560485/ Drainfield Pump-656 ETM-30h 31m On-2m 48s Off-12h Peak-0/ High-7/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/05/2023 | Alternative | Reportable Incident | 136-16-0140 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a red light on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The Clearstream tank needs to be pumped and cleaned out and the septic tank needs to be pumped out. The timer is set to 4 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/05/2023 | 01:45 PM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0347 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
06/30/2023 | Alternative | Routine/Scheduled | 234-17-198 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 11:45AM
02/15/2023 | Alternative | Initial Visit | 166-12-178 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - Alarming. Primary septic tank - normal level Aeration Tank - compressor failure - replaced - mixing restored. Pump Tank - float sensors failed - replaced - pump & controls operating. DBox - lid fractureed | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/16/2023 | 08:15 AM
03/30/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
12/12/2023 | Alternative | Reportable Incident Component Maintenance | 179-12-0191-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to burnt wire connections in discharge junction box not sending proper signals back to the septic panel. Repaired wires and system pumped itself back to normal levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
01/13/2023 |  | RoutineScheduled | 09-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Aerobic |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/13/2023 | 12:00 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/25/2023 | Alternative | RoutineScheduled | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 01/25/2023 |  | 81.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Bio Barrier | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | replaced bad discharge pump | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
04/19/2023 |  |  | 2003-143-0319 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 12:00 AM
01/06/2023 | Alternative | RoutineScheduled | SD-98-297 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 3.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
01/12/2023 |  | Follow-Up | 179-12-0204-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to replace step 10 pump in recirc tank not pumping at the proper rate with a step 30 pump. While onsite spinners were clogged not processing the proper amount of waste water. Homeowner is doing some remodeling inside the house and rinsed paint brushes out in the sink. I will follow up in a couple of weeks to see if new pump will keep spinners clean. If not proposal will be sent to pump out the entire system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/01/2023 |  | RoutineScheduled | 133 08 0250 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Norweco |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic under 1 " scum layer on top and 8" sludge on bottom. Aeration zone has good aeration and aerator pump is operational. Pump tank has 6" trace sludge. Norweco alarm test good, the Biofilter was cleaned, minimal sludge and scum in the system and still like new. float switch, alarm float are both good, pump is good and settling looks to be the same as last year and not an issue.. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/23/2023 |  | RoutineScheduled |  | Cumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Eco Pod | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | Jan 1 1900 8:30AM
01/04/2023 | Alternative | RoutineScheduled | SD-15-053 | Orange | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Clearstream | none | Pump | Gravity |  | UV |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted previously, the Salcor UV is light is not working so we did not take the required effluent sample. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | 07:17 AM
07/07/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches |  | 450.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 10:37 AM
03/06/2023 | Alternative | Routine/Scheduled | 136-08-0340 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 10:15 AM
09/22/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | Dec 30 1899 11:20AM
06/05/2023 |  | Routine/Scheduled | 2008-143-0145 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Pump | Gravity | Pad |  |  | ["Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/05/2023 | 08:40 AM
04/17/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:00 AM
07/06/2023 | Alternative | RoutineScheduled | 003-STS-31768 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | NORWECO |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 12:00 AM
12/01/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/18/2023 | Dec 30 1899 8:36AM
01/23/2023 | Alternative | Routine/Scheduled | 166-08-178 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 1500 | Ecoflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 07:05 PM
10/26/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 2:15PM
06/14/2023 |  |  |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 109-STS-32032 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
09/21/2023 | Alternative | Reportable Incident | 107-04-0516 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Distribution Pump Operation","Effluent Screens"] | ["Distribution Pump Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | replaced dispersal pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/09/2024 | 12:00 AM
04/07/2023 |  |  | 085-STS-33665 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | 12:00 AM
10/11/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
07/12/2023 | Alternative | Routine/Scheduled | 550-STS-6332 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 9:30AM
09/01/2023 | Alternative | Routine/Scheduled | 234-14-213 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | Dec 30 1899 12:25PM
02/22/2023 |  | RoutineScheduled | 177-STS-88791 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Auxiliary Filter"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
04/20/2023 |  | RoutineScheduled | 179-09-0063-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
12/12/2023 | Alternative | Routine/Scheduled | 095-STS-6869 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 11:00AM
05/22/2023 |  | RoutineScheduled | 175-18-0327 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation"] | ["Disinfection","BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-10"sludge 4"scum/ Microfast-8"sludge Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-11525 Run Time-355/ Override-8/ Hand-31/ High-8/ Jet UV-Light and cord requires replacement/ No breakout or spongy areas on the drip field and dosing correctly. Returned on 5/26/2023 and replaced the UV-Light and cord, cleaned the sleeve. Tested and now working as designed. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/06/2023 | Alternative | Initial Visit | 550-STS-6650 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 8.000000 |  | 1.000000 | [5 empty] | Owner called due to red light on since Saturday - lost power. Serviced system. Need to pump and clean out the tanks due to them having paint in them. The grade on the pipe in the Clearstream is not okay - needs to be addressed. Replaced the diffuser in the Clearstream, replaced the filter in the aerator, and replaced the mesh screen in the spinfilter (full of paint). Fixed the UV. Re-wired the buzzer. The timer is set to 9 minutes every 1 hour. Took initial BOD and Fecal samples. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/06/2023 | Dec 30 1899 9:30AM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/04/2023 |  | RoutineScheduled | 2129-10-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU |  | Pump | Gravity | Discharge | UV | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 7.400000 |  |  |  |  | 03/06/2023 | Sample Chamber | 2.000000 |  |  | 1.000000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/18/2023 | 12:00 AM
11/30/2023 | Alternative |  | 18-142-0302 | Hanover | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chickahominy | Revised Environmental, LLC | 1942001508 | Danna | Revis | [9 empty] | [] | [] | [18 empty] | I arrived onsite around 10:30am on 11/30/23. Upon opening the risers, I noticed the recirculation tank was in high level, with all the floats submerged. However, the system was not alarming. The control panel was attempting to run a cycle, but the pump was not functioning. After checking connections at the splice box and control panel, it appears the recirculation pump and alarm float have failed. This is causing the water level in the recirc section of the tank to remain higher than the system was designed to accommodate. Also, untreated effluent is able to fall into the discharge tank, which can cause premature failure in drip fields. As such, the pump and float should be replaced. Cleaned effluent filter and spin filter. Both seemed to be functioning well and in good shape. Flushed drip field manually until water returned clear. Could not check the function of treatment unit as the pump that feeds it has failed. To summarize, the system needs a new recirculation pump, and most likely a new alarm float. The other components that I was able to inspect and check for function were working as intended. The system has been installed for four years, so a pump out within the next year is recommended. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/01/2023 | Dec 30 1899 1:30PM
10/19/2023 | Alternative | RoutineScheduled | R16-180-0097 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke |  | 1942001505 | John | Burch | 1.000000 | 1000 | Delta Whitewater DF 50 |  | Pump | Gravity | Trenches | Not Applicable | 100.000000 | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | None | Clear | 8.300000 | 5.000000 | 0.000000 |  | aeration unit sludge depth -approximately 6" | [10 empty] | Owner reported an alarm of the air compressor about a week and a half ago, It was found that the diaphragm had failed on the compressor. The owner purchased a replacement compressor and properly installed the unit; unit operating properly at time of the inspection. Aeration unit sludge/flocculant depth satisfactory at about 6" in depth. Adjusted pump tank alarm depth setting. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | Dec 30 1899 9:00PM
05/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. Replaced UV bulb while on site. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Dec 30 1899 12:05PM
10/11/2023 | Alternative | RoutineScheduled | 199-07-0105 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Best |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 12:00 AM
09/06/2023 | Alternative | Routine/Scheduled | 041-STS-259163 | Chesterfield | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | EZ Treat Sandfilter |  | Pump | Gravity | Discharge | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Processing tank - float sensors, recirc pump, RSV serviced. Treatment Module - media bags & spray grid serviced. U.V. system - double bulb - serviced Pump Tank - float sensors, pump and controls operating. Discharge point - rodent guard present - free flowing - signage present. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/07/2023 | Dec 30 1899 12:45PM
07/26/2023 | Alternative | Initial Visit | 166-13-141 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial visit - Alarm - owner reports that neighbor has reported the system alarming last 2+ weeks and has been silencing the alarm. Primary septic tank - normal level - effluent screen serviced. Aeration tank - normal level - compressor diaphragm failed - repaired on property and restored operation. Pump Tank - float sensors, pump and controls operating. DBox - intact - all laterals accepting effluent. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/27/2023 | 09:30 AM
10/18/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/19/2023 | 12:09 PM
12/27/2023 | Alternative | Reportable Incident | 073-STS-93875 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to some bubbling and gurgling and red light on for 4 days and now off. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 1.5 hours. Dug up and fixed the grade on the pipe from the septic tank to Clearstream tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/27/2023 | 12:30 PM
06/19/2023 | Alternative | Reportable Incident Component Maintenance | SP-05-393 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to a failed timer float. Replaced float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
02/27/2023 |  | RoutineScheduled | 033-08-0219-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1500 | 0-2 0-1 0-3 | 0-1 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 4.000000 | [11 empty] | Inspected | sealed all the tank risers | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | 11:00 AM
03/11/2023 |  | RoutineScheduled | 067-STS-38938 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. Cleaned septic tank solids filter. 2" of solids in recirculation portion of treatment unit. 0" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 07:03 PM
01/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/03/2023 | Alternative | RoutineScheduled Component Maintenance | 175-07-0552 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
12/15/2023 | Alternative | RoutineScheduled | 95-113-169 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 2 Chlorine 4 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/15/2023 | 12:00 AM
11/17/2023 | Alternative | RoutineScheduled | 165-STS-335618 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  |  | Trenches | Not Applicable |  | ["Septic Tank Baffles","Recirculation Pump"] | ["Septic Tank Baffles","Recirculation Pump"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/17/2023 | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled | 08-192-132 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 -Blue Crystal tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/05/2023 | 12:00 AM
07/13/2023 | Alternative | Reportable Incident Component Maintenance | 177-11-0039-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm in the drip tank. Observed a strong, acrid smell coming from the drip control panel. Circuit board attached to inner door was charred in lower, right corner and one corner of the X-harness was burnt. Replaced this circuit board and X-harness. The main motherboard did not exhibit any problems. Full power was not making it to zone 2. Replaced rotten butt connectors that the installer had used to splice an extension onto the main harness from the panel to the hydraulic unit. Initiated automatic drip cycles for each zone to verify repairs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
10/06/2023 | Alternative |  | 08-177-1004 | Pulaski | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | Premier Tech STB |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | [17 empty] | Raked peat, cleaned effluent screens, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/10/2023 | 12:00 AM
03/03/2023 |  | RoutineScheduled | 177-09-0322-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | There are roots growing into the Puraflo modules. At some point in the future, this may make it difficult to service the peat. There are small trees & shrubs growing near the header lines of the drainfield. These should be removed to prevent roots from blocking the header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/07/2023 | Alternative | RoutineScheduled | 104-11-0068 | Amherst | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Advantex |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 04:30 PM
10/17/2023 | Alternative | Routine/Scheduled | 06-118-0094 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 50.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Manifold brushed and flushed. Rsv cleaned. Pump vault removed and cleaned. Septic tank pumped out and refilled. Floats adjusted to proper levels. Dbox uncovered and inspected. Dbox had roots in it, we removed the roots and retimed the box. Field is overgrown and should be cleared and maintained as lawn. There is a leak around the rsv penetration and around the discharge force main, these should be sealed. The override float in the recirc chamber is bad and needs to be replaced. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/17/2023 | Dec 30 1899 11:11AM
05/08/2023 | Alternative | RoutineScheduled | 07-160-0282 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | BioMicrobics Microfast 0.5 |  | Gravity | Pressure | Drip | Not Applicable | 200.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | System is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/15/2023 | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
10/24/2023 | Alternative | RoutineScheduled | 09-100-0571 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 3.000000 | 4500 | Septic TankS | Biocoir AT5-6 | Gravity | Pressure | Pad | Not Applicable | 1500.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | 12:15 PM
12/14/2023 | Alternative | Routine/Scheduled | 073-STS-106144 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component At normal level The entire tank is full of sludge and solids, customer approved pumping. No filter or riser access Discharge/Pump Tank Condition of above Component Notes for above Component At normal level Riser, pump, floats and plumbing were replaced last year There is a layer of fog on the top of the water, customer approved to pump the tank out Control Panel Condition of above Component Notes for above Component Panel is new and working properly Discharge pump pulling 11.43amps Distribution Box Condition of above Component Notes for above Component Corner of lid barely broken and part of the box is starting to flake of but nothing major, showed the customer on site, he is not that worried about it. When we ran the pump the dbox over flowed after a few seconds because two lines aren't taking water. Customer approved to jet the drainfield Drain Field Condition of above Component Notes for above Component Showing no signs of surfacing Jetting will be done soon | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 09:56 AM
05/13/2023 | Alternative | RoutineScheduled | 133 19 0068 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. 0" of solids in recirculation portion of treatment unit. 6" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 07:03 PM
06/09/2023 | Alternative | RoutineScheduled | 07-142-0054 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
03/04/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20 RT |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 0" of solids in recirculation portion of treatment unit. 2" of solids in discharge portion of treatment unit. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 07:03 PM
01/09/2023 |  | Routine/Scheduled | 228-19-0062 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 9:30AM
06/14/2023 | Alternative | RoutineScheduled | 087-STS-6424 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
07/13/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Control panel struck by lightning & PC board was replaced. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | Dec 30 1899 1:44PM
06/09/2023 | Alternative | RoutineScheduled | C03-180-0178 | Roanoke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001094 | David | King | 1.000000 | 1500 | Aquasafe AS 900 |  | Gravity | Gravity | Discharge | UV |  | ["Disinfection"] | ["Disinfection"] | NA |  |  | 6.800000 | 5.520000 |  |  |  | 06/06/2023 |  |  |  |  | 37.600000 |  |  | Attached to this report |  | Cleaned UV light, system is working as designed. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/16/2023 | 12:00 AM
05/31/2023 | Alternative | RoutineScheduled | 109-06-0493 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Trouble Shooting . Intermittent high water in the recirc tank alerts sent to my email. However System fully checks out normal, sending alerts due to high level every few days. Appears to lose float signal. Ran fine in test mode and error corrected. Flashed memory updated program and Reinstalled, system in now trending and relearn. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 05:30 PM
04/11/2023 |  | Initial Visit | 175-13-0413 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST | [6 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Recommend boxwood remove from top of FAST | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | 12:00 AM
01/26/2023 |  | RoutineScheduled | 175-18-0452 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
02/22/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/19/2023 | 10:02 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed at this time. There are three emitter spots near the far side of the drainfield that appear highly nitrified but it might just be less cover as the line ends. Recommend homeowner monitor and notify if there are any changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/27/2023 | Alternative | RoutineScheduled | R11-180-0137 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 3000 | Orenco Advantex AX 20 |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic Tank - 3" crust, 5" of accumulated solids. Recirculation tank - 6" of accumulated solids. Discharge pump tank - 4" of solids. Flushed both treatment unit's spray manifolds. Cleaned recirculation pump basket filter. Tested floats, pumps and alarm. Cleaned drip manifold spin filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 7:03PM
11/28/2023 | Alternative | Pump-Out Only | 16-120-0289R | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alternative Septic System- Advantex AX20rt with 2 septic tanks. Pumped out and inspected primary septic tank. Pumped 1000 gallons of extremely heavy solids and medium sludge. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 1:54PM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | SD-09-10 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
11/30/2023 | Alternative | RoutineScheduled | 07-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
09/05/2023 | Alternative | Routine/Scheduled | 166-09-202 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 04:26 PM
10/24/2023 | Alternative | RoutineScheduled | 17-192-154 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 10 - Bio Max tablets installed 1 - Norweco Feeder Tube | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/24/2023 | 12:00 AM
09/01/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-873 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The push to silence button for the alarm is working intermittently. Replacement is recommended. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance | SD-02-812 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
04/28/2023 |  | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. UV disinfection - bulb and housing serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. Mound - no indications of surfacing - vacuum breakers intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 08:15 AM
08/01/2023 | Alternative | RoutineScheduled | 151-10-070 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air blower needs replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
12/12/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92872 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
09/21/2023 | Alternative | RoutineScheduled | 003-STS-33362 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 12:00 AM
06/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/29/2023 |  | Routine/Scheduled | 041-STS-259493 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/29/2023 | Jan 1 1900 8:43AM
08/22/2023 | Alternative | Follow-Up |  | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | Dec 30 1899 9:30AM
09/16/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Cleared roots that had gotten inside the treatment unit. 1" of solids in recirculation portion of treatment unit. 10" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 07:03 PM
09/26/2023 | Alternative | RoutineScheduled | 05-113-278 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 12:00 AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
09/16/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | Purpflo |  | Pump | Pressure | Drip |  | 75.000000 | ["None"] | ["None"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 12:00 AM
03/27/2023 |  | Routine/Scheduled |  | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Richmond | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Processing Tank and pump tank pumped empty for repairs. Confined space entry to re-parge seams. Replaced disccharge access riser and splcie box. Replumbed and re-sealed forcemain penetration at tank. Refilled processing tank for re-start. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Jan 1 1900 9:30AM
10/23/2023 | Alternative | RoutineScheduled | 2015-143-0025 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 1200 | EcoPod |  | Pump | Pressure | Drip |  | 460.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [16 empty] | Inspected | recommend pumping ASAP | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 03:45 PM
04/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | Microfast unit is clogging water level is high | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/20/2023 | Dec 30 1899 5:45PM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/31/2023 | Alternative | Routine/Scheduled | 151-06-0056 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | 12:15 PM
01/24/2023 | Alternative | Reportable Incident | 103-STS-92685 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Alarm reported. No alarm on arrival. System check - okay. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/02/2023 | Alternative | RoutineScheduled Component Maintenance | 177-18-0192-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Auxiliary Filter"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend replacing the psi gauge in the drip dispersal system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
06/07/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Panel was rewired and aerator was reaplaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/27/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0182 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Tree that was next to the distribution boxes in the past has been cut down. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
12/26/2023 | Alternative | RoutineScheduled | 107-05-0332 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 0.000000 | [] | [] | [18 empty] | No Power to System | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 04:55 PM
02/17/2023 |  |  | 18-142-0397 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1000 | 1000 |  | Pump | Pressure | Drip | UV |  | [] | ["Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation"] |  | None | Discolored | 6.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/17/2023 | Jan 1 1900 4:00PM
12/26/2023 | Alternative | Reportable Incident | SD-14-116 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
04/26/2023 |  | Routine/Scheduled | 234-16-79 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 10:00AM
07/20/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | N/A | [17 empty] | Cleaned effluent filter | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/20/2023 | Dec 30 1899 9:00AM
04/20/2023 | Alternative | RoutineScheduled | 115-16-0136 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 3500 | SEPTIC TANK | EZ TREAT | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | SYSTEM DID NOT NEED TO BE PUMPED. THE SEPTIC FILTER WAS CLEANED. THE EZ TREAT PODS WERE CLEANED. CONTROLS WERE OPERATING AS DESIGNED. THERE WERE NO VISIBLE LEAKS IN THE LEECH FIELD. LIDS WERE SECURED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 10:05 PM
01/16/2023 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | septic tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
07/14/2023 | Alternative | Routine/Scheduled | 136-08-0230 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. BioFilter - concrete - Peatmoss ponding - poor condition - raked / turned. Pump Tank - float sensors, pump and controls operating. LPP - no indicates of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 09:00 AM
12/11/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-92523 | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 12/11/2023 | [7 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. No equal distribution at d-box, adjusted dial flows also removed root from around inlet pipe. 3 top lines ponding and backing up into box, inspection done after rainy day plus a little snow. Will visit on dry week. HL-6, LL-10, OVERRIDE-99. "R" counts back to zero. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/02/2024 | 07:39 AM
10/18/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | NA | [16 empty] | Inspected | Septic zone 1" Scum layer & -8-10" Sludge in septic zone, recirculation zone 10 in. sludge, Pump Tank 8-12" fine sludge trace, Clear Effluent on top, system is operational, system is connected to monitoring. Hosed off media, Cleaned Bio-filter, pulled and cleaned - RSV, Brushed and Flushed spray Manifold. All Floats test operational, pumps and alarm- Good & Good spray in treatment box. recirc pump 682.5 hours 81162 cycles, discharge pump 143.8 hours and 802 cycles in history since 6-26-19 CPU upgrade | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 04:30 PM
10/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/23/2023 | Alternative | RoutineScheduled | 067-STS-38687 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | BioMicrobics MicroFast |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | Fourth Quarter 2023 inspection. 12" solids in septic tank. 10" solids in MicroFast septic tank. 16" in treatment unit. 2" solids in discharge pump tank. Aeration is adequate. No sign of smell that has been an issue. Cleaned blower air filter. There is no pump out required at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2024 | 07:03 PM
09/30/2023 | Alternative | Reportable Incident | 181-05-0408 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | Best1 | Pump | Pressure | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [16 empty] | Pumped Out | The Best1 treatment tank was pumped and cleaned. The 1000 Gallon pump tank was pumped and cleaned. The discharge pump was locked up and was pulled and replaced with a new pump. The tank was filled with water and the pressure was adjusted on the drip field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/17/2023 | 05:55 PM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408270 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Chlorination |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
02/24/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Replaced Blower motor and blower alarm panel. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/25/2023 | 09:30 AM
06/29/2023 | Alternative | Routine/Scheduled | 234-14-131 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | Replaced pump relay & diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | Dec 30 1899 2:43PM
05/12/2023 | Alternative | RoutineScheduled | 171-15-082 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Advantex | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","Dispersal System Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [17 empty] | 48" liquid depth 8" Of sludge, no scum on inlet side. 8" loose sludge in outlet side. Breakers in outside panel were off when got there. Had high water alarm. High water was pumped to level. Pumps, Visual alarms, floats all working when I left. Audio alarm not working right. Owner is going to replace. Field is grown up. Needs to be cleared. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/14/2023 | 07:00 PM
09/26/2023 | Alternative | RoutineScheduled | 09-142-0149 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/18/2023 |  | RoutineScheduled | 153-STS-20377 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 04/18/2023 |  | 18.000000 |  | 1600.000000 |  |  |  | Will be sent separately | Inspected | Found UV light unplugged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/07/2023 | Alternative | RoutineScheduled | 107-14-0240 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
10/24/2023 | Alternative | RoutineScheduled | 159-18-0060 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled | 047-STS-22055 | Culpeper | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity |  | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Disinfection" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Disinfection" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Sulphitic | Discolored |  | 28.000000 |  |  |  | 05/02/2023 | Sample Chamber | 28.000000 |  | 2419.600000 | 24.800000 |  |  | Will be sent separately | Inspected | As noted previously, we recommend replacing the EZ Treat filter media. We also recommend replacing the UV bulb that has burned out. And we also recommend pumping the septic tank and clarifying tank due to scum & sludge accumulation in the tanks. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/01/2023 | 06:29 AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
06/07/2023 | Alternative | Initial Visit Component Maintenance | 179-STS-92222 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Start-up with employees from Tolson Construction and M&M Soils present. Reset all "R" counts to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | SD-00-100 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
09/08/2023 | Alternative | RoutineScheduled | SD-06-l84 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-041,513 ETM-0,053,462 On-44s Off-2h/ Turned the Puraflo Peat in all 6 modules and is in good condition/ No breakout or spongy areas on the Pad area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/04/2023 |  | RoutineScheduled | 175-05-0113 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Peat is pretty compacted and granular, but not ponding. While it may still be providing some treatment after 17-1/2 years, it is recommended to be replaced by end of summer. About half of the spreader bars are pretty rusty and will need replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/10/2023 | 05:56 AM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-188 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots growing in media, recommend adding root destroyer. Broken tipping trade, recommend replacing it. customer asked for price for repairs to be done asap. will send price asap and follow up next week. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
08/07/2023 | Alternative | Pump-Out Only |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped septic tank as recommended during initial service visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 06:30 AM
11/03/2023 | Alternative | RoutineScheduled | 04-197-220 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/25/2023 | Alternative | Reportable Incident | 115-12-0008 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank Pumped | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | EcopodN |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Called due to wet spot in the yard the lawn mower reported. Found need to pump system to dig up and repair leaks | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/30/2023 | 09:30 AM
11/01/2023 | Alternative | Routine/Scheduled | S 800-17-0046 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 2:40PM
04/08/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/22/2023 | 12:00 AM
09/04/2023 | Alternative | RoutineScheduled | 107-14-0156 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
02/06/2023 | Alternative | Routine/Scheduled | 157-05-339 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Primary septic tank - effluent screen serviced. bioFilter - peatmoss is spent / compacted - requires replacing. Pump Basin - float sensors, pump and controls operating. DBox - Plastic - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 08:15 AM
09/07/2023 | Alternative | Reportable Incident Component Maintenance | 177-12-0299-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Low level alarm due to bad connection for off float, fixed connection and system went back to normal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
06/07/2023 | Alternative | Reportable Incident Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Blower alarm due to locked up blower. Installed new Gast blower and cleaned the air pre-filter. System has slight septic odor which should fade in about 24 hours. Inlet vent pipe is broken at the hub and system discharge has softened the soil and caused some light erosion around the piping. Owner is in the process of repairing/replacing the fitting. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
03/11/2023 |  | Routine/Scheduled | 041-STS-257943 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/11/2023 | Jan 1 1900 12:00PM
07/25/2023 | Alternative | RoutineScheduled | 127-STS-34169 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Anua Purasys |  | Pump | Gravity | Trenches |  |  | [] | ["Recirculation Pump","Level Sensor Operation","BlowerCompressorAerator Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled | 182-07-0173 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | ["Auxiliary Filter","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
05/23/2023 |  | RoutineScheduled |  | Cumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | ECO POD | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | Jan 1 1900 8:30AM
06/13/2023 | Alternative | Routine/Scheduled | 2007-143-0091 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 09:31 AM
07/14/2023 | Alternative | RoutineScheduled | 157-07-0142 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Repaired the broken air line at blower. OK | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
05/05/2023 | Alternative | RoutineScheduled | 154-02-0009 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/19/2023 | Alternative | Routine/Scheduled | 800-11-0117 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 10:30AM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance | VAG408087 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Gravity | Gravity | Trenches | Chlorination |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | air supply blocked and repaired | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
01/06/2023 |  | Routine/Scheduled | 800-05-0348 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 12:59PM
12/19/2023 | Alternative | Pump-Out Only | 05-160-0069 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 3.000000 | 3000 | Whitewater | [6 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
01/19/2023 |  | Follow-Up | 099-06-0307-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to dissasemble components in recirc tank and assist pumper with proper pump out. Reassembled components and refilled tank back to proper levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Control Operation" ,"Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [5 empty] | 06/12/2023 |  | 26.000000 |  | 79.000000 |  |  |  | Will be sent separately | Inspected | Control panel contactor needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/11/2023 | Dec 30 1899 11:24AM
07/06/2023 | Alternative | Routine/Scheduled |  | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Richmond | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - owner reports system alarmed 07/05/2023 - heavy usage. Processing Tank - RSV, Recirc pump and effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 7:00AM
04/19/2023 |  | Follow-Up | 179-STS-92102 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [7 empty] | 04/19/2023 |  | 24.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
08/10/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-09-0085-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Installed new Or3enco PF300511 pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
08/30/2023 | Alternative | Follow-Up Component Maintenance | 179-12-0201-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank was pumped by others in advance of peat replacement. Old peat was removed by vacuum truck and properly disposed. New peat installed in Puraflo modules. Concrete lid on septic tank was replaced previously. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
10/10/2023 | Alternative | RoutineScheduled | 182-17-0015 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Septic Tank Baffles","Recirculation Pump","Dispersal System Operation"] | ["Septic Tank Baffles","Recirculation Pump","Dispersal System Operation"] | [18 empty] | pump line screen cleaned (clogged). | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/10/2023 | 12:00 AM
04/28/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
12/18/2023 | Alternative | Follow-Up Component Maintenance | 179-14-0212-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed septic tank inlet pipe and top seam of tank on inlet end. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
11/28/2023 | Alternative | RoutineScheduled | 165-STS-337594 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | E-Z Treat |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles"] | ["Auxiliary Filter","Septic Tank Baffles"] | [8 empty] | 11/28/2023 | Pump Chamber | 5.000000 |  |  | 8.500000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/18/2023 |  | RoutineScheduled | 101-14-0281 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | AquaSafe |  | Gravity | Pressure | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/23/2023 | 12:00 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/23/2023 | Alternative | RoutineScheduled | SD-05-352 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens" ,"Level Sensor Operation"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Peat is showing it's age (8 years old) but still providing treatment judging by the effluent clarity in the pump chamber. Warned customer that it might need changing by next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
05/08/2023 |  | Reportable Incident | 153-STS-20370 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Service call repair only: Replaced Microfast Blower, tested and now functioning properly. May have odor for several days but will improve. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/30/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-23886 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Sealed pump tank inlet wedge lid to stop infiltration (that was observed at last inspection). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Blower was replaced since last year, and septic tank was pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | Dec 30 1899 4:51AM
05/17/2023 |  | Reportable Incident | 179-17-0123-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | System was in alarm due to field flush valve was dirty allowing water to loop back into the system. Zone 1 was not geting dosed due to lose wire. Both check valves in the field failed. Replaced both check valves. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | microfast needs pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/03/2023 |  | Routine/Scheduled | 550-STS-6411 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 8.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | Jan 1 1900 11:45AM
01/04/2023 |  | RoutineScheduled | 07-165-0409 | Northampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Bundick | Pump | 1.000000 | 1250 | Septic Tank | Pura-flo | Gravity | Pressure | Pad | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 12:00 AM
11/06/2023 | Alternative | RoutineScheduled Component Maintenance | 099-18-0078 SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection.45 psi. Treatment is crystal clear. RECIRC: HL-0, LL-12, OVERRIDE-72. DISCHARGE: HL-1,LL-14, OVERRIDE0. "R" counts back to zero. SYSTEM DOES NOT NEED PUMP OUT. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
10/20/2023 | Alternative | RoutineScheduled | SWP-05-241 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Dabney & Crooks, Inc. | 1942001489 | Robert | Fessler | 2.000000 | 2,000 | Pura Flo |  | Pump | Gravity | Pad | Not Applicable | 250.000000 | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/22/2023 | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [17 empty] | Septic Tank-8"sludge 4"scum/ Microfast ATU Tank-6"sludge 0"scum/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Found the redundant off float was faulty and was replaced during the inspection/ Controls, pumps, floats and alarms are now functioning properly/ Counts: Pump1-348 ETM-20h 3m/ Pump2-345 ETM-19h 51m On-3m 30s Standard off-12h/ Peak counts-11/ High level-4/ No breakout or spongy areas on the drainfield and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | One lateral appears to be more nitrified than others but is not showing signs of hydraulic saturation or surfacing effluent. Recommend balancing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/23/2023 | Alternative | Routine/Scheduled | 075-STS-31581 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/23/2023 | Dec 30 1899 2:20PM
04/11/2023 |  | Routine/Scheduled | 12-120-0322A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | N/A | [17 empty] | The treatment tank needs pumping | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/11/2023 | Jan 1 1900 3:22PM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-90519 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 2.98 amps. Treatment is crystal clear. HL-9, LL-9, OVERRIDE -5. "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
08/01/2023 | Alternative | RoutineScheduled | 001-STS-93774 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | PURAFLO |  | Pump | Gravity | Pad | Not Applicable |  | [] | [] | YES | [17 empty] | SLUDGE JUDGE 6" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 11:35 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/21/2023 |  | RoutineScheduled | 067-STS-39731 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Annual inspection visit. Septic tank has 8" of solids, pumping not needed at this time. Exercised all valves and repositioned. Tested pump and alarm. 3" of solids in discharge pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 07:03 PM
05/04/2023 |  | RoutineScheduled | 091-STS-337027 | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 3.000000 | 12000 | Septic Tank Only | Recirculating Sand Filter | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did not need to be pumped. The controls were operating as designed. The sand filter was operating as designed. The spin filter was cleaned. There were no visible leaks in the drip field. There was return effluent coming to the pump tank so the drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | 11:20 AM
12/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 10:05AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-0078-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
08/28/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed WE20G05P4-21 drip pump. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 12:58PM
07/17/2023 | Alternative | Routine/Scheduled | 103-STS-93361 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 06:03 PM
12/13/2023 | Alternative | Routine/Scheduled | 2017-143-0197 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level above normal due to clogged effluent screen. Flushed and cleaned effluent screen and septic tank returned to normal level. This resulted in putting the recirculation tank in high level. Septic tank due for pump out. Recirculation Tank Condition of above Component Notes for above Component Water level normal. Excess water from septic tank put recirculation tank in high level. Pumped down to normal level. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Not due for pump out Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Excess water from recirculation tank put discharge tank in high level. Pumped down to normal level. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panels are functioning properly. Checked and confirmed audible alarms are functioning properly. Checked and confirmed visual alarms are functioning properly. Distribution Box Condition of above Component Notes for above Component Water level normal. Structural integrity of distribution box appears to be intact Drain Field Condition of above Component Notes for above Component Surfacing occurred after I pumped excess water from discharge tank. Mrs. Hart stated that she had erosion issues in previous years and had lost a lot of top soil. I checked and found that there was 4" of topsoil at area of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 09:46 AM
05/16/2023 |  |  | 13-197-A1 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/16/2023 |  | 7.090000 | [5 empty] | Will be sent separately |  | BOD: 7.09 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed. On the far side of the mounds there is a small hole/depression. No effluent presented when cycling the system. It appears to be mole/vole burrow possibly? Advised homeowner to monitor and notify us if anything changes/. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/17/2023 |  | RoutineScheduled | 175-18-0102 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 4"scum/ Microfast-2"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-806 ETM-81h 18m On-5m 4s Off-11h 54m/ High-8/ Peak- N/A/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-19-0134 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
12/18/2023 | Alternative | Reportable Incident Component Maintenance | 179-13-0379-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Recirc pump not working, replaced with new step20 turbine pump. Recommend to install sim-tech filter next visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | SD-13-264 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
04/11/2023 |  | RoutineScheduled | 179-STS-90015 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
02/21/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/14/2023 | Alternative | Routine/Scheduled | 196-05-355 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 12.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump tank - float sensors, pump and controls operating. BioFilter - 4 modules - Peatmoss in good condition - raked /turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 10:45 AM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89324 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. She'd on drainfield, customer said he will move it this fall. Wipes in septic tank. Spoke to customer about Do's and don'ts. RECIRC: HL-3, LL-22, OVERRIDE-93. DISCHARGE: HL-3, OVERRIDE-1. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
09/13/2023 | Alternative | RoutineScheduled |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  |  | Trenches | Not Applicable |  | ["Septic Tank Baffles","Attached Growth Medium"] | ["Septic Tank Baffles","Attached Growth Medium"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
04/27/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Dispersal System Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Jan 1 1900 12:48PM
08/11/2023 | Alternative | RoutineScheduled | SD-09-306 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | Pura-flo | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Effluent Screens","Attached Growth Medium"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 12:00 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0128 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
10/26/2023 | Alternative | Routine/Scheduled | 137-17-022 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 100.000000 | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Manifold flushed. First spinner is spinning but the spray pattern is not correct. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | 10:13 AM
09/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | Dec 30 1899 2:00PM
06/21/2023 | Alternative | RoutineScheduled | 15-118-0015 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
08/02/2023 | Alternative | Routine/Scheduled | -STS-43276 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | Jan 1 1900 11:30AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend bringing risers slightly above grade | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/04/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1000 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping treatment unit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 05/25/2023 |  | 18.000000 |  | 1600.000000 |  |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 177-08-0240-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. Cleaned pump intake and disc filters. HL-18. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
01/31/2023 |  | Follow-Up | 179-18-0449-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed pump tank outlet riser at 12? extension. Sealed junction box penetration on pump tank riser. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
04/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/17/2023 | 12:44 PM
10/31/2023 | Alternative |  | SD-10-247 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | see attached analytics | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance | SD 86-159 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
05/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/15/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/18/2023 | Dec 30 1899 3:55PM
03/17/2023 |  | Reportable Incident | {FIPSCode}-STS-1345 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/17/2023 | Jan 1 1900 2:00PM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-23664 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
10/23/2023 | Alternative | Reportable Incident | 115-STS-96591 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Came out to a Purasys and found the system flooded. Plumber was out and found toilet leaking. It was leaking for at least 2 weeks. Drainfiled is heavily saturated. Need to give system time to dry up. So pumping the tank once a week for 4 weeks. And follow up to see how system is doing. Left the system off | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | 02:49 PM
09/27/2023 | Alternative | RoutineScheduled | 2015-143-0133 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 |  | Clearstream |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
08/10/2023 | Alternative | Follow-Up |  | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Effluent Screens","Level Sensor Operation"] | YES | [17 empty] | As per last service visit. Replaced damaged effluent screen with new. Replaced access riser on septic tank. Replaced float sensors in pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:45 PM
10/09/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 12:00 AM
12/19/2023 | Alternative |  | 12-197-A2 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/19/2023 |  | 9.380000 |  |  | 11.200000 |  |  | Will be sent separately |  | BOD: 9.38 TSS: 11.2 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
04/20/2023 |  | RoutineScheduled | 177-07-0424-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 4.0 amps. 1 air release valve cover missing lid. Not much grass on mound. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
07/19/2023 | Alternative |  |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/30/2023 |  | Routine/Scheduled | 234-15-465 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | Jan 1 1900 1:45PM
06/22/2023 | Alternative | RoutineScheduled | 181-05-0247 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Effluent Screens","SludgeScum Accumulation"] | ["Auxiliary Filter","Effluent Screens","SludgeScum Accumulation"] | [17 empty] | Pumped Out | All filters checked and cleaned. System was pumped and cleaned. No apparent leaks i system or drain field area. Control panels functioning properly. Lids were properly secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/14/2023 | 12:10 PM
01/10/2023 |  | Routine/Scheduled | 06-142-0456 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Peat checked and very near the end of it's useful life. Will need to be replaced soon. System appears to be operating normally. Septic tank will need pumpout soon. Ct 48502, etm 7280.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 12:22PM
08/28/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-8940 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Septic Tank Baffles","Dispersal System Operation","BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Septic Tank Baffles","Dispersal System Operation","BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | NA | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/28/2023 | 12:00 AM
02/17/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.350000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 03:00 PM
04/19/2023 |  | Pump-Out Only | NYII-BD4LT5 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [8 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | Jan 1 1900 10:37AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | 2102-05-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Disinfection" ,"Effluent Screens"] | ["Disinfection" ,"Effluent Screens"] | YES | Musty | Clear | 6.700000 | 1.500000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 10/16/2023 | 12:58 PM
02/27/2023 |  | Reportable Incident | 13-163-0038 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Alarm Event Compressor failed - electrical fail Installed new conduit and wiring for compressor Installed new compressor and restored aeration operation. Installed aeration control with time dosing. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/28/2023 | Jan 1 1900 7:15AM
07/03/2023 | Alternative |  | SP-04-386 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 8"scum/ Microfast ATU-20"sludge/ Pump Tank-2"sludge/ Septic-Microfast ATU requires pump out/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-802 ETM-35h 47m/ Pump2-785 ETM-35h 4m/ Peak-12/ High level-9/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/25/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable | 175.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | 01:00 PM
11/22/2023 | Alternative | Reportable Incident | 154-01-0236 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | James Lee Miller III | 1942001468 | Kevin | Blasing | [29 empty] | Conventional with pump. System in Alarm, all components are 20years old. System in great shape for age. Found floats were not working properly. Customer approved to replace all three floats. After replacing I confirmed everything is working properly. Customer paid with check. Alarm call for this visit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 08:59 AM
05/08/2023 |  | RoutineScheduled | SWP-04-557 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
05/05/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | Septic system is in working condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | Dec 30 1899 11:40AM
06/26/2023 | Alternative | Reportable Incident Component Maintenance | SD-04-460 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Customer called because pump was not running, we check system and found pump switch at jbox turned off and a broken wire for pump. Replaced switch because it was corroded and pump started working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
08/11/2023 | Alternative | Routine/Scheduled | 228-06-0898 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Drip | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | Dec 30 1899 9:00AM
11/07/2023 | Alternative | RoutineScheduled | SD-09-168 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | Micrfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/19/2023 | 09:10 AM
12/14/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  | Norweco Trench |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2024 | 12:00 AM
03/24/2023 |  | RoutineScheduled | 06-183-346 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/24/2023 | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | Dec 30 1899 11:24AM
07/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/05/2023 |  | Initial Visit |  | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Multiflo FTB |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit NOTE - No maintenance reported since system install - 2021 - need permit documents. Primary septic tank - Normal level Pump Basin? - float sensors, pump and controls operating. Aeration Tank - mixing present - aerator serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | Jan 1 1900 8:00AM
04/17/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
07/26/2023 | Alternative | Reportable Incident | 093-12-0109 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm (a week ago) and leaking out - forcemain broke under valve box - fixed (1 - 2" ball valve, 2 - 2" 90's, 3' of 2" pipe, and 1 - valve box). Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The septic tank needs additional risers on it to be properly inspected in the future. The timer is set to 1.25 minutes every 3 hours. Rained the previous night before service - could not check the drainfield or mound. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/26/2023 | Dec 30 1899 11:00AM
06/30/2023 | Alternative | RoutineScheduled | 151-11-0091 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service | 1942001034 | Kent | Cuthbertson | 4.000000 | 45000 | 15000 | 15000 |  |  |  |  | 15480.000000 | ["None"] | ["None"] | YES | [8 empty] | Sample Chamber | [6 empty] | Attached to this report |  | This is a wastewater treatment plant rated for 0.05 MGD which discharges into two drain fields. Effluent is sampled weekly per the VA Sewage Regulations, results of which are attached. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 12:25 PM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/19/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 09:55 AM
12/13/2023 | Alternative | Follow-Up | 147-17-0106 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company - pumped and cleaned the Clearstream tank and pumped out the septic tank. Disconnected the pressure switch on the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 1:30PM
07/13/2023 | Alternative | Routine/Scheduled | 234-14-219 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [12 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | Dec 30 1899 5:30PM
01/04/2023 |  | Routine/Scheduled | 228-14-0002 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | Jan 1 1900 2:52PM
04/10/2023 |  | Initial Visit |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - System Commissioning. Primary septic tank - normal level - effluent screen serviced. Processing Tank - Recirc - Recirc pump, media drapes serviced, effluent return and spray grid adjusted for flow. U.V. Disinfection - confirmed bulb operational. Processing Tank - Discharge - Float sensors adjusted IAW permit - pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | Jan 1 1900 7:15AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping Microfast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend adding ball valves. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/08/2023 | Alternative | Routine/Scheduled | 075-STS-32886 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 9:30AM
05/18/2023 |  | RoutineScheduled | 101-17-0617 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
08/07/2023 | Alternative | Reportable Incident | SHUN-B8XMDX | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned UV light bulb. Installed an aerator rebuild kit. Changed the filter in the aerator. The Clearstream tank needs to be pumped out. The timer is set to 3.5 minutes every 3 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/07/2023 | Dec 30 1899 9:00AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | EcoPod | EcoPod | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/14/2023 |  | Routine/Scheduled | 041-STS-257772 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Fuji |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Routine fuji maintenance performed. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Jan 1 1900 9:22AM
06/22/2023 | Alternative | RoutineScheduled | 08-100-0412 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1500 | BIOCOIR |  | Pump | Pressure | Pad | Not Applicable | 300.000000 | [] | [] | YES | [17 empty] | REPLACED FIBER. EVERYING WORKING AS IT SHOULD. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/20/2023 | 12:00 PM
02/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/03/2023 | Alternative | RoutineScheduled Component Maintenance | 177-11-0114-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic/ATU tank due to sludge accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
05/23/2023 |  |  | 085-STS-33441 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EZ Treat | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
05/22/2023 | Alternative | Reportable Incident | 157-10-0044 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Pumped out the septic tank, pumped and cleaned the Clearstream tank, and pumped and cleaned the pump tank. Disconnected the pressure switch on the aerator due to the pumping. The timer is set to 9 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/22/2023 | 10:00 AM
07/10/2023 | Alternative | RoutineScheduled | 175-02-0301 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Advantex Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [17 empty] | Septic Tank-4"sludge 0"scum/ Advantex-4"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Recirc. Bio Filter clogged- Cleaned and also cleaned the recirc. pump intake/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump-006936 ETM-026005/ No breakout or spongy areas on the drainfield and dosing correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as preventative maintenance. Observed whine and slight bearing noise coming from the blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 |  | Follow-Up | 179-16-0020-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pumpout of all tanks. Reassembled components and tanks were refilled with a water truck. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/05/2023 | 07:56 AM
10/06/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-89962 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
09/29/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/29/2023 | 12:00 AM
04/21/2023 | Alternative | RoutineScheduled | SD-15-187 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/23/2023 | 12:00 AM
11/15/2023 | Alternative | Routine/Scheduled | 166-09-070 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Less than 1" of solids with 4" of sludge Pulled and cleaned filter -Discharge/Pump Tank: Pump and floats functioning properly Has indoor alarm box -Peat Moss: Tipping bucket working properly Peat has been compacted and ponding water the past few years Needs replacement -Distribution Box: Dbox in good shape and at normal level Located about 6ft off the ramp of the shed -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 01:31 PM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/24/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/20/2023 | Alternative | Routine/Scheduled | 228-02-0654 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | Dec 30 1899 10:50AM
02/09/2023 |  | RoutineScheduled | 177-16-0226-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
07/07/2023 | Alternative |  | 033-16-0091-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
05/24/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 12:00 AM
02/11/2023 |  | RoutineScheduled | 2011-08-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | UV | 500.000000 | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.900000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/14/2023 | 12:00 AM
04/03/2023 |  | Routine/Scheduled | 03-120-0738A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/03/2023 | Jan 1 1900 12:32PM
08/22/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | Dec 30 1899 7:00AM
06/30/2023 | Alternative | Reportable Incident | 073-STS-105278 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced failed distribution box with new 8 port concrete DBox. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 09:00 AM
09/20/2023 | Alternative | RoutineScheduled | 115-12-0078 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic Tank | Advantex | Pump | Gravity | Trenches | Not Applicable | 350.000000 | [] | ["Control Operation","Attached Growth Medium","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation","Effluent Screens"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | 01:30 PM
01/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation"] | ["Disinfection","BlowerCompressorAerator Operation"] | NA | [7 empty] | 01/26/2023 | Sample Chamber | 31.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Microfast-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ Cleaned UV-Light Sleeve and light working/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-106 ETM-14h 27m Water Meter-0013300/ No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/01/2023 | Alternative | Routine/Scheduled | 093-STS-15047 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | Dec 30 1899 12:40PM
12/28/2023 | Alternative | Reportable Incident | 093-STS-14489 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV light and replaced the UV ballast. There needs to be additional risers on the septic tank in order to properly inspected in the future. The timer is set to 2 minutes every 3 hours. It was raining at the time of the service could not check the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/28/2023 | Dec 30 1899 11:00AM
07/01/2023 | Alternative | RoutineScheduled | 133 17 0309 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 4150 | BioMIcrobics MicroFast |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | 2nd Qtr. 2023 inspection. Grease trap accumulation - Chamber #1 - 12" crust, 12" bottom. Chamber #2 - 6" crust, 12" bottom. Chamber #3 - 18" crust, 24" bottom. Chamber #4 - 12" crust, 12" bottom. Solids in septic tank - First chamber - 0" crust, 12" bottom, Second chamber - 0" crust, 22" bottom. MicroFast clarifier- 0" crust, 48" solids. Cleaned blower filter. 12" solids in discharge pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/04/2023 | 07:03 PM
03/11/2023 |  | Routine/Scheduled | 087-STS-6652 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Gravity | Gravity |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/11/2023 | 11:30 AM
07/31/2023 | Alternative | Follow-Up |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1500 | Micro-fast |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Effluent Screens","Level Sensor Operation"] | ["Effluent Screens","Level Sensor Operation","BlowerCompressorAerator Operation","Distribution Pump Operation"] | YES | Musty | Clear | [15 empty] | The entire system is in compliance with the health department regulations and approved plans | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 10:00 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0446-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Disinfection" ,"Effluent Screens" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Disinfection" ,"Effluent Screens" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Blower stopped working, replaced chamber block in blower and started working. Replaced uv bulb. Checked tanks with mirror and didn't see any leaks. Blower 1.51 amps. HL-3, LL-3, OVERRIDE-4. high level alarm delay was set up to 15 minutes we changed it to zero to make sure it alarms right away if there is any problems. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
08/04/2023 | Alternative | RoutineScheduled | 2007-126-049 | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2000 | 1000 | 1000 | Pump | Gravity | Mound | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Sulphitic | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/04/2023 | 12:00 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/10/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Septic Tank | EZ-Treat Recirc. Pump Tank | Pump | Gravity | Discharge | UV |  | ["None"] | ["None"] | NO |  |  | 6.700000 |  |  |  |  | 01/10/2023 | Sample Chamber | 21.000000 |  | 14.000000 | 7.000000 |  |  | Attached to this report |  | Septic Tank-2"sludge 0"scum/ EZ-Treat Recirc. Tank-0"sludge 0"scum/ Discharge pump tank-0"sludge 0"scum/ No pump out needed at this time/ Controls,pumps, floats and alarms functioning properly/ Counts: Pump1-9501 ETM-98h 34m/ Pump2-9495 ETM-98h 42m/ Peak-191/ High-118/ UV-Light functioning properly/ Discharge point is clear. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
12/09/2023 | Alternative | RoutineScheduled | 2111-06-153m | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 6.800000 |  |  | 1.900000 |  | 12/19/2023 | [10 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/06/2024 | 12:00 AM
10/17/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1000 | anua (puraflo) |  | Pump | Gravity | Trenches | Not Applicable | 100.000000 | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | The existing Peat moss was fluffed and raked and added to prevent freezing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 12:00 PM
05/10/2023 |  |  | 033-18-0004-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/24/2023 |  | Routine/Scheduled | 234-14-149 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 12:40PM
06/07/2023 |  |  | 033-17-0196-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
08/30/2023 | Alternative | RoutineScheduled | 214-16-0014E | Lynchburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank | Norweco Singulair ATU (x 2 units) | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic Tank 1-2" scum 8-10" sludge, septic was pumped 2 years ago. Septic filter had a slight back up Norweco#1 6" sludge, cleaned off both kinetic filter. Norweco #2 4" sludge, both aerators are operational, alarms are operational. both system have clear effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 09:30 PM
04/18/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 540 | Multiflo FTB |  | Pump | Pressure | Trenches |  | 600.000000 | None | None | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/21/2023 | 12:54 PM
09/22/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | Dispersal System Operation | Dispersal System Operation | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/18/2023 | 02:07 PM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/06/2023 | Alternative | RoutineScheduled | 195-Discharge-30134 Aistrop Road | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/06/2023 | 12:00 AM
08/01/2023 | Alternative | Initial Visit | 550-STS-6730 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 2.000000 |  | 1.000000 | [5 empty] | Owner called due to the orange light being on and smell. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream (has paint residue) and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The grade on the pipe in the Clearstream is not okay - serviced tech pushed down as far as he could - needs to be addressed and/or fixed. The timer is set to 5 minutes every 2 hours. Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | Dec 30 1899 1:30PM
05/08/2023 | Alternative | RoutineScheduled | 14-177-1086 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | R & R Enterprises, Inc | 1942001111 | William | Robinson | 1.000000 | 1000 | MICROFAST AST |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 12:00 PM
07/26/2023 | Alternative | RoutineScheduled | 10-160-0196 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1500 | Microfast | [6 empty] | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled | 15-142-0198 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
03/30/2023 | Alternative | RoutineScheduled | 179-10-0314-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 5.000000 | [11 empty] | Inspected | entered under Madison County by mistake/reentering | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 01:00 PM
12/15/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Ecoflo |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles"] | ["Septic Tank Baffles","Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 12:00 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/24/2023 |  | Routine/Scheduled | 550-STS-6588 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/24/2023 |  | 32.000000 |  | 4.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 8:30AM
04/04/2023 |  | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["SludgeScum Accumulation","Septic Tank Baffles"] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | Jan 1 1900 6:30PM
10/18/2023 | Alternative | Reportable Incident | 087-STS-6191 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | [] | [18 empty] | Installed new microfast blower | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/20/2023 |  | RoutineScheduled | 02-113-418 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Trenches | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
07/15/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 | 1k | 1k | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | Cloudy | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/08/2023 | 12:00 AM
03/01/2023 |  | RoutineScheduled | 179-19-0158-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Disinfection" ,"Effluent Screens" ,"Auxiliary Filter" ,"Control Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Control Operation"] | YES | [15 empty] | Will be sent separately | Inspected | System is currently on pump & haul. We recommend replacing two broken air release valve housing lids. We also recommend reattaching the control panel to the house before it falls off and is damaged. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
03/17/2023 |  | Routine/Scheduled | 07-120-0402AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. PUmp Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | Jan 1 1900 9:00AM
12/13/2023 | Alternative | Routine/Scheduled | 133-STS-95138 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal level 4 in of sludge less than 1 in of solids Pulled and cleaned filter No signs of infiltration Recirculation Tank Condition of above Component Notes for above Component Normal level Less than 1 in of suspended solids Tested floats and pump all working as should Pulled and cleaned pump All plumbing intact and pump moving water properly No signs of infiltration Discharge/Pump Tank Condition of above Component Notes for above Component Normal level Less than 1 in of suspended solids Tested floats and pump all working as should Pulled and cleaned pump Pulled and cleaned disc filter All plumbing intact and pump moving water properly No signs of infiltration Media Sheets Ez treat media bags Condition of above Component Notes for above Component All media bags intact, sprayed clean and functional Laterals intact and dispersing water properly Cleaned spray tips Control Panel 1 Recirc panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Recirc pump pulled 9.07 amps All components working as should Control Panel 2 Discharge panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Discharge pump pulled 11.22 amps All components working as should Control Panel 3 Uv panel Condition of above Component Notes for above Component 120 volts coming in All components in panel are functional however uv bulb itself is brunt out and not functioning Drip Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 09:39 AM
05/19/2023 |  | Routine/Scheduled | 228-17-0162 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | Jan 1 1900 11:48AM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20468 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 06:25 AM
07/05/2023 | Alternative | Routine/Scheduled | 550-STS-6601 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | Dec 30 1899 1:36PM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0016 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
02/24/2023 |  | Initial Visit | 182-03-0194 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/24/2023 | 12:00 AM
02/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0477 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Air relief valve broken. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
10/25/2023 | Alternative | RoutineScheduled | SWP-00-353 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-3 | 0-0 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 6.000000 | [11 empty] | Inspected | peat moss degraded ready for replacement | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/25/2023 | 01:00 PM
09/12/2023 | Alternative | Routine/Scheduled | 073-STS-106139 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | - Pumped 1000 gallons from septic tank and inspected. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 12:34 PM
08/14/2023 | Alternative | RoutineScheduled | 154-11-0045 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 3000 | Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["Auxiliary Filter","Recirculation Pump"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge Scum Accumulation - Septic 10", ATU 4", Pump Station 6" Effluent Filter Cleaned Recirculation Pump Pulled - Screen Removed and Cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 11:00 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Fairfax | Ace Contracting Services, Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 | 2000 | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Replaced Cracked Septic Tank Lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | Dec 30 1899 3:09AM
09/12/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 4.000000 |  | 15.000000 | [5 empty] | Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | Dec 30 1899 11:20AM
08/04/2023 | Alternative | RoutineScheduled | 181-09-0042 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin filters were both cleaned. The treatment unit was in operating condition. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 12:35 PM
10/11/2023 | Alternative | RoutineScheduled | 165-STS-338755 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | [8 empty] | 10/11/2023 | Pump Chamber | 3.000000 |  |  | 11.400000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 12:00 AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There are four small trees planted near the end of the lines. Advised homeowner of potential issues and recommended moving them. Lower corner of the field on the house side appears to be evenly nitrified. Recommend homeowner monitor for changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/24/2023 | Alternative | RoutineScheduled | SD-12-31 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Auxiliary Filter"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Half of the EZ treat brass nozzles were plugged. Resumed good spray pattern after cleaning. Since broken force main was repaired last year, flow meter is advancing. Owners averaged about 90 gals per day since last November. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
07/13/2023 | Alternative | Pump-Out Only | PPIE-AJFN8F | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Dispersal System Operation","Distribution Pump Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | As recommended during last service visit - trash tank and aeration tank pumped empty and serviced. Aeration tank refilled with fresh water for restart. Drip field still pending onsite service visit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | Dec 30 1899 7:45AM
06/16/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as preventative maintenance. Pump "Standby" light (yellow) was burnt out, replaced assembly. Observed whine and slight bearing noise from the blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
11/20/2023 | Alternative | RoutineScheduled | 145-STS-261491 | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Septic Pro of Virginia | 1942001780 | Eric | Tambourine | 1.000000 | 1069 | FujiClean CEN7 | Norweco 1500AT UV | Pump | Pressure | Pad | UV | 360.000000 | ["None"] | [] | NA | Musty | Clear | [5 empty] | 11/20/2023 | Pump Chamber | 9.900000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 12:00 AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/18/2023 | Alternative | Follow-Up | 107-06-0298 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Distribution Pump Operation","SludgeScum Accumulation"] | ["Effluent Screens","Distribution Pump Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
09/19/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced riser that was damaged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
03/15/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump" ,"Disinfection"] | ["Recirculation Pump" ,"Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
09/21/2023 | Alternative | RoutineScheduled | 027-STS-15545 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/21/2023 | 12:00 AM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
08/05/2023 | Alternative | RoutineScheduled | 2099-05-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.400000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled | 154-15-0086 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
05/18/2023 |  |  | 2005-143-0129 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 AM
07/24/2023 | Alternative | RoutineScheduled | 175-03-0876 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Advantex Recirculation Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","Attached Growth Medium","SludgeScum Accumulation"] | [] | NO | [17 empty] | Septic/ Recirc. Tank-16"sludge 0"scum/ Drainfield Pump Tank-2"sludge/ Reciriculation Tank Requires Pump Out/ Wiring Issues with the Recirculation Tank: When the bottom float is closed and the 2nd and 3rd float is open or down the processer shows all floats are closed. Recommend a electrician to locate the problem/ System will recirculate with the bottom float closed (turned up) Counts: Recirc-999999 ETM-418,968m/ Recirc override-306,004/ Discharge-11129 ETM-47,155m/ Discharge override-277/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/24/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump relay | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/24/2023 | Dec 30 1899 8:00AM
10/31/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-92913 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/12/2023 | Alternative | RoutineScheduled | 2017-143-0052 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
01/17/2023 |  | RoutineScheduled | 08-192-262 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 5 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/17/2023 | 12:00 AM
10/10/2023 | Alternative | Routine/Scheduled | 05-120-0314A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Effluent screen is obsolete and discontinued. Riser is not properly sealed to septic tank. Due for pump out -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Discharge riser is cracked. -Peat Moss: Structural integrity of tank appears to be intact. Raked and tilled peat moss. Peat moss is bad. Tipping bucket is cracked. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drip Field: Flushed and cleaned disk filters. Found no signs of surfacing on dispersal field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 2:54PM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0028-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Clearstream | none | Pump | Gravity | Pad | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend mowing the drain field area and maintaining it in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
04/04/2023 |  | Reportable Incident |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [16 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 Primary septic tank pumped for real estate inspection. Replaced distribution box with new 8 port concrete DBox Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | 09:00 AM
04/26/2023 | Alternative | RoutineScheduled | 17-100-0128 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | AQUASAFE |  | Pump | Pressure | Trenches | UV |  | [] | [] | [17 empty] | Pumped Out | PUMPED SLUDGE FROM FIRST TANK. EVERYTHING WORKING AS IT SHOULD. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/27/2023 | 03:00 PM
08/08/2023 | Alternative | RoutineScheduled | 02-197-077 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/08/2023 | 12:00 AM
03/29/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air line was repaired. System should resume functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | VAG401195 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
10/10/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
03/13/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Floats replaced. System should begin to function correctly shortly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/18/2023 | Alternative | RoutineScheduled | 147-15-0013 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 | 1000 | Multi Flo |  | Pump | Gravity | Pad |  |  | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/09/2023 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced return solenoid & valve. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
02/20/2023 |  | RoutineScheduled | 065-STS-30074 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
03/28/2023 |  | RoutineScheduled | 177-STS-86685 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Risers are leaking because they are not compatible with the tanks. We recommend replacing the Polylok risers with EZ set risers on the ATU tank & Pump Tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
09/20/2023 | Alternative | RoutineScheduled | 001-STS-92134 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJI CLEAN CEN 5 |  | Pump | Pressure | Mound | UV | 450.000000 | [] | [] | [18 empty] | SLUDGE JUDGE 6-7" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 12:45 PM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
11/27/2023 | Alternative | RoutineScheduled | VAG408244 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/27/2023 | 12:00 AM
12/18/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 9:10AM
05/17/2023 | Alternative | Follow-Up | C 800-17-0369 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Hooked up the pressure switch on the aerator and the breaker for the UV. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/17/2023 | Dec 30 1899 12:00PM
01/25/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2250 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | 04:00 PM
01/03/2023 |  | Pump-Out Only | 234-15-277 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [28 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | Jan 1 1900 9:00AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | SD-00-111 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | None | [14 empty] | Will be sent separately | Inspected | Annual inspection. Both zones drip rates seem a little high, but no effluent surfacing and no spongy spots. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
01/12/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Microfast | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Run Time 1323h, 49m. Doses 6870. Client just had the septic pumped, 0 scum 2" of sludge. nothing in the pump tank. Cleaned spin filter, walked drip field. System working very well | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2023 | 12:15 PM
07/10/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Septic Tank Baffles","Attached Growth Medium"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | 12:00 AM
06/15/2023 | Alternative | Routine/Scheduled | 05-160-0370 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/15/2023 | 11:30 AM
05/17/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [7 empty] | 04/17/2023 |  | 300.000000 | [5 empty] | Will be sent separately | Inspected | Replaced blower, repaired floats, Replaced valve box, Upgraded Timer System was pumped | This AOSS should now return to normal function after having provided the above state routine maintenance | 05/22/2023 | 11:15 AM
02/24/2023 |  | RoutineScheduled | 06-137-0039 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:00 AM
03/29/2023 | Alternative | Routine/Scheduled | 103-STS-100599 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 300.000000 | ["Attached Growth Medium","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | AOSS - Initial Visit - 2nd Opinion for Home owner. System already serviced by "others" and biofilter changeout required. System approximately 20 years old - no routine service reported. Primary septic tank - effluent screen serviced Pump Tank - float sensors, pump and controls operating. BioFilter - 3 modules - peatmoss compacted and ponding - requires replacement - but is functioning | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 07:15 AM
05/18/2023 |  | RoutineScheduled | 003-STS-29638 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
04/07/2023 |  | Pump-Out Only |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 600.000000 | ["Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | As recommended during previous service event. Pumped and serviced primary septic tank. Pumped and serviced secondary septic tank. Pumped and serviced pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | Jan 1 1900 8:30AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/13/2023 | Alternative | Follow-Up | 98-197-A5 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 | ATU | [10 empty] | None | Clear |  |  |  | 0.000000 | [11 empty] | Tablets now added | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 10/16/2023 | 12:00 AM
03/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air blower is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
01/05/2023 | Alternative |  | 099-18-0138 SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/05/2023 | Alternative | Routine/Scheduled | 05-160-0194 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex | Orenco Advantex | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 12:30 PM
03/15/2023 |  | RoutineScheduled | 03-197-235 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 12:00 AM
12/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/25/2023 |  | RoutineScheduled | 165-STS-337937 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 04/25/2023 |  | 13.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal Please keep drainfield mowed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/21/2023 | 03:35 PM
01/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-4"sludge 0"scum/ Microfast ATU .75-20"sludge 0"scum ( REQUIRES PUMP OUT ) Pump Tank-2"sludge 0"scum/ Blower air filter cleaned and blower working properly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-2604 ETM-54h 39m/ Pump2-2319 ETM-52h 50m/ Peak-85/ High-32/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/05/2023 |  | RoutineScheduled | 124-STS-2379 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 1 discharge sign installed. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/05/2023 | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator not functioning | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
03/09/2023 |  | RoutineScheduled | 179-06-0046-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
09/22/2023 | Alternative | RoutineScheduled | 04-125-107 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 10 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/22/2023 | 12:00 AM
08/17/2023 | Alternative | RoutineScheduled | 07-113-265 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/17/2023 | 12:00 AM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 3.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air release valve on Zone 2 had come off. It was replaced and appears to be functioning as designed now. Valve box and air release valve will be replaced and area will be limed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/27/2023 |  | RoutineScheduled | 179-12-0226-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Strongly recommend installing access to septic tank to be able to inspect every year. Cleaned air filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
10/10/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 500 | 1000 |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Other"] | NA | [16 empty] | Pumped Out | Septic/microfast unit pumped out Also dug up in drain field thought there was a break found none. Soil is very oversaturated. It doesn't appear to be absorbing the effluent | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/16/2023 | Dec 30 1899 9:00AM
07/27/2023 | Alternative | RoutineScheduled | 001-STS-92128 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 749 | FUJI CLEAN CEN 5 |  | Pump | Gravity | Mound | UV | 450.000000 | [] | [] | YES | [17 empty] | EVERYTHING WORKING AS IT SHOULD. SLUDGE JUDGE 6" FROM TOP BOTTOM AND 4" FROM TOP | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 11:25 AM
02/23/2023 | Alternative | RoutineScheduled | 17-177-1092 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | Septic | [16 empty] | - everything functioning as designed - if sample has not been taken in last five years, sample is due - ex riser lid cracked and needs to be replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/24/2023 | 12:00 AM
02/20/2023 |  | RoutineScheduled | 132-06-0137 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled | 14-100-0401 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Pressure | Mound | UV | 450.000000 | [] | [] | YES | [16 empty] | Pumped Out | SLUDGE JUDGED SEPTIC TANK, 12-14" FROM BOTTOM 3-4" FROM TOP. PUMPED SEPTIC REPLACED UV LIGHT UNIT EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | 12:10 PM
08/19/2023 | Alternative | RoutineScheduled | 2051-98-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 6.800000 |  |  | 2.200000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | 12:00 AM
05/22/2023 | Alternative | Follow-Up Component Maintenance | SP-05-120 | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for second opinion for root issues in puroflo pods and pad site. Proposal to be sent to correct pods and fix infiltration on both tanks. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:08 AM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0025-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Blower 2.96 amps. Septic tank most likely will need pump out next year. Monster box is almost full of lodge recommend to vacuum It out or pump it out at time of pumping septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/13/2023 |  | RoutineScheduled | 179-06-0218-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Clogged up filter with wipes and other trash cleaned. Recommend pumping both tanks and to stop flushing trash. Media showing its age we will evaluate next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
08/24/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - 4 module - peatmoss spent - root clogged | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/28/2023 | 02:00 PM
11/18/2023 | Alternative | RoutineScheduled | 019-STS-27060 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | Orenco Advantex (2) AX100 |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank - First section - 4" solids crust, 6" in the bottom, second section - 0" crust, 16" on bottom. Recirculation tank - 6" of accumulated solids. Discharge pump tank - 12" accumulated solids. Flushed both treatment unit's spray manifolds. Cleaned recirculation pump solids basket filter. Cleaned drip manifold spin filter. Sprayed solids off of the treatment unit's "sheets". Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 07:03 PM
07/13/2023 | Alternative | RoutineScheduled | 175-12-0350 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic / Ecopod ATU Treatment Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | NA | [17 empty] | Septic Tank-8"sludge 2"scum/ Ecopod-6"sludge/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-11131/ Run Time-1004/ Hand-39/ High-23/ Watermeter-692,640.8/ Repaired broken drip tubing in zone #2/ No breakout or spongy areas on the drip field and now dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | Dec 30 1899 1:00PM
01/19/2023 |  | RoutineScheduled | 147-05-0198 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Onsite Maintenance Team | 1942001039 | Corey | Braxton |  |  | Advantex |  | Pump |  |  |  |  | [] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Level Sensor Operation","Auxiliary Filter","Distribution Pump Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | 107-08-0288 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
01/16/2023 |  | Routine/Scheduled | 087-STS-6527 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/16/2023 | 11:29 AM
07/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["Attached Growth Medium"] | ["None"] | YES | [16 empty] | Pumped Out | System needs peat moss in 5 pods- | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/09/2023 | Dec 30 1899 10:20AM
09/19/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  | 600.000000 | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | 02:30 PM
02/15/2023 |  | Initial Visit | 182-19-0061 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  | Gravity | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles","Recirculation Pump","Distribution Pump Operation"] | ["Distribution Pump Operation","Recirculation Pump","Septic Tank Baffles","Attached Growth Medium","Auxiliary Filter"] | [18 empty] | Baffle filter clogged/backing up. Washed down treatment unit. Cleaned intake screen on both pumps....recirc was clogged. Candy wrappers in tank | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/15/2023 | 12:00 AM
04/03/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
10/03/2023 | Alternative |  | {FIPSCode}-STS-19119 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 5.500000 | 8.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/01/2023 | Alternative | RoutineScheduled | SD-05-457 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annnual inspection. Replaced clean-out adapter and cap close to septic tank that were destroyed by an angry lawnmower. Groundwater infiltration observed at the bottom riser joints in the septic tank and pump tank. Will send a repair proposal to the owner to reseal those joints. Treated effluent is clear, but not crystal clear. Possibly lingering side affect from use of laundry sanitizers. Owner discontinued use about 6 months ago. Will continue to monitor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/05/2023 | 07:56 AM
06/22/2023 | Alternative | Reportable Incident | 800-STS-13766 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream, cleaned the filter in the aerator, and cleaned the filter in the septic tank. The filter in the septic tank was full of dog hair. Changed the mesh screen in the spinfilter. The UV is not working (probably the ballast and bulb). The pump tank and Clearstream tank need to be pumped out and cleaned. The timer is set to 8 minutes every 2 hours. It was raining at the time of service and could not check the drainfield or mound. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/22/2023 | Dec 30 1899 10:30AM
10/04/2023 | Alternative | RoutineScheduled | 2016-143-0011 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
10/13/2023 | Alternative | Routine/Scheduled | 10-160-0176 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 10:00 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-08-0455 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0008-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"SludgeScum Accumulation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend the following: Pump septic tank to remove paint that has been flushed into the system Install a new metal alarm horn on sand filter pump control panel Install a new override float in pump tank Install riser on inlet side of septic tank Install new headwords box heater Install new Orenco riser lid on drip pump tank Excavate by hand to uncover and reseal drip pump tank riser at its base. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/22/2023 | 11:48 AM
01/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
12/21/2023 | Alternative |  |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Disinfection","Control Operation","Attached Growth Medium","Auxiliary Filter"] | YES | None | Discolored | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 9:00AM
03/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Dec 30 1899 12:26PM
08/24/2023 | Alternative | Follow-Up Component Maintenance | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Dripfield grass all cut to good level for inspecting. Tested zones, found 2 air release valves (ARV) stuck open with mud and grass clippings which allowed effluent to spray out during the test cycle. The caps to the valves were gone, which made them prone to clogging. Removed and cleaned the ARV's. No longer leaking (and drip rates back to normal), but new 2" Geoflow valves will need to be ordered. A third valve had its cap, but the locking tabs were broken. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
12/04/2023 | Alternative |  | 151-18-0016 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1500 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/03/2023 |  | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Advanced Septic |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - AquaSafe ATU Primary septic tank - normal level - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 07:30 AM
01/16/2023 |  | Initial Visit | 136-14-0229 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - requires lab sampling Trash Tank - normal level - recommend pumpout. Aeration Tank - mixing present - compressor serviced - recommend pumpout and refill. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | 07:45 AM
08/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Gravity | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/06/2023 | Dec 30 1899 4:30PM
03/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Rappahannock-Rapidan | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-3 0-5 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 5.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 01:00 PM
12/01/2023 | Alternative | Reportable Incident Component Maintenance | SD-97-164 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm yesterday morning, barely out of alarm this afternoon. Zone return valve was not closing fully which allowed some effluent to recirculate back to the septic tank. Cleaned valve and retested. Also observed a small but steady trickle of water coming into the septic tank, typical flow from an out of adjustment toilet. Advised owner to check all toilets carefully and reduce water use for 12 more hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
02/02/2023 |  | RoutineScheduled | 179-16-0057-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Customer hit riser on monster box deforming it and breaking the seal. Recommend taking riser and gasket next visit to repair. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
12/20/2023 | Alternative | RoutineScheduled | VAG401110 (LEGACY DISCHARGE) | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Gravity | Discharge | Chlorination |  | [] | [] | [18 empty] | No discharge. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/03/2024 | 12:00 AM
04/03/2023 |  | Reportable Incident | 234-17-211 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Received a call about water by the tanks. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the disc filter. Changed the diffuser in the Clearstream and changed the filter in the aerator. The UV is not working - was flooded - disconnected alarm - need to go back to check it out and fix. Meet with the pumping company and pumped out the pump tank and pumped the sludge out of the Clearstream tank. The timer is set to 8 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/03/2023 | Jan 1 1900 3:00PM
02/22/2023 |  |  | 124-STS-2379 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 8.000000 |  | 1250 |  | Siphon | Pressure | Pad | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation","Control Operation"] | YES | Musty | Discolored | 6.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | Jan 1 1900 4:00PM
05/26/2023 |  | RoutineScheduled |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-1 | 0-1 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Level Sensor Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | YES | None | Clear | [14 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/26/2023 | 11:00 AM
06/12/2023 | Alternative | RoutineScheduled | 139-05-0140 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Microfast .5l |  | Pump | Pressure | Drip | Not Applicable |  | ["Other"] | ["Effluent Screens"] | YES | Musty | Clear | [14 empty] | Inspected | Sludge Scum - Septic 12", ATU 4", Pump Chamber 2" Reddish Brown Tint in Pump Station - Riser lid leaking, recommend additional riser and lid Solenoid for Auto flush inop - Drip field flush manually for 20mins | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
02/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/22/2023 | Alternative | RoutineScheduled | SD-05-46 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | Pura Flo | Pump | Gravity | Trenches | Not Applicable | 64.000000 | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 08:30 AM
03/31/2023 |  | RoutineScheduled | 113-18-074 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [8 empty] | 1771.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [5 empty] | 06/01/2023 | Pump Chamber | 10.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
06/22/2023 | Alternative | RoutineScheduled | 127-STS-32820 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 12:00 AM
05/18/2023 |  | RoutineScheduled | 101-05-0709 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
03/14/2023 |  | Routine/Scheduled | 234-13-35 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/14/2023 | Jan 1 1900 1:00PM
07/28/2023 | Alternative | RoutineScheduled | 001-STS-92311 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJI CLEAN CEN 7 |  | Pump | Pressure | Mound | UV | 600.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Pumped Out | PUMPED SEPTIC SYSTEM EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | 02:35 PM
05/30/2023 |  | RoutineScheduled | 177-STS-90403 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Discharge: HL 18, PEAK 1. Bottom zone wet, inspection was done after rain. Will stop by on a dry week. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 015-STS-339033 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 11/08/2023 |  | 15.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
11/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | Dec 30 1899 12:45PM
05/30/2023 |  |  | 2005-143-0324 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Advantex |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 12:00 AM
06/26/2023 | Alternative | Routine/Scheduled | 234-15-49 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | Dec 30 1899 12:05PM
07/05/2023 | Alternative | RoutineScheduled | 101-13-0416 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 3.000000 |  | Aqua Safe |  | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 05:10 PM
03/31/2023 |  | Routine/Scheduled | 234-12-128 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | Jan 1 1900 1:40PM
04/27/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Added sludge cleaner on media filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
04/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | pods are ponding. Need to investigate | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
07/18/2023 | Alternative | Reportable Incident | 700-STS-7253 | Newport News | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Sandfilter, High rate |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | Attached Growth Medium | [18 empty] | AOSS - Generic Sand Filter Removed sand media from unit with VAC Truck - Flushed / cleaned / scoured drain lines Replaced media with sand specified in original permit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/19/2023 | Dec 30 1899 10:45AM
09/06/2023 | Alternative |  | SP-05-157 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed. On the far side of the mounds there is a small hole/depression. No effluent presented when cycling the system. It appears to be mole/vole burrow possibly? Advised homeowner to monitor and notify us if anything changes/. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/14/2023 | Alternative | RoutineScheduled | 150-08-0116 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 gallons | septic tank | Delta Whitewater | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | Musty | Clear |  |  | 50.000000 | [12 empty] | Septic tank 4" fog, 3" sludge. Delta Whitewater 50% SS. Cleaned effluent filter and aerator filter. Pump, alarm, floats, controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/23/2023 | 07:00 PM
03/02/2023 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip |  | 450.000000 | Auxiliary Filter | Auxiliary Filter | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/03/2023 | 09:43 AM
12/05/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | Tanks were pumped. Floats, Alarms,pump working. Blower not working. Blower replace 12/9/2023. 8673.03 Hr. Field dry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 11:30 AM
07/18/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced solenoids & valve units. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | Dec 30 1899 1:44PM
11/30/2023 | Alternative | RoutineScheduled | 196.02.132 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | checked sludge, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/13/2023 |  | RoutineScheduled | 18-100-0472 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance | 182-10-0136 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
07/26/2023 | Alternative | RoutineScheduled | 181-01-0240 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | MicroFast | Siphon | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was cleaned. The treatment unit was in operating condition. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 12:00 PM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
02/15/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | EcoPod | Pump | Gravity |  | UV |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Step 20 EZ Treat pump. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 03/31/2023 | Dec 30 1899 12:26PM
09/12/2023 | Alternative | RoutineScheduled | 08-113-251 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/12/2023 | 12:00 AM
09/21/2023 | Alternative |  | VAG401197 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Pressure | Discharge |  |  | ["Distribution Pump Operation","SludgeScum Accumulation"] | ["Distribution Pump Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Repairs made 10/4 and septic and pump tank pumped out | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | 12:00 AM
04/25/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
10/09/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0119-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
09/28/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | Disinfection | Disinfection | [18 empty] | Replaced the UV ballast and replaced the fuse. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/28/2023 | Dec 30 1899 12:00PM
02/15/2023 |  |  | {FIPSCode}-STS-69257 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
12/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 12/12/2023 |  | 121.000000 | [5 empty] | Will be sent separately | Inspected | Discharge pump replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
09/27/2023 | Alternative | RoutineScheduled | 151-09-0225 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | 12:00 AM
06/09/2023 | Alternative | Reportable Incident Component Maintenance |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. System was on high level due to timer float, replaced. Recommend to minimize water usage. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
05/25/2023 |  | Routine/Scheduled | 196-05-228 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine service. Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 01:30 PM
08/10/2023 | Alternative | Routine/Scheduled | 095-STS-5641 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2.25 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 8:15AM
06/14/2023 | Alternative | Routine/Scheduled | S 800-17-0012 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 4:02PM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Two of the lines (2/5) appeared to be more nitrified and receiving more effluent. Distribution Box was uncovered and Dialflows were adjusted. System should return to proper design function now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/06/2023 | Alternative | RoutineScheduled | 181-06-0035 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. Control panel functioning properly. System did not need to be pumped. No apparent leaks in system or drain field area. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 11:15 AM
02/14/2023 |  | RoutineScheduled | 181-09-0164 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","Septic Tank Baffles","BlowerCompressorAerator Operation"] | ["Attached Growth Medium","SludgeScum Accumulation","Septic Tank Baffles","BlowerCompressorAerator Operation"] | [17 empty] | Pumped Out | The blower started to alarm because of back pressure on the blower. This was caused by the exit pipe being stopped with sludge causing the water in the treatment side of the tank to be higher than normal. The tank was pumped and cleaned. The treatment unit was pulled and replaced with a new media block. The treatment unit was then reinstalled and resealed. The tank was then filled with fresh water to ensure a fresh restart. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/11/2023 | 01:30 PM
09/07/2023 | Alternative | RoutineScheduled | 05-165-0194 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 1" FROM TOP 6-7" FROM BOTTOM EVERYTHGIN WORKING AS IT SHOULD PEAT LOOKS GOOD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 09:50 AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0212-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
03/02/2023 |  | RoutineScheduled | SP-03-326 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected | Upon arrival, the discharge pump was not working. Owner had pump replaced by others. We recommend replacing two air release valve covers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
01/09/2023 |  | Routine/Scheduled | 196.04.326 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 50.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 05:40 PM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | ATU needs pumped out due to high sludge levels. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | Dec 30 1899 2:02PM
02/14/2023 |  | RoutineScheduled | 179-STS-91611 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] |  | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected | There is effluent coming to the ground surface at the end of the first drainfield line. We contacted the installer and asked him to look at this for a recommended remedy. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | 12:05 PM
02/10/2023 |  | RoutineScheduled | 179-14-0130-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 1-5 0-11 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 20.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 10:00 AM
08/31/2023 | Alternative | RoutineScheduled | VAG408100 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | no discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/31/2023 | 12:00 AM
02/21/2023 |  | RoutineScheduled | 18-100-0018 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.600000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 12:15 PM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/12/2023 | 11:41 AM
02/28/2023 | Alternative | RoutineScheduled | SD-14-166 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Microfast media beginning to clog. Owner to arrange for a pump-out of the septic tank. Instructed owner to refill tank with fresh water after the pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
05/18/2023 |  | Routine/Scheduled | TWOR-A8HGYV | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 11:20AM
08/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | [18 empty] | Septic Tank-12"sludge 4"scum/ Microfast-16"sludge/ Pump Tank-1"sludge/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Replaced faulty contactor in the control box/ Controls, pump, floats and alarms now functioning properly/ Counts: Pump-1981 ETM- 821h 1m/ Peak-20 ETM-531h 25m/ High-29/ Watermeter-0,183,676.95/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS replaced septic pump. System appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
03/07/2023 |  | RoutineScheduled | {FIPSCode}-STS-9611 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Micro fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/31/2023 | Alternative | Reportable Incident | 136-14-0360 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the aerator not working - installed an aerator rebuild kit. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 3.5 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | 02:00 PM
02/24/2023 |  |  | 07-118-0100 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Delta DF Series |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/24/2023 | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled | 103-STS-96394 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/28/2023 | Alternative | Reportable Incident | 159-03-185 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | AOSS - Initial Visit - Alarm - System overflowing - DBox / Absorption field not accepting effluent. Unknown Service Provider! Pumped primary septic tank and aeration tank empty - aeration tank refilling with backflow from absorption field. DBox full of sludge - requires pressure wash of absorption field and further evaluation. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/29/2023 | 07:15 AM
11/01/2023 | Alternative | Routine/Scheduled | 093-18-0180 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Microfast |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 12:33PM
05/05/2023 |  | RoutineScheduled | 179-17-0063-VU | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The lower drainfield has tree saplings growing on it. These should be removed as soon as possible to prevent roots from growing into your drainfield pipes. We recommend maintaining your drainfield area in a mowed condition. We also observed that the drain near the basement walkout, is clogged & almost backing up into the basement. We recommend cleaning this drain before summer stom Season. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was not functioning upon arrival. Blower was replaced and the system should return to proper function | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/30/2023 |  | RoutineScheduled |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Prince William | EcoVirginia LLC | 1942001235 | William | Poindexter | 1.000000 |  | Clearstream ATU |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | Musty | Clear | [15 empty] | Recommended pumpout | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
01/03/2023 |  |  |  | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton |  |  | Delta Ecopod |  | Pump |  |  |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Distribution Pump Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/23/2023 | Alternative | Routine/Scheduled | 18-142-0272 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Checked the sludge level in the trash and treatment tanks and they were good. We replaced the blower and system is working properly now. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/23/2023 | Dec 30 1899 10:25AM
01/12/2023 |  | RoutineScheduled | 175-18-0470 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance | SWP 01-768 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend replacing both concrete lids & broken air release valve housing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
10/02/2023 | Alternative | Reportable Incident Component Maintenance | 099-06-0361-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to rock in pump intake not allowing pump to work. Removed rock. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
02/06/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","Septic Tank Baffles"] | ["Septic Tank Baffles","Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | SD-15-204 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
06/21/2023 |  |  | 033-14-0004-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
10/12/2023 | Alternative | Routine/Scheduled | 228-05-0163 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 8:35AM
09/29/2023 | Alternative | Routine/Scheduled | 12-120-0358A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out. No riser access -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge floats are not properly secured. Discharge floats have met life expectancy -Aeration: Water level normal. Flushed and cleaned weir. Flushed and cleaned diffuser. Checked and found high level alarm float is faulty -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 11:02AM
12/08/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced UV bulb and ballast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 11:45AM
05/15/2023 |  | RoutineScheduled | 18-163-0071 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Distribution Pump Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:00 AM
03/16/2023 | Alternative | RoutineScheduled | 061-19-172 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Control Operation" ,"Disinfection" ,"Dispersal System Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Disinfection" ,"Dispersal System Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Completed annual inspection. Replaced uv lamp as maintenance. UV housing was plugged with sludge, rinsed it out. Zone 2 check valve would not seal properly, replaced it. Drip rate on zone 1 dropped from 3.10 to 1.5 after repairs. The drip rates for both zones have dropped from the start-up rates. If there is any further decrease in rates, a bleach flush will need to be done. Microfast media is showing beginning stages of plugging. Discussed with owner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Peat fiber is badly broken down and will need replaced also sample came back bad. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/23/2023 | Dec 30 1899 3:10PM
08/04/2023 | Alternative | RoutineScheduled | 04-118-0103 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/04/2023 | 12:00 AM
11/30/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.490000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 02:20 PM
02/23/2023 |  |  | 99-120-0495A | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2250 | 1250 | 1000 | Pump | Pressure | Pad | Not Applicable |  | [] | [] |  | Septic | Black | [16 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/23/2023 | Jan 1 1900 1:45PM
12/14/2023 | Alternative | Routine/Scheduled | 800-11-0310 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 10:55AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance | 107-12-0116 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired leaks in drainfield | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
05/31/2023 | Alternative | Reportable Incident | S 800-17-0300 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | Control Operation | Control Operation | N/A | [17 empty] | Replaced pump relay | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/31/2023 | Dec 30 1899 2:30PM
06/13/2023 |  |  |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled | SD-11260 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 12:00 AM
01/31/2023 |  | RoutineScheduled | 177-17-0403-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Water in septic tank still looks a little dark but treatment is clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
03/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air line had broken. DSS moved the blower and replaced the air line. System appears to be functioning as designed at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
01/18/2023 |  | RoutineScheduled | 09-177-1091 | Pulaski | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - New River | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Eco Pure |  | Gravity | Gravity | Pad | Not Applicable | 200.000000 | ["Dispersal System Operation","Effluent Screens"] | ["Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/18/2023 | 12:00 AM
10/13/2023 | Alternative | RoutineScheduled | 196-15-0048 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | peat okay, cleaned septic filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/27/2023 |  | Routine/Scheduled | 234-15-216 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/27/2023 | Jan 1 1900 5:37PM
09/20/2023 | Alternative | Routine/Scheduled | 157-12-0074 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal level Less than 1 in of sludge 1 in of solids No signs if infiltration -Discharge/Pump Tank: Normal level 2 in of suspended solids Pulled and cleaned pump Pulled and tested all floats working properly Pulled cleaned uv light flushed housing Uv light functioning properly Plumbing intact Pump working and moving water properly Roots running through riser Riser lid is missing -Aeration: Normal level 13 in of suspended solids Tested float working properly Pulled and cleaned weir Pulled and cleaned diffuser Air line working properly -Aur Pump/Blower: 120 volts coming in Cleaned filter Air pressure sensor functioning properly Pulled 1.49 amps -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Pump pulled 11.46 amps -Drip Field: Drain field wet but not any concern | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 01:52 PM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance | 2113-06-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 | 306000 | Puraflo | none | Pump | Gravity |  | Chlorination |  |  | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The following corrections are necessary: Replace Alarm Float Control, Repair Conveyance line from the septic tank to the pump chamber, the outlet tee / effluent filter is no longer at its original elevation, improper fall between inlet and outlet tees, no Disinfection tablets present, Missing Discharge Sign, no # 3 Bluestone Present at Discharge Point for proper Post Aeration. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 10/16/2023 | 12:58 PM
08/23/2023 | Alternative | RoutineScheduled | SD-11-388 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | PuraFlo | Pump | Gravity | Trenches | Not Applicable | 56.600000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 08:00 AM
04/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Home owner called us out for wet spot at tank. Found sewage coming out of tank. Pumped out septic tried camera snaking conveyance line but was clogged. Was able to unclog an opening in the conveyance line Dug up the d-box it is 2 feet below the surface. We pumped out the d-box. A steady stream of water was running back into d-box from the 3 drain filed lines. Finally water was just dribbling into d-box. D-box has no cracks but a lot of spalling and rock showing. Camera snaked headers snake goes 50-60 feet out then stops. Not able to see to much sludge. Home owner needs to get with an AOSE Septic system is not working as it should. Also home owner said he has been pumped out in the past but its not in RME | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:00PM
12/11/2023 | Alternative | Routine/Scheduled | 136-04-0645 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The pressure switch on the aerator is not hooked up. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/11/2023 | 03:00 PM
05/16/2023 |  | Pump-Out Only | 196-14-0140 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Trash tank and processing tank pumped empty as recommended during last service visit. Refilled with fresh water for re-start. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 08:00 AM
01/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2024 | 11:49 AM
12/01/2023 | Alternative | RoutineScheduled | 16-142-0094 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 182-16-0034 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 09/26/2023 |  | 31.000000 | [5 empty] | Will be sent separately | Inspected | Repaired float that was hung up Removed roots from tank Need to move firepit and table off of drainfield | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance | 033-16-0042-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank due to scum & sludge accumulation in the tank. It is advisable to pump the aerobic treatment unit at the same time. Also the aspirator tip on the aerator is missing and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | Dec 30 1899 12:05AM
05/01/2023 |  | Reportable Incident | 234-16-192 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/01/2023 | Jan 1 1900 7:00AM
12/22/2023 | Alternative | RoutineScheduled | 132-07-0133 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/18/2024 | 12:00 AM
06/15/2023 | Alternative | Routine/Scheduled | 136-19-0184 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad |  | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - peatmoss in fair condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 07:00 AM
06/30/2023 | Alternative | Follow-Up Component Maintenance | 179-STS-90548 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Pressure | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to verify drip rates. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 04:50 AM
10/04/2023 | Alternative | RoutineScheduled | 96-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | [5 empty] | Musty | Clear | 7.000000 | 5.000000 |  | 0.000000 | [11 empty] | Chlorine Tablets Empty, de-chlorine is stocked aerator running. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | 145-04-0013 | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20 | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The recirculating pump was pulled and cleaned. The RSV was pulled and cleaned. The textile sheets were sprayed off. The lateral grid was pulled and rodded. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | 08:55 PM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
05/02/2023 |  | RoutineScheduled | 181-09-0072 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | MicroFast | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system will be pumped next year as a routine pumping. The effluent and blower filters were both cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 09:50 PM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | ATU needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/16/2024 | Dec 30 1899 1:58PM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-335114 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Auxiliary Filter" ,"Control Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"Control Operation" ,"Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | filter clog | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
03/09/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 03/09/2023 |  | 175.000000 | [5 empty] | Will be sent separately | Inspected | Repaired float wiring and adjusted dbox to help with saturated drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
11/08/2023 | Alternative | Follow-Up Component Maintenance | {FIPSCode}-STS-67146 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new blower and air filter and mounted them on tank. Installed EZ Set riser & lid on inlet of septic tank. Treated and cleaned aerobic treatment unit. Septic/ATU tank & distribution tank pumped by others. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
05/03/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | 12:00 AM
01/13/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2992 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/13/2023 | Jan 1 1900 9:40AM
05/02/2023 | Alternative | RoutineScheduled | SD-06-83 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 43.750000 | ["Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens","Dispersal System Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 10:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | anua tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/28/2023 |  | Routine/Scheduled | 234-17-0039 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Jan 1 1900 12:05PM
03/14/2023 |  | RoutineScheduled | 099-STS-91941 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Septic | Cloudy | [5 empty] | 03/14/2023 |  | 431.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Sample most likely will fail due to blower being off when we arrived, turned back so treatment should get better and bad smell should go away in couple days. Blower 3.33 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
03/05/2023 |  | Follow-Up | 041-STS-260783 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 4540 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/05/2023 | Jan 1 1900 10:30AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Alarm was on upon arrival. Audible had been unplugged and was plugged back in. Recirculation float was stuck down. The system should return to proper operation now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/03/2023 |  | RoutineScheduled | 09-192-012 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 4 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/03/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0401-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
03/28/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
11/28/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | Dec 30 1899 2:25PM
06/13/2023 | Alternative | Routine/Scheduled | 2003-143-0223 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 10:19 AM
02/23/2023 |  | Routine/Scheduled | NYII-AZMPW2 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | Jan 1 1900 8:15AM
07/17/2023 | Alternative | RoutineScheduled | VAG401198 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 02:30 PM
09/27/2023 | Alternative | Follow-Up | 15-120-0320AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [19 empty] | 09/27/2023 |  | -6.000000 |  |  | 2.700000 |  |  |  |  | -Installation of 18" Riser on the Septic Tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 11:16AM
08/22/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Real Estate Inspection Processing tank pumped empty by Consolidate Waste Services - RSV, recirc pump & effluent screen serviced - refilled with fresh water for restart. Treatment Module - media drapes & Spray grid serviced. Pump tank - float sensors, pump and controls operating. DBox - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | Dec 30 1899 7:00AM
05/04/2023 |  | RoutineScheduled | 153-STS-20276 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
05/26/2023 | Alternative | Reportable Incident | 073-STS-105176 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced damaged distribution box with new 8 port concrete DBox. Spliced to existing Conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 PM
11/06/2023 | Alternative | Routine/Scheduled | 16-142-0266 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Due for pump out. Refill is required for proper operation and to prevent damage to components -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Flushed and cleaned disk filter -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Media lid safety support struts have failed. Media lid is warped and cracked. Media has exceeded life expectancy -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly -Drip Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 10:57AM
03/27/2023 |  | RoutineScheduled | SWT-98-363 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The return diaphragms.in the drip dispersal system are not holding properly. Unfortunately, this part is obsolete and cannot be replaced. We recommend installing a new hydraulic unit, control panel, air release valves and check valves. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/02/2023 | 07:49 AM
04/13/2023 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Loudoun | SLUSSER, JAMES B | 1934000064 | JAMES | SLUSSER | 1.000000 | 1250 | Delta Environmental Products, DF Series | Septic Tank Only | Pump | Drip | Drip Tubing | None |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] |  |  | brackish_clear |  |  | 10.000000 | [12 empty] | [Comments]: Sludge in pump station needs to be removed. Pump out scheduled for 5/17/2013 jbs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/12/2013 | 12:08 PM
08/03/2023 | Alternative | RoutineScheduled Component Maintenance | 107-06-0513 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 08/03/2023 |  | 14.000000 | [5 empty] | Will be sent separately | Inspected | Blower air supply repaired Blower loud squeal could be issue soon | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
03/18/2023 |  | RoutineScheduled | 175-16-0043 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | SBR |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | 7.300000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/23/2023 | 12:00 AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
08/25/2023 | Alternative | Reportable Incident |  | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | Distribution Pump Operation | N/A | [17 empty] | System alarming - found discharge pump separated from forcemain - drip field is saturated and not accepting effluent at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/29/2023 | Dec 30 1899 12:30PM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-91864 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Effluent Screens" ,"Recirculation Pump" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Effluent Screens" ,"Recirculation Pump" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
07/05/2023 | Alternative | Routine/Scheduled | 05-160-0446 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 28.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 09:00 AM
09/08/2023 | Alternative | RoutineScheduled | SD-08-124 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2000 | Eco-Pure |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter","Attached Growth Medium"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge/Scum Accumulation - Septic 4", Pump 3" Peat Moss Raked | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 09:30 AM
04/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
12/09/2023 | Alternative | RoutineScheduled | 109-09-0262 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20 |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Flushed treatment unit spray manifold. Cleaned recirculation pump solids basket filter. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2024 | 07:03 PM
02/07/2023 |  | RoutineScheduled | 179-16-0108-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. R.O. float was stuck on, replaced it under warranty. Small rust stain observed at midseam corner closer to garage, inlet end of tank. Not leaking now, will continue to monitor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
06/15/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Multi-Flo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/06/2023 |  | RoutineScheduled | 153-STS-20288 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
04/28/2023 | Alternative | Routine/Scheduled | 097-STS-96191 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Purasys |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped and serviced septic tank as recommended during last service visit. Refilled Poly tank with fresh water for system re-start. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 08:30 AM
12/04/2023 | Alternative | RoutineScheduled | 128-04-284 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 2.000000 | 1500 | 500 solids | 1000 microfast | Pump | Pressure | Pad | Not Applicable |  | ["None"] | ["None"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled | 181-04-0327 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin filters were both pulled and cleaned. The treatment unit was in good operating condition. The controls were operating as designed. There was return effluent returning to the pump tank so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 01:45 PM
08/17/2023 | Alternative | Follow-Up Component Maintenance | 179-15-0141-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank to assist pumper with proper pump out. Reassembled components and homeowner refilled thr tank back to proper levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
06/05/2023 | Alternative | RoutineScheduled | 101-12-0027 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Mound | Not Applicable | 150.000000 | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 11:30 AM
04/21/2023 | Alternative | RoutineScheduled | 115-07-0203 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | [15 empty] | Inspected | Sludge levels-1" Scum & 16" Sludge in Septic tank. Pump tank 12" Sludge. Cleaned Effluent Filter, it was very backed up. 1hp Goulds 1012H pump operational. Alarm float is functional. Peat moss has some minor ponding water in all 4 quadrants, Turned Peat in all parts it shows it age, minor roots noted. May need to pump out tank next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
09/11/2023 | Alternative | Pump-Out Only | 121-STS-12233 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | [7 empty] | [] | [] | [17 empty] | Pumped Out | Pumping & Cleaning Septic Tank and PreTreatment Unit (1000 gallons) JOB SCOPE: Pumped/cleaned septic tank; septic system is functioning at this time but not as designed as there are components that are recommended to be repaired/replaced. - septic tank has two inlet lines entering, inlet line coming from home is swagged outside of the tank - outlet line is kicked up but tee levels are normal - septic tank has crack in the corner but appears to be holding water at this time - Whirlwind blower was not working, customer is aware of required inspections | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/12/2023 | 12:00 AM
07/05/2023 | Alternative | Routine/Scheduled | 073-STS-101944 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Routine Service - Real Estate inspection. Septic tank - pumped for inspection - effluent screen serviced. Pump Tank - 500g - float sensors, pump and controls operating. BioFilter - fiberglass - Peatmoss new - recently replaced - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 07:00 AM
08/24/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance | 182-04-0612 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
10/12/2023 | Alternative | Follow-Up Component Maintenance | 179-07-0064-SWT | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with a proper pump out. Reassembled components and tank was refilled by a water truck. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
10/26/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 2:35PM
01/20/2023 | Alternative | RoutineScheduled | 133-STS-101232 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 01/20/2023 | [10 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/10/2023 | Alternative | Routine/Scheduled | 234-14-297 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced screen filter and pump relay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | Dec 30 1899 10:00AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/07/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | Jan 1 1900 7:20PM
12/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 02:30 PM
05/01/2023 | Alternative | Routine/Scheduled | 800-11-0074 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | Dec 30 1899 10:20AM
04/10/2023 |  | RoutineScheduled | 124-STS-2379 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 2 homes | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/10/2023 | 12:00 AM
02/28/2023 |  | Routine/Scheduled | 234-15-21 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | Jan 1 1900 9:20AM
07/25/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 12:00 AM
01/03/2023 |  | Reportable Incident | 175-05-0868 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm. Pump running, but effluent level not dropping. Eventually located 2 broken forcemain elbows in the filterbed. Vacuum used to extract sand and gravel from about 6' of pipe. Old manifold was removed to facilitate forcemain repair. Due to some crack damage and being constructed from sch 30 piping, the manifold was replaced with a sch 40 manifold and wrapped in weed fabric to reduce root intrusion. Flushed forcemain and verified full flow to the new manifold. Four new willow trees were planted to replace dead or missing trees. Reseeded areas of excavation on January 9th. Air pre-filter cleaned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | ATU compressor needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/17/2023 | Dec 30 1899 12:46PM
04/20/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/12/2023 | Alternative |  | 179-STS-92019 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/11/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids i septic tank. Flushed treatment unit spray manifold. Cleaned recirculation pump solids basket filter. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 07:03 PM
08/02/2023 | Alternative | RoutineScheduled | 06-163-0130 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Dispersal System Operation","Level Sensor Operation","Distribution Pump Operation","Control Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 12:00 AM
01/09/2023 |  | Routine/Scheduled | 234-17-138 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 11:55AM
03/07/2023 |  | Pump-Out Only |  | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out | Sale inspection | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/13/2023 | 07:20 AM
02/13/2023 | Alternative | Reportable Incident | 157-05-339 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Biofilter Changeout - Pumped septic tank empty - replaced aged effluent screen with new. 02/16/2023 - removed spent biofilter and replaced with new. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/17/2023 | 07:45 AM
08/14/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex RT |  |  | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation","Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | ["SludgeScum Accumulation","Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
12/19/2023 | Alternative | RoutineScheduled | VAG408231 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/19/2023 | 12:00 AM
12/12/2023 | Alternative | RoutineScheduled | 107-15-0052 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | SEPTIC TANK ONLY | ADVANTEXAX20 | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | THE SYSTEM DID NOT NEED TO BE PUMPED. THE EFFLUENT FILTER WAS PULLED AND CLEANED. THE TWO PUMPS WERE BOTH PULLED AND CLEANED. THE TEXTILE SHEETS WERE SPRAYED OFF. THE LATERALS WERE CLEANED. THE CONTROLS WERE OPERATING AS DESIGNED. THERE WAS EFFLUENT RETURNING TO THE PUMP TANK. THE DRIP FIELD WAS OPERATING AS DESIGNED. THERE WERE NO VISIBLE LEAKS IN THE DRIP FIELD. THE LIDS WERE SECURED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 01:15 PM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | 047-16-194 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank and aerobic treatment unit due to the scum and sludge accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
01/05/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | [7 empty] | 01/05/2023 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected | Septic tank pumped Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90436 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Bad float (off). Water flowing out of ground while pump is dozing field, possible broken fitting. settlement around tanks. Customer will contact builder to have installer to come back and repaired since system still under warranty. Hl 10, Blower 2.92. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:08 AM
02/01/2023 |  | RoutineScheduled | 127-STS-33297 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 |  | EZ Treat 600 |  | Gravity | Pressure | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | Jan 1 1900 12:00PM
12/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/28/2023 | Alternative | Reportable Incident | 093-14-0080 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced timer enable float and WE 20 pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/28/2023 | Dec 30 1899 2:00PM
12/13/2023 | Alternative | Routine/Scheduled | 127-STS-35535 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 11:00AM
01/04/2023 |  | Routine/Scheduled | NYII-AYTJT3 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV control panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | Jan 1 1900 8:15AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 5.000000 |  | Clearstream | Clearstream | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent pump in (600NC on Left from Splitter) is stuck on and will not stop running without shutting off breakers. Pump was left running so as not to flood the tank and cause further issues. Repairs are in progress | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
03/07/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Jan 1 1900 12:26PM
10/24/2023 | Alternative | Reportable Incident | 2019-143-0048 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Other"] | ["Other"] | [18 empty] | Replaced Norweco Agitator | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
12/11/2023 | Alternative |  | 033-11-0105-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/20/2023 |  | RoutineScheduled | 179-13-0215-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Recomend we pump out all tanks during next years inspection. Heavy wipes from prior homeowner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
03/03/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower connection was repaired. System appears to be functioning as designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
04/27/2023 |  | RoutineScheduled | 06-172-0179A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Best One |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","BlowerCompressorAerator Operation","Control Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Distribution box was uncovered and the dialflows were adjusted | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/14/2023 | Alternative | Initial Visit | 093-STS-14995 | Isle Of Wight | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to some issues - system was flooded. Meet with the pumping company and pumped out the Clearstream tank and pump tank. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream, cleaned the filter in the septic tank, and cleaned the mesh screen in the spinfilter. Disconnected the pressure switch on the aerator. Due to the tanks being flooded the UV was as well. The timer is set to 7 minutes every 2 hours. Did not take initial samples. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/14/2023 | Dec 30 1899 12:00PM
12/12/2023 | Alternative | Reportable Incident Component Maintenance |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Owner heard panel making rapid clicking noises and turned off the pump switches. Water level was all the way down to the pump intakes, timer float was stuck on. Replaced timer float and override float. Added some water back to the tank and checked pumps. Pump #1 not pumping. Removed pump and checked capacitor, not working. Reinstalled the pump and locked out pump #1 with alternating relay selector lever (so now control panel will only run pump #2). Capacitor on order. Advised owner that pump may have more damage from running dry that the capacitor won't fix, but worth a try. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
03/30/2023 |  | RoutineScheduled | 085-STS-33743 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | Purasys SBR |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
07/25/2023 | Alternative | Reportable Incident Component Maintenance | SD-11-168 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm. Spin filter was plugged and reduced the drip rate. Cleaned the filter and pump intake. Ran one complete dose of 9.25 minutes and only netted 36 gals after water finished draining back through spin filter flush line and return-to-septic line. Monitored pressure gauges during cycle and determined that adequate back-pressure was not reached till 1 min 45 seconds. Drip rate after pressurization was approximately 4.8 gpm. Increased run time to 12 min to get the full 50 gal dose. If filter clogs again, tank will have to be pumped and rinsed to attempt to remove the debris. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
03/20/2023 |  | Routine/Scheduled | 12-120-0305A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/20/2023 | Jan 1 1900 9:03AM
07/11/2023 | Alternative | RoutineScheduled | 171-08-0453 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 04:45 PM
11/06/2023 | Alternative | Routine/Scheduled |  | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [16 empty] | Test Tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | Dec 30 1899 9:00AM
12/04/2023 | Alternative | Reportable Incident | 147-17-0007 | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | System was flooded due to a running toilet. Need to pump and clean the Clearstream tank and pump tank. Too much solids got through stopping up screens on the pump. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/04/2023 | Dec 30 1899 12:00PM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-07-0146 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/22/2023 |  | RoutineScheduled | 067-STS-38653 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 6" of accumulated solids in first compartment of septic tank with a 3" crust. 4" of accumulated solids in second compartment of septic tank with 0" of crust. 2" of accumulated solids in recirculation portion of treatment unit. 1" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Adjusted flow rate of the recirculation pump slightly. Tested floats, pump and alarm. Excellent treatment. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 07:03 PM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping ATU. Recommend mowing drainfield area to keep larger vegetation down. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
07/17/2023 | Alternative | RoutineScheduled | 15-152-061 | Lee | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ADVANTEX |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Distribution Pump Operation","Recirculation Pump","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Recirculation Pump","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 12:00 AM
05/15/2023 |  | RoutineScheduled | 175-06-0532 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Air relief valve is broken. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
12/21/2023 | Alternative | RoutineScheduled | 07-197-A12 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/21/2023 | 12:00 AM
09/28/2023 | Alternative | Routine/Scheduled | 093-05-0388 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | Dec 30 1899 9:17AM
09/14/2023 | Alternative | RoutineScheduled | 09-197-041 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | 1 1/2' Solids in pretreatment side | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Gravity | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-2"sludge 3"scum/ Microfast-16"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and working properly/ Control, pump, floats and alarms functioning properly/ Counts: Pump-8551 ETM-703h 36m On-4m 54s Off-1h 30m/ Peak-1154/ High-58/ Watermeter-1,858,426/ No breakout or spongy areas on the drip field and dosing properly/ Drip rates-4.9 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/01/2023 | Alternative | Reportable Incident | 181-08-0192 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | MicroFast | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Control Operation"] | YES | [17 empty] | The system did not need to be pumped. It was determined that lightning had come in on the system taking out the blower, discharge pump and the high water alarm float. All three components were pulled and replaced with new components. The return pressure gauge was also replaced. The spin filter and blower filter was both pulled and cleaned. The control boxes were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/16/2023 | 12:15 PM
10/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | J&G Septic Service |  | James | Kleindl | 2.000000 | 3000 | Mirco fast |  | Pump | Pressure | Pad | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | Dec 30 1899 9:30AM
06/26/2023 | Alternative | RoutineScheduled | 18-142-0350 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
08/02/2023 | Alternative |  | {FIPSCode}-STS-3859 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/02/2023 |  | 12.900000 |  |  | 17.400000 |  |  | Will be sent separately |  | BOD: 12.9 TSS: 17.4 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/02/2023 | 12:00 AM
10/13/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine Annual, nothing to report | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
11/01/2023 | Alternative | Routine/Scheduled | 228-17-0384 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 1:55PM
10/17/2023 | Alternative | RoutineScheduled | 101-14-0521 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Aquasafe |  | Gravity | Gravity | Discharge | UV | 150.000000 | [] | [] |  |  |  | 6.400000 | 7.730000 |  |  |  | 10/17/2023 | Sample Tap |  |  | 235.900000 | 1.500000 |  |  | Attached to this report |  | Ecoli testing was 235.9 prior to UV bulb cleaning. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 11:00 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Uv bulb was burned out at time of inspection and was replaced while onsite. ATU needs to be pumped due to high sludge levels. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
05/22/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-02-365 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
01/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
01/03/2023 |  | RoutineScheduled | 08-118-0060 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton |  |  | Advantex |  | Pump |  |  |  |  | [] | ["Attached Growth Medium","Control Operation","Level Sensor Operation","Effluent Screens","Distribution Pump Operation","Recirculation Pump"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | 12:00 AM
05/19/2023 | Alternative | Routine/Scheduled | 128-10-023 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level - recommend pumpout and refill. Aeration tank - normal level - mixing present - compressor serviced. PUmp tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 02:00 PM
11/22/2023 | Alternative |  | 12-113-109 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/22/2023 |  | 2.650000 |  |  | 1.200000 |  |  | Will be sent separately |  | BOD: 2.65 TSS: 1.20 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/22/2023 | 12:00 AM
03/31/2023 |  |  | 2004-143-0327 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","BlowerCompressorAerator Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
11/29/2023 | Alternative | Routine/Scheduled | 228-12-0133 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | Dec 30 1899 2:00PM
12/26/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0058-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the aerobic treatment unit. It may be advantageous to pump the septic tank at the same time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
11/15/2023 | Alternative | Routine/Scheduled | 166-97-304 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Was flooded due to discharge pump being bad Pulled and cleaned filter Has about 1-2" of solids and wipes and 6" of sludge -Discharge/Pump Tank: Replaced discharge pump on site Pump and floats working properly -Peat Moss: Peat in good condition Raked out any low spots -Control Panel: Working properly Discharge pump pulling 8.86amps | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 01:29 PM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Floats need replacing. Puraflo modules ponding. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/17/2023 | Dec 30 1899 12:46PM
12/15/2023 | Alternative | Follow-Up Component Maintenance | 154-06-0241 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank pumped out by others 2 days prior. Degraded peat was removed by hand and new peat was installed. Peat was purchased from Wrights Ready Mix. Degraded peat was disposed at Spotsylvania Refuse. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
03/02/2023 |  |  | -STS-92104 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
07/21/2023 | Alternative | Initial Visit | 127-STS-33095 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls operating. LPP Field - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | Dec 30 1899 9:30AM
11/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | Dec 30 1899 2:40PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Drip panel audible alarm is intermittent. Recommend replacing it. Visual is still functional. Blower motor sounds odd but is functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/16/2023 | Alternative | RoutineScheduled | 150-18-0173 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled | 128-06-205 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, peat, & sludge. system check -okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/16/2023 | Alternative | RoutineScheduled | 09-192-239 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/16/2023 | 12:00 AM
12/08/2023 | Alternative | Routine/Scheduled | 145-STS-259415 | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 12:00PM
09/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  | 1500 |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 2:45PM
11/01/2023 | Alternative | Follow-Up Component Maintenance | 099-06-0328-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed septic tank inlet riser. Replaced low quality compromised distribution box with high quality monster distribution box. Investigated the header line not taking water. Replaced header line 1 close to old stump. Replaced header line 3. Added Root-X to all lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
08/01/2023 | Alternative | RoutineScheduled | 027-STS-17384 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/01/2023 | 12:00 AM
06/22/2023 | Alternative | RoutineScheduled | 150-07-0283 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [7 empty] | 06/01/2023 | Sample Chamber | 23.000000 | [5 empty] | Attached to this report |  | Septic Tank-0"sludge 0"scum/ Microfast-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Replaced faulty redundant off float/ Controls, pumps, floats and alarms now functioning properly/ Counts: Pump1-806 ETM-41h 11m/ Pump2-760 ETM-39h 29m On-3m 11s Off-9h 57m/ Peak-13/ High-15/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/18/2023 |  | Routine/Scheduled | 234-17-0332 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 3:05PM
07/10/2023 | Alternative | Routine/Scheduled | 234-13-187 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/10/2023 | Dec 30 1899 9:35AM
01/20/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 12:02 PM
06/14/2023 | Alternative | Follow-Up | 2012-126-013 | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Paul Small LLC | 1942001402 | Paul | Small | [8 empty] | 3500.000000 | [] | [] |  | None | Clear | 7.000000 |  |  |  |  | 06/14/2023 | Pump Chamber | 4.000000 |  |  | 3.100000 |  |  | Attached to this report |  | Purpose of visit was for formal lab sampling only. No observable issues were found. System is operating exceptionally well. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | Dec 30 1899 10:40AM
02/09/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/18/2023 |  | RoutineScheduled | 2006-143-0270 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | BioMicrobis Microfast |  | Pump | Pressure |  |  |  | [] | ["Attached Growth Medium","Level Sensor Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | 12:00 AM
07/08/2023 | Alternative | Pump-Out Only | 043-03-304 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 | 1000 | 1000 | [6 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
05/02/2023 |  | RoutineScheduled | 101-06-0350 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Pump | Gravity | Trenches |  | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 09:15 AM
11/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0085-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted on last year?s inspection, there is effluent surfacing in several parts of the dispersal area. We would recommend contacting an Alternative Onsite Soil Evaluator for repair options. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | 08:44 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-09-0104-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | NA | Musty | Clear | [5 empty] | 06/27/2023 | [7 empty] | Will be sent separately | Inspected | Routine inspection. Found water coming to surface on drip field due to 2 bad emitters, replaced. Pressure at ARV"s was high, so we installed a 40 psi regulator to bring it down. Root growing in recirc tank. Drip field needs bleach flush. Will send proposal for bleach flush drip field, to remove root and seal tank, at the time we will check drip field to see if there is any more bad emitters. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
10/09/2023 | Alternative |  |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1000.000000 | 750 |  |  | Pump | Pressure | Trenches | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | None | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | Dec 30 1899 9:30AM
09/25/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced 2" brass check valve. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 12:58PM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | SD-14-303 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Level Sensor Operation" ,"Control Operation"] | ["Recirculation Pump" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Replaced burnt out alarm horn in drip panel. Replaced both bottom floats (stuck on) in the drip tank. Phone line tested good for Vericomm panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
02/13/2023 |  | RoutineScheduled | 041-STS-260004 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1000 | 1000 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation","Control Operation"] | YES | None | Clear | 9.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | Jan 1 1900 11:00AM
04/13/2023 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | SLUSSER, JAMES B | 1934000064 | JAMES | SLUSSER | 1.000000 | 1250 | Septic Tank Only | Septic Tank Only | Pump | Manifold | Aggregate Trench | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/12/2013 | 12:24 PM
03/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/15/2023 | Alternative | RoutineScheduled | 031-STS-25809 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Norweco |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | routine inspection - Old septic tank - 2" scum on top and 12" sludge on bottom, Norweco Septic zone 6 " sludge- Aeration zone- aerator working good aeration- No smells- Discharge tank 3" sludge trace (light), Cleaned Biofilter- both parts, very dirty- - Lids are secure- | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
01/03/2023 |  | RoutineScheduled | SWP-04-252 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Pungent | Dark Brown | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank due scum & sludge accumulation in the tank. As noted previously, the peat has deteriorated and is no longer providing proper treatment. We recommend replacing the peat or installing a different treatment unit. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | 07:17 AM
01/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/13/2023 |  |  | 127-STS-31603 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Purasys | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-111 | Culpeper | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | The ATU blower has stopped working and will need to be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/02/2023 | 06:05 AM
07/14/2023 | Alternative | Reportable Incident Component Maintenance | SD-15-113 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Level Sensor Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm. Found all floats working incorrectly: RO (bottom) stuck off, TE flickering on & off, OVRD & H/L both stuck on. Replaced all 4 float switches and verified proper operation. Cleaned disc filter and then ran a test cycle. Pump rate initially was high due to debris under the field flush diaphragm. Drip rate returned to normal after cleaning the valve. Advised owner to go easy on water use until the alarm light cleared. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0215 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
09/08/2023 | Alternative |  | 150-09-0137 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["SludgeScum Accumulation"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/28/2023 | Alternative | Reportable Incident | S 800-17-0089 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Meet with the pumping company and pumped and cleaned the pump tank, pumped and cleaned the Clearstream tank, and pumped the septic tank. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the mesh screen in the spinfilter, and changed the filter in the aerator. Replaced the UV ballast. Disconnected the pressure switch on the aerator due to the pumping. Raining at the time of service - could not check the drainfield. The timer is set to 8 minutes every 2 hours. Need to go back set pressures, perform a draw down test, turn UV back on, and hook the pressure switch back up. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/28/2023 | Dec 30 1899 9:45AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
12/15/2023 | Alternative | RoutineScheduled | 05-173-228 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Eco Flo |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | ["Effluent Screens"] | ["Effluent Screens","Dispersal System Operation","SludgeScum Accumulation","Attached Growth Medium"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | Dec 30 1899 12:00PM
11/10/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0324-SWP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic/ATU tank and pump tank due to the scum and sludge accumulation in the tanks. We recommend installing a new blower and blower control panel and raising the blower to prevent it from flooding. We also recommend installing a new headworks box heater and zone return diaphragm. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | 08:44 AM
08/13/2023 | Alternative | Follow-Up |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Dispersal System Operation"] | ["Attached Growth Medium","Dispersal System Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/18/2023 | 01:33 PM
09/15/2023 | Alternative | Reportable Incident | SWP-04-595 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [17 empty] | Inspected | replaced pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 10:00 AM
03/30/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/30/2023 | Alternative | RoutineScheduled | 061-17-219 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Strongly recommend pumping Norweco tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/11/2023 | Alternative | RoutineScheduled | 175-05-0001 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank to Delta DF-ATU | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [17 empty] | Septic Tank-6"sludge 3"scum/ ATU-2"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-38777 ETM-14h/ High-21/ Watermeter-1545230 On-6m 8s Off-1h 54m/ No breakout or spongy areas on the drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | Dec 30 1899 11:25AM
02/08/2023 | Alternative | RoutineScheduled | SD-15-68 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2500 | septic | Microfast | Gravity | Pressure | Discharge | UV |  | [] | [] | YES | None | Clear | 7.020000 |  |  |  | Eff D.O. = 6.1 E.coli = 84.5 | 02/08/2023 | Sample Chamber | 4.000000 |  |  | 2.300000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/27/2023 | 08:55 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 182-03-0018 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend media replacement due to ponding. Let us know if want this completed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-18 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, we recommend replacing the Advantex module lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
03/03/2023 |  | RoutineScheduled | 177-11-0112-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/27/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Fast O.5 Bio-Microbics |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Initial routine yearly inspection -Advantex AX20 RT-3 Control Panel, alarm sounds, ran in test mode. Owner confirmed a lightning hit took out his irrigation. Septic Tank- minimal scum & 8" sludge- Recir zone 8" sludge - Dischagre zone - 8" sludge- Pump meter reading recirc 933 vs 526 min and 73919 vs 39423 cycles, discharge 110min vs 69.2 min and 1809 cycles vs 1147 cycles last year- Lightning burned up the wirenuts on each side of junction boxes replaced them and system should return to normal opperation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/28/2023 | 08:30 PM
08/07/2023 | Alternative | Routine/Scheduled | 19-120-0014AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/07/2023 | Dec 30 1899 8:43AM
01/03/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-69890 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Pad | Not Applicable |  | [] | [] | [18 empty] | Levels High due to ground water but nothing surfacing on ground. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
01/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Dec 30 1899 3:55PM
08/08/2023 | Alternative | Reportable Incident | 234-17-282 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | Control Operation | Control Operation | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/08/2023 | Dec 30 1899 4:00PM
09/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1000 | septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled | 153-STS-20320 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-6"sludge 1"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pump, floats and alarms are functioning properly/ Puraflo peat turned in all 5 modules and is in good condition/ Counts: Pump-073677 ETM-0054180 On-56s Off-2h/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/08/2023 | Alternative | Follow-Up Component Maintenance | 107-06-0802 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2000 | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Peat replaced and septic tank pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
03/17/2023 |  | RoutineScheduled | 132-04-0326 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Trenches | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/19/2023 | 12:00 AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Was unable to access septic and advantex unit. Covered over with bushes | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
07/14/2023 | Alternative | RoutineScheduled | 103-STS-101197 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/27/2023 | Alternative | Routine/Scheduled | 228-03-0308 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/27/2023 | Dec 30 1899 8:30AM
04/14/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:05 PM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20225 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
12/05/2023 | Alternative | Routine/Scheduled | 228-14-0301 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced aerator and UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | Dec 30 1899 2:00PM
12/19/2023 | Alternative | Routine/Scheduled | 800-STS-15023 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 9:00AM
11/06/2023 | Alternative | RoutineScheduled Component Maintenance | 099-18-0080 SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Water level in media a little above normal due to filamentus bacteria taking over, treatment looks amazing (crystal clear) will check next year. septic tank has a products that don't break down, spoke to customer about it. HL-8,LL-17, OVERRIDE-4. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0298-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Leak on both risers on septic tank. Small tree planted on top of septic tank, spoke to customer about moving it. Media showing its age, recommend evaluating it next year. Will send proposal for sealing leaks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
10/31/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | See attached analytics | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
02/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Pressure | Mound | Not Applicable |  | ["Attached Growth Medium"] | [] | NO | [17 empty] | Septic Tank-4"sludge 2"scum/ Pump Tank to Puraflo Modules-2"sludge/ Discharge Pump Tank-3"sludge/ No pump out needed at this time/ Peat in 3 of 5 modules requires peat replacement due to ponding issues/ Controls, pumps, floats and alarms are functioning properly/ Counts for Puraflo Panel: Pump1-136832 ETM-1194304h 7m/ Pump2-989888 ETM-2800128h 2405m/ Peak-262720/ High-58/ Counts for Pump to Mound: Pump1-3679 ETM-382542/ Pump2-5432 ETM-26837/ No breakout or spongy areas on the mound. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
08/28/2023 | Alternative | Pump-Out Only |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | Supervised pumpout of trash tank and pump tank by Ducks Septic Service - no refill required. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | Dec 30 1899 8:30AM
03/15/2023 |  | Follow-Up |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] | [8 empty] | 03/15/2023 |  | 3.000000 |  |  | 4.900000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 08:40 AM