03/28/2023 |  | RoutineScheduled | 179-STS-91798 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [5 empty] | 03/28/2023 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Blower 3.22amps. HL 2, LL3. Leak on pump tank riser below junction box. Pump tank has an access point on inlet side and that plastic lid is buried 12 inches in the ground may not be watertight, strongly recommend bring it up to grade. This would also provide access to tank when needed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-337314 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Need to relocate water softner discharge off of drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
08/01/2023 | Alternative | RoutineScheduled | 15-113-104 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/01/2023 | 12:00 AM
05/02/2023 | Alternative | Routine/Scheduled | PPIE-9LNKKH | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EcoPod |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Dec 30 1899 11:15AM
11/02/2023 | Alternative | Routine/Scheduled | 2018-143-0109 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/02/2023 | 10:17 AM
06/01/2023 | Alternative | Routine/Scheduled | 151-07-0172 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Trenches | Not Applicable | 300.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - single module - peatmoss in poor condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 11:00 AM
01/03/2023 |  | RoutineScheduled | 179-15-0004-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Hoot | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | ["Effluent Screens" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Customer had alarm. Cleaned pump, filters and disk filter. We recommend replacing the psi gauge in the pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
02/16/2023 |  | Routine/Scheduled | 234-19-0033 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | Jan 1 1900 11:30AM
05/17/2023 |  | RoutineScheduled | 2130-09-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | UV | 250.000000 | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NA | Musty | Clear | 7.200000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/20/2023 | 12:00 AM
08/07/2023 | Alternative | RoutineScheduled | 01-137-0430 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/11/2023 | Alternative | RoutineScheduled | 019-STS-23891 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | BioMicrobics MicroFast 0.50 |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 20" of accumulated solids in septic tank. 4" of solids in discharge pump tank. Cleaned drip manifold spin filter. Cleaned blower air filter. Adjusted discharge off time - 2 hours to 1 hour. It may be necessary to pump out septic tank next year. Good aeration and excellent treatment quality. Repaired drip tubing where a coupling had become detached. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 07:03 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Upper right lines might be receiving more effluent than the rest. Recommended to homeowner to contact DSS regarding the possibility of balancing and/or flushing the lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/03/2023 |  | Routine/Scheduled | 234-16-119 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [14 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | Jan 1 1900 3:35PM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/16/2023 |  | Routine/Scheduled | 04-142-0147 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 200.000000 | ["Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | NO | [17 empty] | The Advantex manifold was flushed. A few emitters on the manifold were unclothed. The recirculation pump vault filter was checked. The phone line for telemetry did not work. There were no overrides in the past 30 days | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/16/2023 | Jan 1 1900 2:09PM
07/25/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Aquarobic Mini Plant |  | Pump | Gravity | Trenches |  | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/17/2023 | 01:38 PM
01/23/2023 |  |  | 087-STS-6181 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Aquaklear | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
11/14/2023 | Alternative | Routine/Scheduled | 15-120-0262A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/14/2023 | Dec 30 1899 12:30PM
03/24/2023 |  | RoutineScheduled | SWP-04-417 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend filling in drainfield lines where they have settled, then regrading and reseeding them with grass. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
04/25/2023 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex | Orenco Advantex | Pump | Gravity | Pad | Not Applicable | 750.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - recommend pump out. Processing Tank - RSV, Recirc pump and effluent screen serviced. Treatment Modules (2) - media drapes & spray grids serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 1:00PM
07/28/2023 | Alternative | RoutineScheduled Component Maintenance | 033-17-0013-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Multiflo FTB | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
04/27/2023 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 01:54 PM
12/18/2023 | Alternative | RoutineScheduled | 121-STS-12842 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 2.000000 | 2000 | ATL |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Distribution Pump Operation","SludgeScum Accumulation"] | NA | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 2000 | Puraflo Peat Moss |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [16 empty] | Inspected | Sludge level-1-2" scum-8-9" sludge in Septic tank - Pump Is operational, timer controlled dosing. 18978 vs 17668 cycle count last year = 1310 cycles pumped this year and time pumped 177.64 hrs vs 169.80 hours. Pump ran about 7.76hrs since last visit. Peat moss was replaced in 2020 and looks like new- Peat was turned in all 5 pods, Looks in very good condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 09:30 AM
02/09/2023 |  | RoutineScheduled | 177-STS-89799 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 02/09/2023 | [10 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
08/30/2023 | Alternative | Reportable Incident |  | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | System Alarming - found compressor pulling extreme high amperage - and tripping breaker - requires replacement - rotary compressor cannot rebuild on property. Trash Tank - normal level Aeration tank - normal level - no mixing present - compressor failure. Pump Tank - float sensors, pump and controls operating. DBox - plastic - intact New compressor ordered. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/06/2023 | 09:45 AM
09/01/2023 | Alternative | RoutineScheduled | SD-86-241 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 |  |  |  | Pump | Pressure | Trenches | Not Applicable | 600.000000 | ["None"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 12:00 AM
05/20/2023 | Alternative | RoutineScheduled | 109-18-0071 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. 0" of solids in recirculation portion of treatment unit. 8" of solids in discharge portion of treatment unit. Cleaned drip manifold spin filter. Flushed treatment unit spray manifold. Replaced passive charcoal air vent due to breakage and moss growth blocking air flow. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 07:03 PM
05/12/2023 | Alternative | RoutineScheduled | 09-173-131 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Norweco |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens","Control Operation"] | ["Control Operation","BlowerCompressorAerator Operation","Effluent Screens","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | Dec 30 1899 1:30AM
11/02/2023 | Alternative | Routine/Scheduled | 093-06-0162 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 10:15AM
05/19/2023 |  | Follow-Up | 175-06-0532 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
09/02/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  | 1000 | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
10/09/2023 | Alternative | Initial Visit | 163-STS-339544 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | Advantex AX20 |  | Gravity | Pressure | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/12/2023 | 08:45 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/27/2023 |  |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1530 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | repaired discharge alarm float replaced valve box | This AOSS should now return to normal function after having provided the above state routine maintenance | 07/06/2023 | 08:40 AM
10/10/2023 | Alternative | Routine/Scheduled | 145-STS-259769 | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/10/2023 | Dec 30 1899 11:37AM
09/18/2023 | Alternative | Routine/Scheduled | 085-STS-31746 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly -Media Sheets: Cleaned media sheets. Checked and confirmed spray pattern is good -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 4:05PM
02/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | LPD lines need cleaning. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/30/2023 | 10:30 AM
03/09/2023 |  | RoutineScheduled | 177-06-0671-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
11/14/2023 | Alternative | RoutineScheduled | 16-113-061 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 12 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/14/2023 | 12:00 AM
10/10/2023 | Alternative | RoutineScheduled | 125-STS-31602 | Nelson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Aqua Safe | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was cleaned. The treatment unit was in good operating condition. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 12:10 PM
10/27/2023 | Alternative | RoutineScheduled Component Maintenance | 154-03-1015 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
09/13/2023 | Alternative |  | 051-STS-17493 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 09/13/2023 |  | 9.900000 |  |  | 5.600000 |  |  | Will be sent separately |  | BOD: 9.90 TSS: 5.60 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
02/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [17 empty] | Septic-6"sludge 0"scum/ Pump Tank-3"sludge/ No pump out needed at this time/ Recirc. pump intake cleaned and EZ-Treat media in good condition/ Recirculation pump timer settings: On-2m Off-10m/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/13/2023 | Alternative | RoutineScheduled | 07-113-163 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/13/2023 | 12:00 AM
08/03/2023 | Alternative | Reportable Incident | S 093-19-0089 | Isle of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Environmental Services of Virginia | 1942001182 | Steve | Haley | 1.000000 |  | S/T+NC3T+D/F Pad |  | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/03/2023 | 12:00 AM
01/16/2023 | Alternative | RoutineScheduled | 115-12-0224 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank | Advantex AX20RT | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-2" scum layer and 6" Sludge in Septic tank. 8" Sludge in Recirc tank, 14" sludge in Discharge zone. Media looks ok, smells ok/normal. some residual sign of high chemical ussage but much improved since pumping the system last year. Reccomend to renters not to use any non approved cleaning chemicals, toilet chemicals, bleach, Quat ammonia or sanitizers in the system. Cleaned the effluent filter it was clogged. Ran in test mode. System fully opperational at this time. System has active monitoring attached | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 05:30 PM
06/23/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0167-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/10/2023 | 10:02 AM
04/10/2023 |  | Initial Visit | 177-STS-92238 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Start-up inspection. Recirc float switches initially not registering in control panel. Traced problem to a loose connection on the terminal strip (by installer's electrician) for the float common. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
01/04/2023 |  |  | 133 06 0436 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss | [9 empty] | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 01/04/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:40 AM
10/25/2023 | Alternative | Follow-Up | 151-13-0172 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced control panel, uv panel and bulb, rebuilt pump head works, flushed DF LPD lines, regraded top of sand mound (removed cover soil, added 2" pea gravel & geotextile, replaced cover soil). Pumped out all tanks. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/17/2023 | Alternative | Routine/Scheduled | 800-12-0020 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A |  |  | 7.000000 | 3.000000 | [13 empty] | Replaced diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Dec 30 1899 10:03AM
10/27/2023 | Alternative | RoutineScheduled Component Maintenance | VAG401688 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
03/22/2023 | Alternative | Routine/Scheduled | 06-160-0401 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | 11:00 AM
08/11/2023 | Alternative | Reportable Incident Component Maintenance | 047-STS-21307 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | None | [14 empty] | Will be sent separately | Inspected | Atu alarm. Replaced blown diaphragms for air pump and replaced dirty air filter. Verified good aeration in atu tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance | 099-14-0004-SR | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The third, fourth and fifth Puraflo modules are holding water and the drainage pipes are likely clogged. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | 08:44 AM
07/07/2023 | Alternative |  | 033-18-0084-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
03/21/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Drip tubing needs repairing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | Jan 1 1900 7:20PM
01/17/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | Jan 1 1900 11:08AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
02/27/2023 |  | RoutineScheduled | 05-125-081 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/27/2023 | 12:00 AM
08/29/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Microfast |  | Pump | Pressure | Drip |  | 150.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/13/2023 | 10:51 AM
12/22/2023 | Alternative |  | 132-14-0068 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Tasha & Clint | Birckhead | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled | 11-142-0296 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/31/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/07/2023 |  | RoutineScheduled | 2014-143-0185 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  |  | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 12:00 AM
03/15/2023 | Alternative | Routine/Scheduled | 136-04-139 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 300.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump tank - float sensors, pump and controls operating. BioFilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 09:00 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-04-0589 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Media Cleaner added due to sludge on filter visible | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
02/20/2023 |  | RoutineScheduled | 2126-09-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | UV | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | YES | Musty | Clear | 7.800000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/22/2023 | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled | 171-09-0179 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","Attached Growth Medium"] | ["Control Operation","Attached Growth Medium"] | NA | [16 empty] | Inspected | New circuit board has about 3 hours on it since installed. Hour/min/sec meter reading 3:09:49 Doses 189 , Replaced tipping tray, Added peat one bag, will bring back more next time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 09:30 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 107-04-0489 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 10/11/2023 |  | 22.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
07/24/2023 | Alternative | Routine/Scheduled | 234-14-417 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | Dec 30 1899 10:00AM
08/11/2023 | Alternative | Routine/Scheduled | 179-18-0053 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 50.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 06:51 PM
05/17/2023 |  | Routine/Scheduled | 234-14-31 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Jan 1 1900 9:10AM
05/23/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-333615 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 4.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 09/11/2023 |  | 124.000000 | [5 empty] | Will be sent separately | Inspected | Zones 3-8 saturated in field PT2 and microfast tanks full no aeration due to drainfield not able to take flow Supply and return line gauges installed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/13/2023 | 01:07 PM
09/07/2023 | Alternative | RoutineScheduled | 05-165-0305 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1250 | MIRCROFAST |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 5-6" FROM BOTTOM, 1" FROM TOP EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 10:30 AM
06/09/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/04/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | Dec 30 1899 1:05PM
01/30/2023 |  | RoutineScheduled | 179-07-0234-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. System doing well since both tanks and pump were replaced 6-8-22. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
11/28/2023 | Alternative | RoutineScheduled | 1998-143-0123 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Puraflo |  | Pump | Pressure | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
01/11/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2023 | 12:00 AM
06/17/2023 | Alternative | RoutineScheduled | 133 05 1174 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned recirculation pump solids basket filter. Flushed treatment unit spray manifold. 10" of solids in discharge pump tank. Tested floats, pumps and alarm. May need a pump out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 07:03 PM
11/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | ["None"] | ["None"] | NO | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | Dec 30 1899 12:35AM
12/05/2023 | Alternative | RoutineScheduled Component Maintenance | 2032-96-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 7.200000 | 23.900000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 12/18/2023 | 08:36 AM
12/02/2023 | Alternative | RoutineScheduled | 067-STS-39120 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | NA | [17 empty] | Annual inspection. Adjusted recirculation pump timers , recirculation pump flow rate and float switch levels per the manufacturer's updated service memorandum. This system fell into a specific serial number range that required the adjustments to avoid high levels in the recirculation tank. 12" of accumulated solids in septic tank. 10" of solids in the recirculation portion of the treatment unit. 10" of solids in the discharge portion of the treatment unit. Flushed treatment unit spray manifold. Cleaned septic tank solids filter. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/22/2024 | 07:03 PM
05/23/2023 |  |  | SP-05-99 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0086-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 1.49 amps. Treatment looks good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
02/02/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/07/2023 | Alternative | Routine/Scheduled | 2011-143-0047 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/07/2023 | 01:02 PM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0032-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/09/2023 |  |  | 06-142-0215 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Pumped Out | Replaced bad pump with L280. Pumped 1000 gallon from Ecoflo tank and pump pit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/05/2023 | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Media ponding would recommend upgrading to new media Replaced motherboard due to bad alarm output | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
07/25/2023 | Alternative |  | 12-195-224-DIS | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/25/2023 |  | 5.810000 |  |  | 2.300000 |  |  | Will be sent separately |  | BOD: 5.81 TSS: 2.30 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/25/2023 | 12:00 AM
02/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-4"sludge 0"scum/ Microfast-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly, Odor and color normal in the Microfast unit / Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-440 ETM-23h 35m/ Pump2-430 ETM-23h 2m/ Peak-4/ High-7/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:00 AM
03/29/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 3 bottom pods are holding effluent. Need to investigate if drainpipe has settled. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
02/07/2023 |  | RoutineScheduled | 03-197-179 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 12:00 AM
04/21/2023 | Alternative | RoutineScheduled | 005-STS-42701 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The recirculating pump was pulled and sprayed off. The textile sheets were sprayed off. The pressure was adjusted on the treatment unit. The timers were adjusted for the number of occupants living in the house. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | Jan 1 1900 9:00PM
09/12/2023 | Alternative | Routine/Scheduled | 11-120-0245A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/12/2023 | Dec 30 1899 10:02AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-01-113 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
12/29/2023 | Alternative | Reportable Incident | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Ecopod to American drip. Customer said alarm went of yesterday. Found the timer enable and override floats were intermittently failing. Customer approved to replace all four instead of just the two. After replacing floats we confirmed everything is working and the pump is moving water, pulled and cleaned the disc filter while on site | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | Dec 30 1899 9:59AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
12/27/2023 | Alternative | Routine/Scheduled | 136-05-0852 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component High level upon arrival due to breaker being off 1 in of sludge less than 1 in of solids Pulled and cleaned filter No signs of infiltration Discharge/Pump Tank Pump chamber Condition of above Component Notes for above Component High level upon arrival due to breaker being off Floats are faulty and wiring is corroded All plumbing intact and pump moving water properly No signs of infiltration Peat Moss Condition of above Component Notes for above Component Tipping bucket and dispersal trays intact Peat moss broken down with heavy root intrusion No standing water Raked peat moss Module intact Control Panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Pump pulled 8.34 Wires are faulty in panel Drain Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 08:33 AM
05/18/2023 |  | Routine/Scheduled | 11-142-0178 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Air filter cleaned. Weir cleaned. Scum layer stirred. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 10:23AM
08/28/2023 | Alternative |  | 003-STS-33831 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Ron & Joan | Kluck | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/14/2023 | Alternative | Routine/Scheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 01:30 PM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Element for blower canister filter replaced and air pre-filter cleaned as a matter of preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
11/24/2023 | Alternative | Reportable Incident | 196-06-415 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Puraflow. Jacob had replaced the discharge pump to a bigger pump to move water. Everything is now at normal level and working properly. Customer maybe wants to look back into the Peat replacement next spring | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 09:41 AM
08/02/2023 | Alternative |  | 03-125-273 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/02/2023 |  | 6.750000 |  |  | 9.600000 |  |  | Will be sent separately |  | BOD: 6.75 TSS: 9.60 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/02/2023 | 12:00 AM
05/03/2023 |  | Routine/Scheduled | 11-120-0116ACR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Microfast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/03/2023 | Jan 1 1900 10:14AM
02/13/2023 |  | RoutineScheduled | 179-16-0130-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Alarm call by owner and annual inspection. Installed new timer float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
10/18/2023 | Alternative | Follow-Up | 093-STS-15037 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 10/18/2023 |  | 4.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | Dec 30 1899 1:00PM
07/05/2023 | Alternative |  | 03-120-0556A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3250 | 1250 | 1000 | Pump | Gravity | Discharge | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | Pungent | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 2133-10-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Whitewater ATU | none | Pump | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 12/01/2023 | 10:33 AM
07/05/2023 | Alternative | Reportable Incident | 103-STS-95844 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Force main deflected in d-box. Resealed pipe in d-box | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/25/2023 |  | RoutineScheduled | 033-STS-89277 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/22/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
08/09/2023 | Alternative | Routine/Scheduled | 06-120-0167A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Microfast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/09/2023 | Dec 30 1899 10:41AM
10/18/2023 | Alternative | RoutineScheduled | 061-17-397 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Advantex | Pump | Pressure | Drip |  |  | [] | ["Control Operation","Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","Recirculation Pump"] | [18 empty] | 0 scum, 6" of sludge. 4.5' overall. alarms, floats, pumps all working. one spinner was missing. fixed. field dry. recic 1925.5h, 42474 discharge, 478.6 hr, 6322 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2024 | 10:30 AM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
03/06/2023 |  | RoutineScheduled | 179-08-0261-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The Advantex pod vent cap should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
07/14/2023 | Alternative | RoutineScheduled | 07-120-0365 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | Pungent | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/28/2023 | Alternative | RoutineScheduled | 15-125-100 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Level Sensor Operation"] | NA | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/28/2023 | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.800000 | [14 empty] | Pump is not operational. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/15/2023 | 12:15 PM
03/10/2023 | Alternative | Routine/Scheduled | 136-06-0001 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 10:00 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/13/2023 |  | RoutineScheduled | 175-04-0402 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
08/23/2023 | Alternative | Pump-Out Only |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumpout of septic tank and aeration tank as recommended during last service visit. Aeration tank refilled with fresh water for re-start. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 09:00 AM
07/25/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 12:00 AM
11/24/2023 | Alternative | RoutineScheduled | SD-05-30 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | Puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 09:00 AM
05/16/2023 | Alternative | RoutineScheduled | SD-05-187 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 36.000000 | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 03:40 PM
11/01/2023 | Alternative | Routine/Scheduled | 01-120-0771A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Just above the Inlet tee Has 1" of solids with 4" of sludge Pulled and cleaned rsv -Recirculation Tank: Found the timer enable float was 2" off the alarm float which is the reason for the random alarms. I lowered the timer enable float to 14" above the low level and pumped the tank down. The level is now below the tee. Tank has 10" of sludge Pulled and cleaned the pump, floats and filter -Discharge/Pump Tank: At normal level Pump and floats working Riser is leaking Has buried splice box -Media Sheets: The sheets are stuck together and ponding water, customer approved sheet replacement Lid has no locking strut -Control Panel: Panel working properly Recirc pump pulling 12amps Discharge pulling 5.29amps Visual and audible alarms working -Distribution Box: Box is at grade At normal level No signs of cracking or deterioration -Drain Field: Showing no signs of surfacing Repairs for 11/07: Advantex Engineered Textile Media Filter Replacement in Treatment unit: Removal & disposal of existing Engineered Textile Media Filters Installation of new Engineered Textile Media Filters Includes installation of new Bars & Hangers | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/02/2023 | Dec 30 1899 10:33AM
08/28/2023 | Alternative | RoutineScheduled | 167-STS-16735 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/28/2023 | 12:00 AM
11/07/2023 | Alternative | Reportable Incident Component Maintenance | 179-17-0442-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed override float and high level float in recirc tank. Replaced both floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
02/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator control panel was replaced and the system appears to be functioning as designed at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/12/2023 | Alternative | RoutineScheduled | 163-STS-337956 | Rockbridge | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Discharge | Chlorination |  | ["None","BlowerCompressorAerator Operation"] | ["None","BlowerCompressorAerator Operation"] | NA | None | [16 empty] | The system did not need to be pumped. The blower filter was cleaned. The controls were operating as designed. The system did not have a discharge at time of visit so a sample draw could not be performed. The evaporation bed was full so it was operating as designed. The tablet feeders did not need tablets. The post air pump had gone bad to it was replaced the same day of the inspection. The lids were secured. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 06/06/2023 | 10:05 PM
10/01/2023 | Alternative | Routine/Scheduled | 041-STS-260920 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1000 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/01/2023 | Dec 30 1899 11:00AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
04/10/2023 |  | RoutineScheduled | 175-04-0373 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
08/28/2023 | Alternative | Routine/Scheduled |  | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level - minor root intrusion noted. Aeration Tank - normal level - mixing present - compressor serviced. U.V. disinfection - Unknown - technicians did not make note of service. Pump Tank - float sensors, pump and controls operating. Drip headworks - UNKNOWN - technicians did not make note of service. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/31/2023 | 07:15 AM
11/28/2023 | Alternative | RoutineScheduled | 109-STS-29486 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | eco flo |  | Pump | Pressure | Drip |  |  | ["None"] | ["None"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 11:30 AM
05/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | UV |  | ["Effluent Screens" ,"Auxiliary Filter" ,"Disinfection"] | ["Effluent Screens" ,"Disinfection" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
04/17/2023 |  | Routine/Scheduled | 234-13-191 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 12:15PM
07/18/2023 | Alternative | RoutineScheduled | SD-02-323 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | Advantex | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 08:20 AM
05/16/2023 | Alternative | RoutineScheduled | SD-05-140 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 33.900000 | ["Effluent Screens","Control Operation","Attached Growth Medium"] | ["SludgeScum Accumulation","Effluent Screens","Control Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 03:15 PM
04/13/2023 |  | Routine/Scheduled | 133 16 0227 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 11:30 AM
07/31/2023 | Alternative | RoutineScheduled | 166-12-181 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned atu and spin filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/27/2023 | Alternative | RoutineScheduled | 03-160-0158 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | ["Dispersal System Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/07/2023 |  | Routine/Scheduled | 550-STS-6394 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the UV light bulb. Changed the filter in the aerator and changed the mesh screen in the spinfilter. Raised the aerator. The timer is set to 6 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | Jan 1 1900 12:00PM
04/24/2023 | Alternative | RoutineScheduled | 107-07-0586 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["None","Other"] | ["None","Other"] | NO | Musty | Clear | [15 empty] | second opinion | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
12/05/2023 | Alternative | Follow-Up | 08-142-0324 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 2.000000 | 2500 | BioMicrobics MicroFast |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Auxiliary Filter"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Septic | Clear |  |  | 5.000000 | [12 empty] | Initial visit 11-22-2023 found tank in high level, no alarm. Pump not functioning. Wiring in splice box corroded, cleaned wiring for pump, pump ran. Tested floats, high level float not working, bloated cord at bulb. Ring compressor not running, had effluent leaking at flange. Compressor motor locked up. Returned 12-5-2023 to replace ring compressor, replace alarm float, service pump screen and filter, check solids levels. Pump, floats, controls, compressor all functioning properly now. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/05/2023 | Dec 30 1899 8:40PM
06/21/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
03/03/2023 |  | RoutineScheduled | 177-09-0062-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There are roots growing into the Puraflo modules. At some point in the future, this may make it difficult to service the peat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/07/2023 | Alternative |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:00 PM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | 107-09-0255 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend removing trees near drainfield Homeowner has agreed to pumping all tanks to be done soon | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
01/18/2023 | Alternative | RoutineScheduled | SD-06-30 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Battlefield Soil And Septic LLC | 1942001084 | Josh | Johnston | 2.000000 | 3000 | 1500 gal septic tank | Puraflo Modules | Pump | Pressure | Trenches | Not Applicable | 500.000000 | [] | ["Control Operation","Effluent Screens"] | YES | Musty | Discolored | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/30/2023 | 08:25 AM
05/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/20/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS repaired air release valve and cleaned Advantex spray heads. Effluent pump had failed. The system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower failed. New blower was installed and appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Notice that garden is on drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:17 AM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
03/24/2023 |  | RoutineScheduled | 04-183-280 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Level Sensor Operation"] | ["Septic Tank Baffles","Level Sensor Operation","Distribution Pump Operation","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/24/2023 | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator was not functioning | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
01/03/2023 |  | RoutineScheduled | 177-08-0034 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/26/2023 | Alternative | Reportable Incident | 159-07-229 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Owner reports system has been alarming for 2+ weeks, but NO problem in the home. - Last documented service by Millers Services was 2019! Trash Tank - normal level - recommend pumpout. Aeration Tank - normal level - NO MIXING PRESENT - Compressor extremely hot to the touch - operating, pulling 3+ amps. Pump Tank - float sensors, pump and controls operating. DBox - intact - all laterals accepting effluent. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/27/2023 | 08:15 AM
10/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | [17 empty] | Septic Tank-12"sludge 6"scum/ Microfast-14"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Pump out needed at this time on the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-334 ETM-24h 38h/ Pump2-326 ETM-24h 19m On-4m 35s Off-12h/ Peak-10/ High-9/ No breakout or spongy areas on the LPD Pad area and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled | 08-113-200 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/18/2023 | 12:00 AM
06/15/2023 | Alternative | RoutineScheduled | 107-18-0238 | Augusta | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter | [9 empty] | ["Dispersal System Operation","Effluent Screens"] | ["Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | leak in dripline repaired | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/06/2023 | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0114 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Effluent Screens" ,"Control Operation" ,"Disinfection"] | ["Effluent Screens" ,"Control Operation" ,"Disinfection"] | YES | Musty | Clear | 7.700000 | 8.700000 | [11 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
10/26/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | [] |  |  |  | 8.370000 | 0.340000 | 50.000000 |  |  | 10/11/2023 |  | 175.000000 |  |  | 55.000000 | 132.700000 |  |  |  | Flow meter is not operational, however, flow exceeds permit. We believe the high results are due to the excessive flow. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/06/2023 | 06:15 PM
10/18/2023 | Alternative | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 3175.000000 | [] | [] |  |  |  | 7.610000 | 4.860000 | 24.000000 |  |  | 10/11/2023 |  | 24.000000 |  |  | 7.600000 | 26.480000 |  |  |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 06:10 PM
07/14/2023 | Alternative |  | 033-STS-89023 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
12/12/2023 | Alternative |  | 125-STS-29522 | Nelson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/15/2024 | 12:00 AM
01/30/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 12:27 PM
07/19/2023 | Alternative | Routine/Scheduled | 157-01-116 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Rotuine Service with pumpout. Primary septic tank - pumped empty and serviced. Aeration Tank - pumped empty, compressor serviced - refilled with fresh water for re-start. Pump Tank - pumped empty - serviced - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 06:15 AM
09/19/2023 | Alternative | Routine/Scheduled | 08-160-0123 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 97.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 04:00 PM
09/08/2023 | Alternative | Routine/Scheduled | 234-18-156 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 8:00AM
12/29/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1000 | Anua/Puraflo |  | Pump | Pressure | Trenches | Not Applicable | 50.000000 | ["Attached Growth Medium","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Effluent Screens","Dispersal System Operation","Control Operation","Attached Growth Medium"] | YES | Musty | Clear | [15 empty] | Peat moss was replaced. Tanks pumped, timers, and floats were adjusted accordingly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/29/2023 | 07:00 PM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/27/2023 | Alternative | RoutineScheduled | VAG408475 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  |  | Discharge | Chlorination |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/09/2024 | 12:00 AM
11/07/2023 | Alternative | Routine/Scheduled | 085-STS-34776 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level high upon arrival due to clogged effluent screen. Flushed and cleaned effluent screen and water level returned to normal. Not due for pump out -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. -Media Sheets: Cleaned media sheets. Checked and confirmed spray pattern is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 11:41AM
12/20/2023 | Alternative | RoutineScheduled | 115-10-0091 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 4.000000 | 8000 | Septic Tank | Advantex | Gravity | Gravity | Trenches | Not Applicable | 3600.000000 | ["Effluent Screens"] | ["Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 01:30 PM
05/01/2023 |  | Reportable Incident | 179-07-0241-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Repeat high level alarms. Control panel has override function that activates pump while the high level float is activated. Owner finally cut off the pump switch to stop the audible alarms. The high level alarm float and timer float were tested and found to be stuck on, replaced both. Effluent flowed continuously into the pump tank throughout the duration of the repair. Owners advised to check all toilets, especially the one known to be problematic. Peat and drainfield not inspected today. Two years ago, pods were observed overflowing and drainfield had trees that needed to be removed. Peat needs replaced but a "road" will need to be built to access the pods. Waiting on approval from the owners. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/05/2023 | 07:56 AM
04/28/2023 |  | Initial Visit | VAG408071 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | Constructed Wetlands |  | Gravity | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] |  | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/05/2023 |  | RoutineScheduled | 179-STS-89380 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 4"scum/ Microfast-2"sludge / Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Cleaned Blower air filter and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-266 ETM-13h 12m On-3m 2s Off-12h/ High cnts-5/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/16/2023 |  | Initial Visit | 165-STS-337232 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | EZ Treat |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","Distribution Pump Operation","Dispersal System Operation"] | ["Auxiliary Filter","Distribution Pump Operation","Dispersal System Operation"] | [18 empty] | Reattach floats | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 12:00 AM
04/13/2023 |  | Routine/Scheduled | 067-STS-38057 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:15 PM
10/02/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-23956 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 5.000000 |  | 0.000000 | [11 empty] | Aerator running, no odor, both tablets stocked. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/03/2023 | 12:00 AM
06/02/2023 | Alternative | RoutineScheduled | 154-06-0720 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Pura Flo 5 mod |  | Gravity | Gravity | Trenches |  | 150.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 11:25 AM
10/02/2023 | Alternative | RoutineScheduled | 02-197-A9 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/03/2023 | 12:00 AM
08/31/2023 | Alternative | Reportable Incident |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - Repair - found RSV damaged and required replacing - Processing tank pumped empty to conduct repair. Replaced damaged RSV on outside and inside of riser access. Refilled treatment system with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 11:30 AM
03/29/2023 |  | Routine/Scheduled |  | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Advanced Septic |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 05:33 PM
09/22/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0389-SWT | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Outstanding proposal for replacing risers on both tanks and installing correct lids. Roots into drainfield line closer to tree line, starting to Come into D-box. Recommended to add root x but customer said they will do them selves. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
05/24/2023 |  | Initial Visit | 085-STS-34999 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 600.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial visit - System Commissioning. Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - adjusted recirc flow, adjusted spray grid. U.V. - verified bulb functioning - set amperage tolerances. Processing Tank - discharge - adjusted settings - verified controls and pump functioning. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Jan 1 1900 11:30AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Force main needs repair & floats need replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/07/2023 | Dec 30 1899 6:39AM
01/07/2023 | Alternative | RoutineScheduled | SD-15-146 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | Trash | Microfast | Gravity | Pressure | Drip | UV |  | [] | [] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 03:30 PM
07/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | Septic Tank-12"sludge 6"scum/ Microfast-14"sludge /Pump Tank-2"sludge/ Septic - Microfast Tank may need pump out by next year/ Blower air filter cleaned and blower working correctly/ UV-Light sleeve cleaned and light functioning properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-6222 ETM-124h 32m/ Peak-24 ETM-400h 49m/ High-25/ Watermeter-0,408,655.27/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/17/2023 | Alternative | Reportable Incident | LEGACY | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Found system for the Oakwood lodge in high level and alarming. Both pumps were running and pulling 10amps but not moving water. After doing some exploring I found a gate valve at the head of the drainfield that is marked with an orange road cone. I opened it up all the way and turned the pumps on, water is now moving freely. I pumped the system back to normal level and informed Rich about what I found and about the recommend options. He has to speak with a couple people for approval of any estimates. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 10:07AM
05/02/2023 | Alternative | Routine/Scheduled | 093-03-0270 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Dec 30 1899 9:50AM
01/04/2023 |  | RoutineScheduled | 175-00-0086 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/24/2023 | 08:34 AM
08/10/2023 | Alternative | RoutineScheduled | 171-10-0206 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1000 | Advantex | none | Pump | Pressure | Trenches | Not Applicable | 300.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/21/2023 | 03:00 PM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The system appears to be functioning as designed at this time. The field is slightly overgrown and difficult to tell that is going on. No surfacing effluent was observed. There appears to possibly have been vehicles driven on or near the drainfield. This is strongly discouraged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/26/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1500 | Advantex |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Distribution Pump Operation","Effluent Screens"] | ["Control Operation","Distribution Pump Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | The system is operating as intended and in general conformance with the health department regulations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | 05:00 PM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 2.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Disinfection" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [7 empty] | 3.000000 |  | 5.200000 | 2.800000 |  |  | Will be sent separately | Inspected | DO Test Results - 7.09 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
05/20/2023 | Alternative | RoutineScheduled | 03-100-0189 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad |  | 600.000000 | [] | [] | [18 empty] | PEAT LOOKS GOOD. EVERYTHING WORKING GREAT. CLEANED EFFLUENT FILTER. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/31/2023 | 01:25 PM
06/30/2023 | Alternative | Routine/Scheduled | 234-16-286 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 8:55AM
01/04/2023 |  | Routine/Scheduled | 228-03-0217 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | Jan 1 1900 11:50AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/14/2023 |  | RoutineScheduled | 043180038 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 10:25 AM
03/31/2023 | Alternative | Routine/Scheduled | 2008-126-199 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Dec 30 1899 2:07PM
04/05/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | 03:22 PM
12/22/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87214 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | UV |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"Disinfection"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | New EZ Treat Pump was installed. We also recommend installing a new EZ Treat UV Bulb, cord, and quartz sleeve as the current UV bulb is not working. 2/21/24: Per email from Ed Scott to MWebb: "We provided a quote for a new EZ Treat bulb, cord and quartz sleeve on 12/22/2023. No response to date. Owners did replace a pump in December, so expense may be a factor." | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/02/2024 | 11:12 AM
10/30/2023 | Alternative | RoutineScheduled | 175-15-0037 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-2"sludge 0"scum/ Microfast ATU Tank-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-002917 ETM-0017825 hrs On-4m 12s Off-11h 55m/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/14/2023 | Alternative | Routine/Scheduled | 150-17-0044 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level - noted Fracture on outlet side of tank - does not appear to be fully through the tank. Aeration Tank - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 07:00 AM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20216 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/30/2024 | 01:28 PM
05/10/2023 |  |  | SP-05-688 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
01/19/2023 |  | RoutineScheduled | 179-11-0062-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/28/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Air line between blower and Microfast needs to be excavated to determine if there is break or blockage. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | Jan 1 1900 7:20PM
12/18/2023 | Alternative | RoutineScheduled | 182-03-0361 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
09/08/2023 | Alternative | RoutineScheduled | 132-06-0274 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Mound | Not Applicable | 150.000000 | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 11:45 AM
08/29/2023 | Alternative | RoutineScheduled | 085-STS-33678 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1000 | Purasys PS1-6 |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled | 17-195-160-SP | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Recirculation Pump","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | 12:00 AM
03/29/2023 |  | RoutineScheduled | 09-192-191 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
11/15/2023 | Alternative | RoutineScheduled | 19-163-0037 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/14/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20291 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity |  | Not Applicable |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 12/20/2023 | 02:30 PM
07/19/2023 | Alternative | RoutineScheduled | 2017-143-0179 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | EZ treat | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 09/19/2023 | Sample Chamber | 34.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/19/2023 | Alternative | RoutineScheduled | 107-17-0075 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  |  | Trenches | Not Applicable |  | ["Septic Tank Baffles","Recirculation Pump"] | ["Septic Tank Baffles","Recirculation Pump"] | [18 empty] | recirc pump washed/cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
03/16/2023 |  | RoutineScheduled | SWP-05-256 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Peat moss has very little fiver left, is very low and has alot of roots. We fluffed it very good with shave and pitch forks to get it work for 1 more year but it should be replaced next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
05/18/2023 | Alternative | Routine/Scheduled | 151-06-0420 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | 04:53 PM
09/20/2023 | Alternative | Reportable Incident | 06-120-0178A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Septic Pro of Virginia | 1942001780 | Eric | Tambourine | 1.000000 | 1500 | Advantex AX-20 |  | Pump | Gravity | Trenches | Not Applicable | 360.000000 | ["Attached Growth Medium","Other"] | ["Attached Growth Medium","Other"] | NO | Pungent | Discolored | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/25/2023 | Dec 30 1899 12:20PM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
07/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87861 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 4.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Pungent | Clear | [5 empty] | 07/17/2023 |  | 41.000000 |  |  | 41.000000 |  |  | Will be sent separately | Inspected | Routine inspection. Sample taken. Bad R.O float for discharge tank, replaced. Influent results: BOD5=600 mg/l, TSS= 121 mg/l, HEM 57.2. Effluent results: BOD5=41 mg/l, TSS=41 mg/l, HEM=11.7, results failed but have improved compared to past samplings. System is running to it's max capacity. Manager should continue to look for ways to reduce water usage. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
07/28/2023 | Alternative | Routine/Scheduled | 09-160-0031 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 15.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | 10:15 AM
06/02/2023 |  |  |  | Caroline | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/23/2023 | 12:00 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired air supply and pressure gauge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
07/31/2023 | Alternative | RoutineScheduled |  | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 12:00 AM
05/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["Disinfection" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-01-575 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["Distribution Pump Operation" ,"Dispersal System Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The headworks box has settled and the zone solenoids are pushing against the lid. We recommend excavating by hand and releveling the headworks box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Hydro-Action ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/20/2023 | Alternative | Routine/Scheduled | 093-05-0421 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 8:25AM
08/19/2023 | Alternative | RoutineScheduled | 019-STS-26931 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank - 1" crust, 16" of accumulated solids on bottom. The solids in the septic tank will most likely decrease as they get more dense. 0" of solids in recirculation portion of treatment unit. 0" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Cleaned septic tank solids filter. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 07:03 PM
02/04/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Adjusted recirculation pump timers slightly to allow for more flow during higher usage. 6" of solids in recirculation portion of treatment unit. 4" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 07:03 PM
10/13/2023 | Alternative | RoutineScheduled | 17-163-0145 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced failed recirc pump, system check - okay | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/13/2023 |  | RoutineScheduled | 177-STS-91864 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | UV |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The drip return line was broken next to the pump tank. The builder was notified, and the installer made the repairs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
09/28/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine Annual | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 12:00 AM
03/17/2023 |  | RoutineScheduled | 09-184-5004 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/17/2023 | 12:00 AM
02/05/2023 |  | Routine/Scheduled | 041-STS-260149 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/05/2023 | Jan 1 1900 11:00AM
06/30/2023 | Alternative | Routine/Scheduled | 087-STS-6467 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/30/2023 | 01:21 PM
05/31/2023 | Alternative | RoutineScheduled | 061-STS-21662 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/24/2023 | Alternative | RoutineScheduled | 2059-99-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | SBR |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | 7.300000 |  |  | 2.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/03/2023 | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 182-00-0549 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 10/31/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected | Replaced timer Installed remanufactured blower Replaced middle float Pumped all tanks and added inlet riser | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance | 177-14-0057-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
05/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
07/24/2023 | Alternative |  | 177-07-0247-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
05/17/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3647 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/17/2023 | Jan 1 1900 9:45AM
06/15/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Water was turned on. Serviced the Singulair Treatment unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/19/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
03/20/2023 |  | RoutineScheduled | 177-STS-91823 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Not enough water in system for fully test drip dispersal system. Did not locate air release valves. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
07/18/2023 | Alternative | Routine/Scheduled | 03-137-0330 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - recommend pumpout - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump tank - float sensors, pump and controls operating. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 11:15AM
04/18/2023 |  | Reportable Incident |  | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 4.000000 | 9000 | None | None | Pump | Pressure | Trenches | Not Applicable | 4000.000000 | ["Control Operation","Distribution Pump Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | System evaluated for pump failure - pumped pump tank empty and 1000g from septic for storage - pulled pumps to ascertain make / model. Ordered pumps. One pump operating - system is still operating on one pump, one absorption field. Proposal is to replace both pumps, manufacturer float tree and restore operation Wednesday 04/19/2023 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/19/2023 | Jan 1 1900 8:15AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
02/06/2023 |  | RoutineScheduled | 179-STS-88276 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
07/24/2023 | Alternative | Reportable Incident | 234-13-457 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/24/2023 | Dec 30 1899 8:00AM
08/28/2023 | Alternative | Pump-Out Only |  | Westmoreland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pump out of primary septic tank in preparation for a biofilter change out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/31/2023 | 06:45 AM
07/10/2023 | Alternative | RoutineScheduled | 196-16-0027 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | 12:00 AM
02/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/07/2023 | Alternative | Reportable Incident | 08-113-231 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | Samantha received letter needed service and tablets 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/07/2023 | 12:00 AM
06/28/2023 | Alternative | Routine/Scheduled | 150-05-359 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Biofilter - peatmoss in good condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | 07:45 AM
11/09/2023 | Alternative |  | 099-13-0132-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-552 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend replacing the damaged Orenco lid on the Advantex tank. We also recommend uncovering the distribution box to evaluate if water is flowing evenly to the drain field lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
01/23/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/27/2023 | 07:00 PM
07/18/2023 | Alternative | RoutineScheduled | 07-118-0039 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/23/2023 | Alternative | Initial Visit | SD-12-045 | Culpeper | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST | [6 empty] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | replaced blower | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/28/2023 | 12:00 AM
07/17/2023 | Alternative | Routine/Scheduled | 166-12-187 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Norweco Singulair ATU |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 75.000000 | [11 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 05:50 PM
04/03/2023 |  | Routine/Scheduled | 03-120-0462A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/03/2023 | Jan 1 1900 4:45PM
10/05/2023 | Alternative | RoutineScheduled | 061-17-326 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | sludge checked, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | Airline is broken. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | Dec 30 1899 2:02PM
08/04/2023 | Alternative | RoutineScheduled | 182-08-0107 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/04/2023 | 12:00 AM
09/01/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-436 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Clean treatment. Media looks good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
04/13/2023 |  | RoutineScheduled | 10-192-200 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/13/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
10/02/2023 | Alternative |  | 10-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 6.000000 |  | 0.000000 | [11 empty] | Aerator working, both tablets in place | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/06/2023 |  | RoutineScheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 | Puraflo |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Peat Moss is degraded and ponding water and needs to be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/27/2023 | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/22/2023 | 12:00 AM
10/27/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed Microfast blower, E188 effluent pump & (4) control floats. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/15/2023 | Dec 30 1899 2:02PM
11/10/2023 | Alternative | RoutineScheduled Component Maintenance | SD-07-33 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Flow rate is still very low to the d-boxes. Force main is either sludged up from slow flow, or partially air-locked. Needs further investigation. Concrete lid for Puraflo dosing tank has been replaced since last year's inspection. The tank itself, however, is in poor shape/leaks and should be replaced. Multiple spreader bars in the Puraflo pods have rotted in half (which causes unequal distribution within the pods) and need to be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
04/26/2023 | Alternative | RoutineScheduled | 133-STS-95033 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/10/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
03/22/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Added media cleaner Recommend take water softener off septic psi case | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
05/18/2023 |  | Routine/Scheduled | 550-STS-6558 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 6.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 3:14PM
07/20/2023 | Alternative | RoutineScheduled | 165-STS-337232 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | EZ Treat |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 12:00 AM
03/13/2023 |  | RoutineScheduled | 003-STS-31471 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/19/2023 | 12:00 AM
01/31/2023 |  | Follow-Up | 099-13-0097-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [7 empty] | 01/31/2023 |  | 7.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
11/20/2023 | Alternative | RoutineScheduled | 2019-143-0030 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Aqua Klear |  | Pump |  | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 12:00 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/30/2023 | Alternative | Routine/Scheduled | 18-120-0145A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2.5 minutes every 2.5 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | Dec 30 1899 12:45PM
11/20/2023 | Alternative | Routine/Scheduled | 17-120-0274A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Aeration: Water level normal. Checked and confirmed sludge return pump is functioning properly. Checked and confirmed aerator is functioning properly. Checked and confirmed discharge pump is functioning properly. Checked and confirmed floats are functioning properly. Not due for pump out -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | Dec 30 1899 3:27PM
12/01/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 01:30 PM
10/20/2023 | Alternative | RoutineScheduled | 09-100-0130 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | SLUDGE JUDGE TEST REVEALED 8-9" FROM BOTTOM, 1" FROM TOP. CLEANED NOZZLES. EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | 01:35 PM
05/15/2023 | Alternative | Reportable Incident | 157-10-0128 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | AOSS - Alarm - discharge pump fail. Replaced Zoeller pump with same make/model - replaced float sensors. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 06:30 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/24/2023 |  | Routine/Scheduled |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 7:30AM
02/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/14/2023 | Dec 30 1899 5:31AM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance | 107-04-0710 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | [7 empty] | 09/05/2023 |  | 15.000000 | [5 empty] | Will be sent separately | Inspected | new timer, buzzer, visual alarm contacter and effluent pump fixed leak | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
06/07/2023 | Alternative | Pump-Out Only | 043-10-0050 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | 11:50 AM
04/21/2023 | Alternative | RoutineScheduled | 115-05-0407 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | YES | [16 empty] | Inspected | Returned to repair float wiring issue, found the float wirenuts were burns and blackened, possibly due to water shorting them out and one wire was burned up. Re cut wire and replaced wire nuts. Alarm functional and pumps operational. RTU 140402 - Ran in Test mode- Good Spray pattern - Recirc pump 1030 time and 76296 cycles, Discharge pump 76.4hours and 2275 cycles. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/30/2023 | 09:30 AM
08/07/2023 | Alternative | Routine/Scheduled | 05-174-0017 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Gravity | Gravity | Trenches |  |  | ["Attached Growth Medium","Auxiliary Filter","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/07/2023 | Dec 30 1899 10:58AM
03/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 | 1500 | 1200 | Pump | Gravity | Drip | UV | 450.000000 | ["BlowerCompressorAerator Operation","Other"] | ["BlowerCompressorAerator Operation","Other"] | NA |  |  | 7.890000 | 7.000000 |  |  |  | 03/28/2023 | Sample Chamber | 41.000000 |  | 248.100000 | 3.200000 |  |  | Attached to this report | Pumped Out | Jan 23, 23- Blower was not working- Replace Blower/ Replace Sprayer Pump/ Replace Sample Box Air Pump/ Cleaned all tanks, Kept pumped down until parts came in/ and installed- | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Dec 30 1899 11:05AM
03/22/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/23/2023 | 01:49 PM
07/18/2023 | Alternative | Pump-Out Only | 121-STS-12420 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | - this is a LPD system - septic tank is cracked, but still holding water at this time - cleaned filter onsite - system was inspected by King and Sons several months ago, sending copy of our maintenance agreement to customer | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/20/2023 | 12:00 AM
12/29/2023 | Alternative | Routine/Scheduled | 119-STS-94264 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Completed maintenance and inspection Panel was in alarm due to bad alarm float. Gave customer estimates over the phone. Customer approved gold option. We installed alarm float on site. Need to return to complete remain repairs/upgrades. Septic Tank Condition of above Component Notes for above Component Normal level 1 in of sludge less than 1 in of solids Pulled and cleaned filter No signs of infiltration Discharge/Pump Tank Condition of above Component Notes for above Component Normal level Panel in alarm upon arrival due to bad alarm float Replaced alarm float on site All other floats functional All plumbing intact and pump moving water properly No signs of infiltration Control Panel Condition of above Component Notes for above Component In alarm upon arrival due to bad float (replaced alarm float) 120 volts coming in All visual and audible alarms functional All components working as should LPD Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 09:57 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Disinfection" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | 7.100000 | 25.900000 |  | 0.000000 | [9 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 09/15/2023 | Dec 30 1899 2:41PM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
11/02/2023 | Alternative | RoutineScheduled | 10-192-121 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/02/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled |  | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [9 empty] | 2.000000 | [5 empty] | Will be sent separately | Inspected | Control panel breaker was tripped and corrected Lab results normal | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
03/13/2023 |  | RoutineScheduled | 175-09-0212 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Needs new airline for compressor. Yard boxes have been damaged by lawn equipment. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | 07:20 PM
07/24/2023 | Alternative | Reportable Incident | 234-16-134 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/24/2023 | Dec 30 1899 9:00AM
11/01/2023 | Alternative | Reportable Incident | 151-03-195 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: Came out for an alarm call Customer stated alarm was goin off arrived on site to bad alarm float Quoted for new on/off and alarm floats Customer approved on site Replaced both floats | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 10:19 AM
03/14/2023 |  | Routine/Scheduled | 18-142-0387 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Treatment Module - recirc - recirc pump, media drapes & spray grid serviced. Treatment Module - discharge - float sensors, pump and controls operating. Pumps to community absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Jan 1 1900 9:30AM
11/20/2023 | Alternative |  | 04-183-348 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/20/2023 |  | 2.720000 |  |  | 2.600000 |  |  | Will be sent separately |  | BOD: 2.72 TSS: 2.60 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/20/2023 | 12:00 AM
01/31/2023 |  | RoutineScheduled | 113-16-062 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [8 empty] | 1926.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 12:00 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 107-07-0681 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
09/13/2023 | Alternative | Routine/Scheduled | 115-STS-97332 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal level Less than 1in of sludge and solids No signs of infiltration -Recirculation Tank: Normal Level Less than 1in of suspended solids Pulled and cleaned biotube filter Pulled and cleaned pump Pulled and tested floats all working properly No signs of infiltration -RSV: Pulled and flushed rsv -Discharge/Pump Tank: Normal Level Less than 1in of suspended solids Pulled and cleaned filter Pulled and cleaned pump Pulled and tested floats all functioning properly No signs of infiltration -Media Sheets: Flushed and brushed laterals Cleaned media sheets Flushed media module until water ran clear -Control Panel: 120 volts coming in Discharge pump pulled 9.2 amps Recirc pump pulled 11 amps All audible and visual alarms functioning properly -Drip Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 02:54 PM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0018-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Found filter out side housing and signs of high water level due to grease and trash clogging up filter, spoke to customer about Do's and don'ts. Pump tank needs pump out due to sludge levels and trash floating around. Peat is on its last year will need replacement next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
01/23/2023 | Alternative | Routine/Scheduled | 166-05-398 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 07:01 PM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 107-12-0281 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
06/21/2023 |  | RoutineScheduled | 015-STS-336911 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | Advantex RT |  | Gravity | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 03:50 PM
05/26/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 | 1500 Septic w Fast & 1250 pump | Septic | Fast | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | Little scum & 4" of sludge. Pump tank clean. Alarms, pump ,floats good. Field dry Filters cleaned. 378 Cycles & 40 hrs, 47min run time. BOD sample out of limits. Little buildup on media. With only 2 people using the system it has had not had time for bacteria to build up on media to fully treat the system. Need to re-test in a year at the next inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 10:00 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0245 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | None | Clear | [5 empty] | 10/31/2023 | Pump Chamber | 2.000000 | [5 empty] | Will be sent separately | Inspected | Performed annual inspection and routine maintenance. Also collected effluent sample for 5-year BOD test. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
07/18/2023 | Alternative | Routine/Scheduled | 087-STS-6527 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/18/2023 | 09:13 AM
03/08/2023 | Alternative |  | 101-07-0506 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Rod | Howard | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/14/2023 | Alternative | RoutineScheduled | 133-STS-97265 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | changed diffusers | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/14/2023 |  | RoutineScheduled | 07-113-124 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/14/2023 | 12:00 AM
12/26/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0198-SP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | The peat in the Puraflo modules is saturated and no longer providing treatment. We recommend that the peat be replaced or that you consider installing a different alternative treatment unit. If you wish to consider installing a different alternative treatment unit, you will want to contact an Alternative Onsite Soil Evaluator (AOSE). The AOSE who designed your system was M&M Soil Consultants. They can be reached at 540-373-3414. 2-21-24: Per email from Ed Scott to MWebb : " We offered to assist with peat replacement, but also suggested contacting M & M Soil Consultants (system designer) about considering installing a different treatment system." | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/02/2024 | 11:12 AM
05/19/2023 |  | Reportable Incident | 196-08-0175 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced distribution box with new 8 port concrete DBox. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 02:15 PM
02/13/2023 |  | Routine/Scheduled | 2008-143-0157 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/13/2023 | 01:10 PM
02/01/2023 |  | Follow-Up | S 800-19-0059 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 2.000000 |  | 1.000000 | [5 empty] | Took initial BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | Jan 1 1900 12:00PM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/26/2023 | Alternative | RoutineScheduled | 02-197-A6 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/26/2023 | 12:00 AM
04/14/2023 |  | Reportable Incident |  | King & Queen | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Bionest |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Distribution Pump Operation | None | N/A | [17 empty] | AOSS - Initial Visit - Previous service provider = Churchview Septic. Discharge pump not operating and requires replacing. Treatment system is a bionest ATU, but the clarifier has been "modified" to be a discharge tank by suspending a discharge pump in the chamber. DOES NOT meet manufacturer design! Needs discharge pump and float sensors replaced. Electrical connections made INSIDE of tank and not waterproofed. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/17/2023 | 09:00 AM
01/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Dec 30 1899 4:00PM
06/29/2023 | Alternative | Reportable Incident | 073-STS-104617 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles"] | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | COSS - Maintenance - GMP2018-02 Reparged septic tank at inlet and outlet. Replaced distribution box with new 8 port concrete DBox Spliced to existing conveyance line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 07:15 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0387 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/30/2024 | 01:28 PM
03/31/2023 |  |  | 179-18-0155-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/04/2023 | Alternative | Routine/Scheduled | 151-16-0030 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Control Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Initial Visit - Alarm Event. - System flooded - pumped septic tank and discharge tank - found control panel had blown fuse and tripped circuit breaker. Trash Tank - normal level after pumpout. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - restored to operation - pump, controls operating. no surfacing noted in absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 06:45 AM
10/13/2023 | Alternative | Follow-Up Component Maintenance | SD-05-416 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Chlorination |  |  |  | NA | [9 empty] | 2.000000 | 0.050000 | 5.200000 | 7.700000 |  |  | Will be sent separately | Inspected | Effluent Sampling Only Dissolved Oxygen 8.65 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
04/13/2023 |  | Initial Visit | 165-STS-338755 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["None"] | [] | [18 empty] | Start up | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:00 AM
10/10/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 8.160000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
05/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 05/03/2023 | Sample Chamber | 40.000000 | [5 empty] | Attached to this report |  | Septic Tank-6"sludge 1"scum/ Microfast-12"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-1980 ETM-50h 56m/ Pump2-1910 ETM-49h 19m On-1m 33s Off-6h Peak off-4h 48m/ Peak-36/ High-22/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/26/2023 |  | Routine/Scheduled | 234-18-360 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/26/2023 | Jan 1 1900 11:45AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/14/2023 | 10:47 AM
10/24/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | Dec 30 1899 9:05AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance | 182-13-0161 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Kennel on drainfield should be moved | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
05/05/2023 | Alternative | Routine/Scheduled | 166-09-098 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | 05:28 PM
01/31/2023 |  | Routine/Scheduled | 228-11-0244 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/31/2023 |  | 3.000000 |  | 30.000000 | 2.000000 | 20.000000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 10:18AM
12/22/2023 | Alternative | Reportable Incident Component Maintenance | 177-08-0023-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. System was on high level due to bad contactor blowing pilot fuse causing processor not to work. Replaced contactor and fuse and system started working. Advised customer to minimize water usage for 24 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
01/13/2023 |  | RoutineScheduled | 043-15-0063 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 09:20 AM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-88653 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
02/20/2023 |  | RoutineScheduled | 179-09-0007-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Cloudy appearance of treated effluent suggests that effluent would not pass if sampled. Found 3 cleaning agents in use that contain quats. Residue cannot go down the drain (including wipes used for spray disinfectants)! Manager urged to switch to bleach-based cleaners. Drip rate high on zone 2, possibly due to stuck check valve on zone 1 or bad emitters. Ran out of effluent for testing. Will check again at next inspection. Zone 1 arv's still blocked by downed tree limbs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
07/07/2023 | Alternative | Initial Visit | 800-STS-13769 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 14.000000 |  | 10.000000 | [5 empty] | Owner called due to a red light. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV light bulb. The timer is set to 2.5 minutes every 2 hours. Took BOD and Fecal samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/07/2023 | Dec 30 1899 8:30AM
07/14/2023 | Alternative | RoutineScheduled | 175-05-0141 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | NA | [17 empty] | Septic Tank-12"sludge 4"scum/ Microfast-18"sludge/ Pump Tank-2"sludge 0"scum/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-400009 ETM-509512/ Drip counts: Z1-13347/ Z2-13353/ Z3-12665/ Replaced faulty zone2 air release valve/ No breakout or spongy areas on the drip field and dosing correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/15/2023 |  | Follow-Up | 177-06-0247-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Gravity | Gravity |  | UV |  |  |  | NA | [9 empty] | 16.000000 |  | 105.900000 | 36.600000 |  |  | Will be sent separately | Inspected | DO 10.02 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/06/2023 |  | Routine/Scheduled | 2010-143-0093 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 09:00 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/29/2023 | Alternative | Follow-Up | 550-STS-6575 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Installed a new Norweco UV unit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/29/2023 | Dec 30 1899 12:00PM
12/18/2023 | Alternative | Routine/Scheduled | -STS-6730 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Trash Tank Condition of above Component Notes for above Component Water level normal. Flushed and cleaned effluent screen. Not due for pump out Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Not due for pump out Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning. Checked and confirmed visual alarm. PH: 6.7 - Low Adjusted recirculation off time from 15 minutes to 17 minutes Distribution Box Condition of above Component Notes for above Component Homeowner did not want distribution box excavated Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 2:24PM
08/30/2023 | Alternative | Routine/Scheduled | 800-06-0459 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | Dec 30 1899 8:50AM
07/11/2023 | Alternative |  | 033-16-0135-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
04/24/2023 |  | RoutineScheduled | 04-125-055 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/24/2023 | 12:00 AM
03/09/2023 |  | Pump-Out Only | 2009-143-0110 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Hoot |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Pumped trash tank and pump tank empty to effect additional repairs to treatment system. Sensor probe appears to have failed - replacement probe ordered. System wired for float sensor operation until replacement probe arrives. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/13/2023 | 07:45 AM
05/03/2023 |  |  | 04-120-0126A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
01/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | Dec 30 1899 11:08AM
08/14/2023 | Alternative | RoutineScheduled | 107-06-0396 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-19005 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. All tanks have been pumped out since last December. Infiltration was observed at domed lid of atu tank last December after a very heavy rain. No rain-related alarms since then. Monitor for now as it may require a new tank. Not necessary at this point. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
06/07/2023 | Alternative | Routine/Scheduled | 550-STS-5874 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The timer is set to 4.75 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | Dec 30 1899 2:45PM
04/16/2023 | Alternative | Routine/Scheduled | 149-STS-10957 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | Dec 30 1899 9:30AM
12/05/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | LP |  |  | Pressure | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
01/25/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Advantex |  | Pump | Pressure | Drip | Not Applicable | 175.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | 05:30 PM
07/26/2023 | Alternative |  | 051-STS-17328 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 |  |  |  |  | 8.000000 |  |  | Will be sent separately |  | BOD: BDL TSS: 8.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
12/09/2023 | Alternative | RoutineScheduled | 2060-98-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NA | Musty | Clear | 7.200000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/12/2023 | 12:00 AM
12/08/2023 | Alternative | RoutineScheduled | 147-18-0048 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1000 | Aquaklear |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | None | Clear |  |  | 5.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | Dec 30 1899 11:00AM
07/18/2023 | Alternative | Routine/Scheduled | 550-STS-6449 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/18/2023 | Dec 30 1899 11:25AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | Dec 30 1899 11:24AM
12/11/2023 | Alternative | RoutineScheduled | 163-STS-338724 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | SEPTIC TANK ONLY | ADVANTEXAX20RT | Pump | Gravity | Discharge | UV |  | ["None"] | ["None"] | NO | [7 empty] | 12/11/2023 | Pump Chamber | 1.000000 |  |  | 5.000000 |  |  | Attached to this report |  | THIS VISIT WAS FOR THE 180 DAY SAMPLE DRAW. THE BOD AND TSS WERE WELL WITHIN PERMITTED LIMITS. THERE WERE NO OTHER FIELD SAMPLES TAKEN BECAUSE THERE WERE NO DISCHARGE FROM THE OUT FALL PIPE. THE LIDS WERE SECURED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 01:05 PM
11/10/2023 | Alternative | Routine/Scheduled | 800-07-0126 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge pump has exceeded life expectancy. Discharge pump plumbing has exceeded life expectancy. Discharge floats have exceeded life expectancy -Media Sheets: Cleaned media. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly -Distribution Box: Surge box has collapsed. Distribution box lid is cracked -Drain Field: Noted surfacing issues that may be sub surface run off from collapsed surge box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 3:08PM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
01/26/2023 |  | RoutineScheduled | 132-14-0132 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/28/2023 | 12:00 AM
07/03/2023 | Alternative |  | 027-STS-15415 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/03/2023 |  | 4.130000 |  |  | 6.170000 |  |  | Will be sent separately |  | BOD: 4.13 TSS: 6.17 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/03/2023 | 12:00 AM
09/15/2023 | Alternative | RoutineScheduled | 2116-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 1000.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | Musty | Clear | 7.300000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/16/2023 | 12:00 AM
09/19/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Bio Barrier | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed filter on Microfast to control odor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
12/07/2023 | Alternative | Routine/Scheduled | 228-07-1005 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | Dec 30 1899 10:00AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Homeowner had tree company plant shallow saplings on the property. Tree company had planted some saplings on the end of the lines. They do not appear to be causing an issue at this time. The homeowner is contacting the tree company to move them off the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Parking on distribution box is falling off. There is root infiltration and the level is low. Recommend adding a 90 or a Tee to the inlet pipe. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
08/31/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | 12:00 AM
07/11/2023 | Alternative | Routine/Scheduled | 085-STS-31560 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Norweco Singulair ATU |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | NO | [17 empty] | System checked. System appears to be operating normally. Trash tank will need to be pumped out at next visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | Dec 30 1899 9:35AM
10/31/2023 | Alternative | RoutineScheduled | 133-STS-97272 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 10/31/2023 | [9 empty] | BOD = 5mg/l | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/11/2023 | Alternative | Routine/Scheduled | 093-07-0102 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | Dec 30 1899 10:07AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/03/2023 | Alternative | Follow-Up Component Maintenance | 179-06-0455-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Checked distribution box and video inspected drainfield. Drainlines 1, 2 & 3 are fully saturated. Line 4 is partially saturated. We propose to Terralift the 4 lines in an attempt to improve drainage. Proposal to be sent to Terralift drainfield, replace peat and replace worn pump. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 04:50 AM
10/16/2023 | Alternative | RoutineScheduled | 128-08-0042 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/07/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Pressure | Drip |  | 600.000000 | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens"] | Effluent Screens | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/27/2023 | 01:41 PM
06/27/2023 | Alternative | Routine/Scheduled | 157-10-0255 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Real Estate Inspection Trash Tank - pumped empty for inspection. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip Field - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 10:00 AM
11/28/2023 | Alternative | Routine/Scheduled | 14-142-0189 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/28/2023 | Dec 30 1899 2:44PM
09/22/2023 | Alternative | Routine/Scheduled | 2013-126-031 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/22/2023 | Dec 30 1899 2:16PM
03/07/2023 |  | Pump-Out Only |  | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 07:20 AM
07/14/2023 | Alternative | RoutineScheduled | 179-07-0261-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-0 | 0-0 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear | [14 empty] | Inspected | tank pumped a few months ago | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 PM
02/13/2023 | Alternative | RoutineScheduled | 17-160-0191 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | Dark Brown | [14 empty] | Inspected | - recommend pretreatment tank be pumped/cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | 12:00 AM
09/22/2023 | Alternative | Reportable Incident | 107-05-0260 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | Clear | [15 empty] | replaced peat moss | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/09/2024 | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance | 107-05-0333 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
05/02/2023 | Alternative | RoutineScheduled | 115-02-0128 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Septic Tank |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | [18 empty] | System ok | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 02:15 PM
02/08/2023 |  | RoutineScheduled | 185-STS-15925 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/08/2023 | 12:00 AM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | YES | [17 empty] | Septic Tank-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pump, floats, alarms and hydraulic unit functioning properly/ Counts: No pump counts or ETM/ Peak-034771/ High level-30/ Watermeter-2,437,033/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/14/2023 |  | Reportable Incident | {FIPSCode}-STS-4989 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | N/A | [17 empty] | Replaced aerator and Norweco UV | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/14/2023 | Jan 1 1900 7:30AM
09/22/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [13 empty] | Replaced pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | Dec 30 1899 12:15PM
04/18/2023 |  |  | 087-STS-6430 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | 12:00 AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
02/01/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.500000 |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:00 AM
10/27/2023 | Alternative |  | VAG408348 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST |  | Gravity | Gravity | Discharge | Chlorination |  | [] | ["BlowerCompressorAerator Operation","Disinfection"] |  | None | [16 empty] | Vacant: Not Discharging at time of inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/12/2023 | 09:30 AM
05/04/2023 |  | RoutineScheduled | 133 14 0192 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Cleaned recirculation pump intake screen. 12" solids in discharge portion of treatment unit. 8" of solids in recirculation portion of treatment unit. Excellent treatment quality. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 07:03 PM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-370 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
11/01/2023 | Alternative | Reportable Incident | 093-07-0226 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: Upon arrival, I found the system in normal level. Checked and found no incoming power for,recirculation pump. Checked and found residential breaker had tripped. Noted that residential breakers for pumps are 15 amps. Checked and confirmed recirculation pump is functioning properly and pulling normal amperage. I was not able to replicate issue. Noted that the recirculation pump, pump plumbing, and recirculation floats have exceeded life expectancy. Recommended that homeowner upgrade residential pump breakers to 20 amps. She is interested in upgrading pump, pump plumbing, and floats after the beginning of the year when she may be in a better financial situation | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | Dec 30 1899 10:49AM
06/14/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/15/2023 | Dec 30 1899 12:05PM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/16/2023 | Alternative | Reportable Incident Component Maintenance | SP-04-958 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to Rsv leaking water in recirc tank not allowing water to get to drainfield. Jumper was missing in the panel not letting panel to function properly and putting the panel in vacation mode. Video inspected header lines they all had blockages or crushes in all header lines. Proposal to be sent to fix header lines and replace rsv. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/01/2023 | 05:07 AM
03/02/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/02/2023 | 12:00 AM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0815 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
01/16/2023 |  | Follow-Up | 175-03-0956 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | Tank pumped by Septic Clean. Tank pressure washed and all sludge and debris removed. Torn diffuser was the reason for the single-point aeration. Ballast blocks removed and pvc support stands installed to allow for 360 degree aeration. A new manifold was installed, flush valve added for future maintenance, and pvc spring check valve added at the manifold inlet to prevent backflow of water into the blower if the system overflows. Replaced failed blower with new Gast blower. Applied additional fiberglass to the mechanical manway to repair the holes and provide additional strength. New LB cover installed. Refilled tank with enough fresh water to verify excellent aeration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
08/14/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Fuji |  | Gravity | Gravity | Trenches |  | 600.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 02:37 PM
08/03/2023 | Alternative | Follow-Up Component Maintenance | SD-04-l88 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | [14 empty] | Will be sent separately | Inspected | (Note: all tanks pumped out yesterday by local pumper.) Spin filter was not crushed, but was starting to look dirty already. Bleach-cleaned the filter and reinstalled it. Placed 4" solid blocks under the pump to give it some separation from accumulated sludge and peat fines. Shortened pump piping to accommodate the blocks, eliminated the recently installed weep hole, and added an air release valve with schrader to enable testing of pump supply pressure. Hopefully all of the above will help the spin filter to go a full year without crushing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
01/10/2023 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sandfilter |  |  | Pressure | Discharge | Chlorination |  | ["SludgeScum Accumulation"] | [] | [18 empty] | Recommend digging off Septic for pumping | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/10/2023 | 12:00 AM
09/18/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/18/2023 | Dec 30 1899 8:00AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 181-09-0018 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Bio Barrier | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 07/26/2023 |  | 44.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
12/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 11:50AM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | none | none | Gravity | Gravity |  | Chlorination |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Added tablets | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
03/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The best 1 tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
01/30/2023 |  | Routine/Scheduled | 196-09-121 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 05:45 PM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-443 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Effluent Screens"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | As noted on last year's inspection, the Advantex sheets are bridging. We recommend pumping the tanks and installing new sheets. Additionally, the split flow tee is settling and causing water to back up int he Advantex module. We recommend installing a new style RSV and raising the Advantex module. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
05/16/2023 |  | RoutineScheduled | SWP-02-463 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
11/15/2023 | Alternative | RoutineScheduled | 109-18-0191 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Scum level-under 1"- 14" sludge in Septic tank. Treatment unit - Recirculation zone 6" sludge - Discharge zone 8" sludge, Owner has addressed the surround of septic tank and run off around tank area, Clear effluent on top of discharge. Cleaned Effluent filter- sprayed off media, Ran in test mode, all floats tested ok, Alarm functional. Box 428520 and RTU 136855 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-349 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Installed new riser & lid on the Septic Tank. Also installed used return diaphragm. All tanks pumped just prior to inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/07/2023 | Alternative | Initial Visit | 03-160-0280 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | Whitewater |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] |  | Septic | [6 empty] | 04/07/2023 | [8 empty] | Inspected | - recommend that both tanks be pumped/cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/10/2023 | 12:00 AM
11/01/2023 | Alternative | Routine/Scheduled | 151-09-0142 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Ecoflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 05:07 PM
01/10/2023 | Alternative | Reportable Incident | 800-07-0230 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/10/2023 | Dec 30 1899 9:00AM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/29/2023 | Alternative | RoutineScheduled | 02-163-0154 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/25/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Best 1 | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Filter was clogged but able to clean | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
12/04/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | Dec 30 1899 11:55AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0503 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/27/2023 | Alternative | Routine/Scheduled | 05-160-0080 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 122.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 10:45 AM
05/03/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/29/2023 |  | RoutineScheduled | 08-192-039 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/29/2023 | 12:00 AM
08/04/2023 | Alternative | RoutineScheduled | 181-09-0164 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was cleaned. The controls were operating as designed. The treatment unit was in good operating condition. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 01:15 PM
11/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | Dec 30 1899 9:34AM
01/17/2023 |  | RoutineScheduled | 175-19-0038 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-4" Sludge 0"scum/ Microfast ATU-2"sludge/ No pump out needed at this time/ Blower, controls and alarm functioning properly/ Blower air filter cleaned/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/02/2023 | Alternative | RoutineScheduled | 151-13-0152 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/04/2023 | Alternative | RoutineScheduled | 043090078 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine Annual | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/04/2023 | 12:00 AM
11/27/2023 | Alternative | Routine/Scheduled | 151-17-0135 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Arrived on site, Dutch had pumped tank before I got there and cleaned filter. -Discharge/Pump Tank: Found at normal level, floats and pump are working. Can hear alarm from outside Floats and pump are aged. Riser showing signs of streaking -Peat Moss: Peat moss is broken down and compacted. Peat moss in need of replacement. Tipping bucket and trays are in working order. Signs of streaking on ecoflo riser -Distribution Box: Found dbox at normal level, all lines balanced. No signs of roots or cracks -Drain Field: No signs of surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 10:01 AM
01/10/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2269 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 12:50PM
08/15/2023 | Alternative | Routine/Scheduled |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Trash tank - normal level - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip field - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | Dec 30 1899 7:00AM
04/10/2023 |  | RoutineScheduled | 95-197-A6 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/10/2023 | 12:00 AM
03/10/2023 |  | RoutineScheduled | 033-STS-87124 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
06/20/2023 | Alternative | Reportable Incident | 151-16-0045 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | 06/20/2023 - septic tank pumped for storage 06/23/2023 - biofilter changeout conducted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | 09:00 AM
07/10/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1000 | anua (puraflo) |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Effluent Screens"] | ["Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | The entire system is in compliance with the health department regulations and approved plans. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 03:30 PM
06/01/2023 |  | RoutineScheduled | 124-STS-2379 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Virginia Beach | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Advantix | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/27/2023 | Alternative | RoutineScheduled | SD-15-273 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | EcoVirginia LLC | 1942001235 | William | Poindexter | 2.000000 |  | Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Effluent Screens"] | ["Attached Growth Medium","Auxiliary Filter","Effluent Screens"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/06/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
09/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/21/2023 | Dec 30 1899 2:30AM
06/13/2023 |  |  | 179-STS-89524 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/06/2023 | Alternative | Routine/Scheduled | S07-180-0014 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | Jan 1 1900 11:30AM
10/26/2023 | Alternative | RoutineScheduled | 153-STS-20238 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation","Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank-10"sludge 4"scum/ EZ-Treat Tank-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Recommend pump out of the Septic-EZ Treat Tank with in the next several months/ Recirculation pump intake cleaned/ Controls, pumps, floats and alarms are functioning properly/ Counts: EZ-Treat Pump-0,122,667 ETM-05,483.79/ Pump Tank to Drip-4393 ETM-943h 15m On-13m 33s Off-2h 40m/ Peak-4/ High level-27/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/24/2023 |  | Initial Visit | 550-STS-6912 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 2.000000 |  | 1.000000 | [5 empty] | Received a called about the pump being bad. Serviced system. Checked the panel and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the P-20 pump (new serial # 2207-139425). The timer is set to 6 minutes every 1 hour. Took BOD and Fecal sample. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/24/2023 | Jan 1 1900 9:45AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Control panel enclosure cleaned and seals treated (for now). Seals need replaced. "Power On" light and "Pump Running" light (both green) were both burnt out, assemblies replaced. Remote alarm was found in the silenced position and power turned off. Power restored, alarm reset and then tested to verify proper operation. Filter element for blower canister filter replaced. Water level was low enough that the pump looked like it was set too high off the bottom. Measured and verified that pump was 15" from tank bottom, should be 10". Weeds and trees at filter bed vent need to be eradicated. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | UV light is not functioning as designed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Homeowner had tree company plant shallow saplings on the property. Tree company had planted some saplings on the end of the lines. They do not appear to be causing an issue at this time. The homeowner is contacting the tree company to move them off the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
04/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
12/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Programmed panel properly lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-202 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Water level was high on septic tank due to clogged filter, cleaned, customer said they have been using garbage disposal but the wont use it any more. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
10/27/2023 | Alternative | Routine/Scheduled | 151-08-0107 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: High level when arrived on site 10 in of sludge Less than 1in of solids Pulled and cleaned rsv Pumped to normal level on site No signs of infiltration -Recirculation Tank: High level when arrived on site due to discharge pump not working Tested floats and pump all working as should All plumbing intact and pump moving water properly Pumped down to normal level No signs of infiltration -RSV (Recirculating Splitter Valve): Pulled and cleaned -Discharge/Pump Tank: High level when arrived on site due to pump not working Tested floats and pump all working as should All plumbing intact Pump moving water pulling high amperage Pump approved to be replaced Need to return to install new pump No signs of infiltration -Media Sheets: Flushed and brushed media sheets Flushed module until water ran clear Sprayed media sheets clean Module intact -Control Panel: 120 volts coming in All visual and audible alarms functioning properly All components working however panel is Aged Approved replacement of new panel Will need to return to replace panel -Distribution Box: Unable to locate -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 08:14 AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0309-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend replacing the broken air release valve on the upper zone of the drip dispersal system. We also recommend replacing both lids on the air release valve housings. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
05/03/2023 | Alternative | Reportable Incident | S 800-17-0207 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | None | [16 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/03/2023 | Dec 30 1899 2:00PM
07/19/2023 | Alternative | Reportable Incident | 800-09-0274 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | None | [16 empty] | Replaced aerator, diffuser and Clearstream alarm float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/19/2023 | Dec 30 1899 11:00AM
11/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 8"scum/ Microfast-10"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time but may be necessary next year/ Blower air filter cleaned and blower is functioning properly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-1694 ETM-64h 34m/ Pump 2-1679 ETM-55h 53m/ High-14/ Peak-23/ No breakout or spongy areas on the djainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/27/2023 | Alternative |  | 2015-143-0056 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 12:00 AM
12/14/2023 | Alternative | RoutineScheduled | 12-113-215 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/14/2023 | 12:00 AM
11/13/2023 | Alternative | Routine/Scheduled | S-175-16-0038 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 1:50PM
07/25/2023 | Alternative | RoutineScheduled | 109-18-0162 | Bedford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | EZ treat 600 | none | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | re-circulation pump is bad needs to be replaced. Emailed and spoke to customer. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/26/2023 | 04:30 PM
05/04/2023 | Alternative | RoutineScheduled | 04-160-0157 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 3.000000 | 1250gal | Ecoflo (peat moss) |  | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [] | YES | Septic | Cloudy | [6 empty] | Pump Chamber | [9 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
08/25/2023 | Alternative |  | 101-18-0200 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Leslie | Andrus | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/06/2023 | Alternative | RoutineScheduled | 041-STS-259428 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Carrington Pump & Irrigation | 1942001121 | John | Carrington | 1.000000 |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["Effluent Screens","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
10/29/2023 | Alternative | RoutineScheduled | 136-02-0616 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex AX20 |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
06/02/2023 |  |  | 033-06-0020-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
06/28/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 09:00 AM
08/01/2023 | Alternative | RoutineScheduled | 182-07-0082 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Replaced blown spin filter. Replaced blower | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/01/2023 | 12:00 AM
07/17/2023 | Alternative | RoutineScheduled | 104-07-0333 | Amherst | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | [15 empty] | Inspected | Septic Recirc Zone 3-4" scum 12-14" Sludge- Recirc zone 8-1- " sludge, Discharge zone 6" sludge, Pump Tank basin 14-16" sludge- We reccomend to arrange a pump out of septic tank prior to next years visit. Cleaned BioFilter, RSV, Sprayer Manifold- brushed and flushed. Tested both Pumps ok, 12 amps on recirc pump and 11.7 amps on discharge pump, Float switches appear opperational but suspect lower float going bad in discharg. Alarm functional. Noticed water leaking into septic tank. infiltration around 4 in T. high number of alarms in history due to infiltration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/30/2023 | 09:30 AM
06/29/2023 | Alternative | RoutineScheduled | 150-08-0222 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 gallons | septic tank | Clearstream | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear |  |  | 40.000000 | [12 empty] | Septic tank 2" fog, 18" sludge. Clearstream 40% SS. Clearstream aerator not running, rebuilt aerator functioning properly now. Pump, alarm, floats, controls operating properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/23/2023 | 07:45 PM
03/15/2023 | Alternative | RoutineScheduled | 159-10-015 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt | No incoming power found breaker and powered on | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
08/07/2023 | Alternative | Routine/Scheduled | 151-05-371 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank Pumped | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | [26 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 05:50 PM
03/29/2023 | Alternative | Follow-Up | 047-17-148 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 | 600 | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Follow up. Added access point to septic tank inlet side ( Ez-set plastic riser). Removed scum layer in ATU tank. Dug up and sealed inlet pipe in ATU tank also removed root that was growing in there. Pumped out pump tank completely due to solids. Added root destroyer around inlet pipe of ATU and the new riser we installed on septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
05/12/2023 | Alternative | RoutineScheduled | SD-03-449 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic | FAST ATU | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/26/2023 | 08:30 AM
08/01/2023 | Alternative | RoutineScheduled | 18-173-013 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service, Inc | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Purasys |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | Dec 30 1899 10:00AM
01/27/2023 | Alternative | RoutineScheduled | 154-05-0614 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
04/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/31/2023 | Alternative | RoutineScheduled | 181-05-0331 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1000 | Ecoflo |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","Other"] | ["Auxiliary Filter","Other"] | NA | [17 empty] | Septic tank filter checked and cleaned. Cleaned tipping trays. Septic system did not need to be pumped. Peat moss in Ecoflo raked. Ponding on peat moss <50% after raking. No apparent leaks in system or drain field area. Lids were properly secured. We discussed with the land owner about changing treatment unit to another alternative system (other than peat moss) when needed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/16/2023 | 10:15 AM
03/13/2023 |  | RoutineScheduled | 14-100-0361 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 099-07-0062-ST | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. peat still looks ok but recommend to auger it next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:55 PM
07/26/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced (2) N163 effluent pumps. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | Dec 30 1899 1:44PM
11/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [7 empty] | 11/15/2023 | [10 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | Dec 30 1899 12:00PM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | alarm switch and gauge repaired | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
04/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/11/2023 | 01:03 PM
09/22/2023 | Alternative | Follow-Up Component Maintenance | SWP-05-120 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Dug up both distribution boxes. Pumped excess effluent back to septic tank. Replaced lid on distribution box #1. Terra lifted all drain lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
02/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/25/2023 | Alternative | RoutineScheduled | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 01/25/2023 |  | 28.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
12/06/2023 | Alternative | RoutineScheduled Component Maintenance | 175-08-0576 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/08/2023 | 08:29 AM
08/18/2023 | Alternative | RoutineScheduled | 06-100-1677 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 300.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 3-4" FROM THE BOTTOM AND 1" FROM THE TOP REPLACED ALARM FLOAT NEW PEAT RECENLTY EVERYTHING WORKING AS IT SHOULD | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/12/2023 | 09:55 AM
10/27/2023 | Alternative | RoutineScheduled | VAG401973 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST |  | Gravity | Gravity | Discharge | Not Applicable |  | [] | ["BlowerCompressorAerator Operation"] | NA | None | [16 empty] | Not discharging at time of inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/12/2023 | 09:15 AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
04/07/2023 | Alternative | Reportable Incident | 800-09-0213 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and air sensor | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/07/2023 | Dec 30 1899 8:00AM
05/30/2023 |  | RoutineScheduled | 2002-93-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 7.400000 | 10.200000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 06/15/2023 | 12:05 PM
07/14/2023 | Alternative | RoutineScheduled | 127-STS-34220 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 2250 | 1000 | 10000 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | None | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
02/22/2023 | Alternative | RoutineScheduled | 061-16-468 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/04/2023 | Alternative | Routine/Scheduled | 109-09-0451 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/04/2023 | 11:00 AM
12/04/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | ["None"] | ["None"] | YES | None | Clear | [5 empty] | 12/04/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2024 | 11:55 AM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
02/20/2023 | Alternative | RoutineScheduled | 154-14-0156 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Gravity | Gravity | Trenches | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation","Auxiliary Filter"] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation","Auxiliary Filter"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 01:10 PM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance | 182-12-0151 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | pumped septic tank replaced buzzer and pump tank lid alarm was unhooked ponding in field but no leaks | This AOSS should now return to normal function after having provided the above state routine maintenance | 07/06/2023 | 08:40 AM
06/03/2023 | Alternative | Routine/Scheduled | 183-STS-10391 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | Dec 30 1899 9:00AM
12/07/2023 | Alternative | RoutineScheduled | 03-184-051 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | [5 empty] | None | Clear | 7.500000 | 6.000000 |  | 0.000000 | [11 empty] | This is a UV unit | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/05/2023 |  | RoutineScheduled |  | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 1-3 0-0 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | None | Clear |  |  | 3.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | 10:00 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2024 | 12:23 PM
12/05/2023 | Alternative | Follow-Up Component Maintenance | VAG408340 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | UV |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced blower panel and UV System | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/01/2023 | Alternative |  | 15-113-047 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/01/2023 |  |  |  |  | 3.800000 |  |  | Will be sent separately |  | BOD: BDL TSS: 3.80 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/01/2023 | 12:00 AM
04/24/2023 | Alternative |  | 11-160-0128 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | - pumped/cleaned Microfast Tank - installed ground access riser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 12:00 AM
03/28/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Manifold was repaired and riser was replaced. System should now function as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 12:00 AM
02/10/2023 |  | Initial Visit | 550-STS-6402 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 3 hours. Did not take initial sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | Jan 1 1900 12:45PM
12/20/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0004-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Hoot | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Effluent Screens" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Effluent Screens" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Upon arrival, the pump and filter were clogged and not moving much water. System went to 3.9gpm after cleaning pump and filter. Additional alarm on 12/22 appears to be caused by a defective sensor in the control panel. We plan to meet A&S on January 3 to assist with pumping the tanks and to install a new PSI Gauge in the pump tank. Please have the water turned on. We will also meet an electrician at that time to explore options to install a new control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
02/09/2023 | Alternative | RoutineScheduled | 061-STS-26764 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 4.000000 |  | Septic Tank #1 | Septic Tank #2 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | [] | NO | [17 empty] | This system services 2 houses: Master house- Septic tank #1-0"sludge 0"scum/ Septic tank #2-4"sludge 0" scum/ Pump Tank-0"sludge 0"scum/Septic tank (Other house) 0"sludge 0"scum/ No pump out of any of the tanks needed at this time/ Noted: 3 out of 4 Puraflo peat modules are ponding, other pod not ponding but peat quality is very poor/ Requires all peat be replaced/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-036468 ETM-0095219/ No breakout or spongy areas on the drainfield. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
05/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
03/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
01/07/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | 01:31 PM
10/02/2023 | Alternative | RoutineScheduled | 08-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 6 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/02/2023 | 12:00 AM
08/14/2023 | Alternative | Routine/Scheduled |  | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - five modules - Peatmoss in good condition - raked / turned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 12:45 PM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/13/2023 |  | Pump-Out Only |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Pumped out advantex tank Septic system in working condition | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/15/2023 | 11:00 AM
09/26/2023 | Alternative | RoutineScheduled | 019-STS-23807 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 8" of accumulated solids in first section of septic tank. 14" of accumulated solids in second section of septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 07:03 PM
08/24/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Blower replaced | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/24/2023 | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 139-06-0116 | Greene | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired puraflo alarm float | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/15/2023 |  |  |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | [7 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | replaced blower motor | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:00 AM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92341 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | 7.200000 | 14.700000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 08/15/2023 | 01:44 PM
01/24/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  |  | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Dispersal System Operation","Recirculation Pump","Level Sensor Operation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | [18 empty] | replace float, boxes and lids | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0404-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The capacitor has broken off its base and should be replaced. The bottom two floats are working intermittently and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
05/05/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 |  |  | Pump | Pressure | Trenches |  | 600.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 10:13 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | One lateral appears to be more nitrified than others but is not showing signs of hydraulic saturation or surfacing effluent. Recommend balancing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/21/2023 | Alternative | RoutineScheduled | 05-192-015 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/21/2023 | 12:00 AM
10/12/2023 | Alternative |  | 179-STS-91869 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/10/2023 | Alternative | Routine/Scheduled | 228-04-1181 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 1:20PM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Filter element for blower canister filter replaced and the air pre-filter cleaned as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
12/06/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
11/21/2023 | Alternative |  | 167-STS-17733 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/21/2023 |  | 9.210000 |  |  | 1.700000 |  |  | Will be sent separately |  | BOD: 9.21 TSS: 1.70 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/21/2023 | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/14/2023 | Alternative | Follow-Up | 053-STS-10727 | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Paul Small LLC | 1942001402 | Paul | Small | [8 empty] | 700.000000 | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NO | None | Clear | 7.000000 |  |  |  |  | 06/14/2023 | Pump Chamber | 4.000000 |  |  | 3.700000 |  |  | Attached to this report |  | This is the required 6 month sample from startup. It is working perfectly. No maintenance necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | Dec 30 1899 10:15AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/27/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/02/2023 | 12:00 AM
06/30/2023 | Alternative | Routine/Scheduled | 14-172-0185A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/30/2023 | Dec 30 1899 2:27PM
10/16/2023 | Alternative | Routine/Scheduled | 150-06-379 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level, 4in of sludge and less than 1in of solids. Pulled and cleaned filter -Discharge/Pump Tank: Found st normal level, tested floats and pump all working as they should. Found less than 1in of sludge and solids. -Aeration: Found at normal level, found 6in of sludge and less than 1in of solids. turned air pump on and treatment wasn't moving water. Air is making it to treatment tank. Media seems to be clogged -Air Pump/Blower: 120 volts. Air filter is clean. Air pump pulling 4.1 amps. Panel has 120 volts audio and visual alarms working as they should. -Control Panel: 120 volts audio and visual alarms working as they should. Pump pulled 11.2 amps moving water -Distribution Box: Surge box, at normal level, no roots or cracks. Dbox at normal level, lines balanced and taking water. No signs of surfacing in drainfield area. -Drain Field: No signs of surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 09:28 AM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["Other"] | ["None"] | YES | [17 empty] | Needs Peat Moss Topped Off & 3 Screws For Pod | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/31/2023 | 12:00 AM
12/12/2023 | Alternative | Initial Visit |  | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-0 0-0 | 0-0 | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | None | Clear |  |  | 0.000000 | [11 empty] | Inspected | fuji usa unit riser infiltration issue | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 PM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/29/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-5045 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/29/2023 | Dec 30 1899 8:00AM
09/26/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | Dec 30 1899 11:00AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/05/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Don't use toilet drops Peat starting to pond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
03/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/21/2023 | Alternative | Routine/Scheduled | 073-STS-94521 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 6 in of sludge and less than 1 of solids No signs of infiltration -Discharge/Pump Tank: Normal level Less than 1 in of suspended solids Pulled and cleaned pump Pulled and tested all floats working properly Pulled and cleaned filter Plumbing intact Pump properly moving water No signs of infiltration -Aeration: Normal level Less than 1 in of suspended solids Pulled and cleaned air line properly moving air Pulled and cleaned diffuser Pulled and cleaned weir Float working properly No signs of infiltration -Air Pump/Blower: 120 volts coming in Pulled and cleaned filter -Control Panel: 120 volts coming in All visual and audible alarm functioning properly Air pump pulled .63 amps -Drip Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 03:30 PM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/22/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/17/2023 | Alternative | Routine/Scheduled | 157-07-0054 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating - basin is leaking at seams. biofilter - peatmoss is rootbound - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:45 AM
11/15/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to some problems. Serviced system. Checked the panel and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The alarm in the Clearstream is not working. Replaced the P-20 pump (new serial # 2204-137388). Installed 8 silicone wire nuts, installed a new alarm light bulb, and installed a new alarm float. The UV is not working - circuit board is bad - possibly cord and bulb also. - will need to be replaced. The UV breaker was tripped. Meet with the pumping company and pumped out the sludge in the Clearstream tank and pumped the pump tank. The timer is set to 8 minutes every 2 hours. Need to replace gauges to set pressures and perform a draw down test. There was no water to check the vacuum breakers - will check them when setting pressures. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/15/2023 | Dec 30 1899 2:00PM
06/07/2023 | Alternative | Routine/Scheduled | 157-10-0043 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump tAnk - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 10:45 AM
03/13/2023 |  | Follow-Up | 107-11-0087 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  |  | Trenches |  |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [18 empty] | Septic needs to be pumped. Customer to schedule | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 12:00 AM
01/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air blower air line is broken and alarm light not working. Drain field was unable to inspect due to overgrowth. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
11/13/2023 | Alternative | RoutineScheduled | 05-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","SludgeScum Accumulation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/13/2023 | 12:00 AM
05/02/2023 |  | Routine/Scheduled | 085-STS-34456 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | 180 day system inspection / service. Primary septic tank - normal level - effluent screen serviced. Treatment Module - media drapes, spray grid, recirc pump serviced. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | Jan 1 1900 7:00AM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-459 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced corroded pieces of support pipes, Will replace the rest when peat gets replaced. Peat showing its age and is 5" below manifold so most likely will need replacement next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
02/23/2023 |  | RoutineScheduled |  | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 02/23/2023 |  | 93.000000 | [5 empty] | Will be sent separately | Inspected | Need to Keep bushes maintained and trimmed | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Zone 2 Solenoid is not opening and the pump is deadheading against the valve. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/15/2023 | Alternative | RoutineScheduled | 18-100-0146 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1500 | Septic Tank | EcoPod E-50 | Gravity | Pressure | Pad | UV | 500.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 02:25 PM
08/10/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Fuji |  | Pump | Gravity | Trenches |  | 750.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 01:42 PM
01/31/2023 |  | Routine/Scheduled | 234-18-406 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The pressure switch on the aerator is not hooked up. Removed the spinfilter screen. Meet with the pumping company and pumped and cleaned the pump tank. The Clearstream needs 2 - 6" x 20" risers and the pump tank needs 2 - 12" 24" risers. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 11:30AM
03/02/2023 |  | Reportable Incident | 099-07-0017-SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed blower. Replaced blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
10/05/2023 | Alternative | Routine/Scheduled | 2008-143-0096 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NO | [17 empty] | Effluent filter checked. Manifolds flushed. System appears to be operating normally. Vent socks and covers need to be replaced. Vent cap needs to be the flat type. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 11:41 AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
11/20/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Microfast |  | Pump | Pressure | Trenches |  | 450.000000 | ["BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation"] |  | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/11/2024 | 12:37 PM
06/07/2023 | Alternative | Reportable Incident | 073-STS-103480 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced failing distribution box with new 8 port concrete DBox. Spliced to existing Conveyance Line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 11:00 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There is a suspect area just before the drainfield. It looks like it could be an issue with the force main. Informed homeowner and gave recommendations for further investigation. Will update as more information is available. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
02/28/2023 |  | RoutineScheduled | 177-09-0282-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We removed three screws that were protruding through the top of the Fralo Monster Box lid because they were a safety hazard. The gasket for the Monster Box lid is missing and should be replaced. The drainfield lines have settled. We recommend adding topsoil to prevent ponding over the lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
10/20/2023 | Alternative | Routine/Scheduled | 151-15-0022 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 06:54 PM
02/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/14/2023 | Dec 30 1899 8:41AM
03/10/2023 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Trenches |  | 450.000000 | None | None | NO | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 02:28 PM
08/21/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0356-SP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We replaced the contactor on the control panel. There appears to be effluent surfacing due to faulty drip emitters. A follow up visit is planned to uncover and evaluate the emitters. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/01/2023 | 07:38 AM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
04/24/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | fuji needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
09/29/2023 | Alternative |  |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | See attachment | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
02/24/2023 |  | RoutineScheduled | SWT-01-897 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. Check valves stock open on zones 1 and 2, Check valve on zone 3 also aloud water through so recommend to replace all 3 Check valves. Customer wants proposal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
04/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping treatment unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87861 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 4.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treated effluent looks pretty good. Not sure if grease issue has been corrected, or low flow of off-season has allowed better treatment. Next spring will reveal the truth. Microfast dosing pump #2 amps higher than average but still dosing at normal rate. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 09:40 AM
03/21/2023 |  | Initial Visit | 147-04-0072 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 | 1000 | Ecoflo |  | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/21/2023 | 12:00 AM
08/08/2023 | Alternative | Routine/Scheduled | 228-18-0017 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 11:00AM
03/29/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
05/23/2023 |  | Follow-Up | -STS-92916 | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Cleaned FAST unit. Tank pumped out by others. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/01/2023 | 04:39 AM
06/01/2023 |  |  |  | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | EZ Treat | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Recommend pump out of the discharge tank. Owner to make arrangements with local pumper. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
09/13/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  | 450.000000 | ["Control Operation","Dispersal System Operation","Effluent Screens","None"] | ["Control Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/05/2023 | 02:43 PM
03/31/2023 | Alternative | Reportable Incident | 06-174-0113 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Biofilter changeout. Septic tank pumped empty for drying. Expended biofilter media removed - new biomedia installed. Replaced pump, float sensors and installed new control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Dec 30 1899 8:00AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/04/2023 |  | Reportable Incident | 179-10-0160-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to male adapter being broke on the force main and pump was air locked. Replumbed pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
03/29/2023 |  | Initial Visit | 182-18-0014 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Septic Tank Baffles","Dispersal System Operation"] | ["Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 12:00 AM
01/19/2023 | Alternative | Routine/Scheduled | 166-05-272 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [10 empty] | 50.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | 06:43 PM
07/10/2023 | Alternative | Routine/Scheduled | 800-STS-14997 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 1:40PM
04/27/2023 | Alternative | Reportable Incident | SD-11-18 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Numerous high level events for recirc tank recorded in the control panel electronic users log. Slow flow from spray nozzles. Only moderately better after cleaning sludge from recirc pump intake, pump piping, lateral and nozzles. Pump was borderline too small from the beginning and is now worn out. Recommend replacement of the PF15 with a PF30 (or equivalent). Increased run time and frequency of recirc cycles to help compensate for the slower flow. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
07/06/2023 | Alternative | RoutineScheduled | 108-05-0032 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The blower and spin filters were both pulled and cleaned. The controls were operating as designed. There was return effluent returning to the pump tank so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 10:15 PM
01/31/2023 | Alternative | RoutineScheduled | 95-160-0608 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 |  | LPD |  | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Septic | Cloudy | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/26/2023 | Alternative | RoutineScheduled | 2016-143-0235 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Pressure |  |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/26/2023 | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 107-06-0298 | Augusta | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 10/03/2023 |  | 10.200000 | [5 empty] | Will be sent separately | Inspected | Pumping required and roots in system | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/22/2023 | 09:18 AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 12:48 PM
05/22/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/30/2023 | 09:36 AM
10/12/2023 | Alternative | RoutineScheduled | SD-06-33 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 43.700000 | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens"] | YES | Septic | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/14/2023 | 08:00 AM
07/21/2023 | Alternative | Reportable Incident | W800-14-0055 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a float or relay problem and doesn't think the aerator is running. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Fixed the grade on the pipe in the Clearstream. Replaced the relay in the control panel. The septic tank needs additional risers on it to be properly inspected in the future. The timer is set to 1.5 minutes every 3 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/21/2023 | Dec 30 1899 10:45AM
03/28/2023 |  | RoutineScheduled | 179-13-0356-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Level Sensor Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Observed a tree growing close to end of last drainfield trench. Tree needs to be cut down level with the ground. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
05/22/2023 |  | RoutineScheduled | 177-15-0107-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Spinners were not functioning a 100 % due to recirc pump intake clogged, cleaned pump intake plus manifold and system started working correctly. DISCHARGE: HL 80, LL 294, OVERRIDE 184. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
08/10/2023 | Alternative | RoutineScheduled | 107-05-0145 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
03/14/2023 |  | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim |  | 750 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Jan 1 1900 5:20PM
09/15/2023 | Alternative | Routine/Scheduled | 2007-143-0087 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/15/2023 | 09:30 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend replacing one of the lids as it was slightly damaged by mower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/04/2023 |  | RoutineScheduled | SP-05-417 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Tanks may require pumping by next year. Will depend on system use. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 5.000000 |  | Clearstream | Clearstream | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent pump in (600NC on Left from Splitter) is stuck on and will not stop running without shutting off breakers. Pump was left running so as not to flood the tank and cause further issues. Repairs are in progress | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs transformer replaced in panel. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
01/02/2023 | Alternative | RoutineScheduled | SD-10-99 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic | Microfast | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | None | Clear | 6.920000 |  |  | 1.110000 |  | 01/02/2023 | Sample Chamber | 2.000000 | 0.000000 |  | 7.600000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/18/2023 | 10:25 AM
01/17/2023 |  |  | ST-04-529 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
10/05/2023 | Alternative | RoutineScheduled | 023-STS-42917 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 10/05/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 7:45AM
03/24/2023 |  | RoutineScheduled | 08-183-181 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation","Effluent Screens","Distribution Pump Operation","Disinfection","BlowerCompressorAerator Operation","Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/24/2023 | 12:00 AM
05/12/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.790000 |  |  |  |  | 05/12/2023 |  | 26.000000 |  |  | 7.900000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 11:45 AM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Whitewater |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic Tank minimal scum, 8" sludge,(was pumped 2 years ago) Treatment unit 1" scum layer- 8 in sludge layer- Pump tank 6-7 in trace- good aeration, cleaned air filter(very dirty), Cleaned spin filter housing and lubricated housing. Ran system and flush. Zoner valves appears to work, Drain field appears dry. pump reading 947,350 vs 925,130min , pump ran about 370 hours since last visit- | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
01/18/2023 |  |  | 124-STS-2379 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1350 | 1250 | 100 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Pungent | Clear | 6.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 10:30 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | SD-14-431 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Recommend pumping Microfast septic tank by next spring. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
09/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 02/15/2023 |  |  |  | 240.000000 |  |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
08/02/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Fuji |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - not opened at request / direction of owner! !!! Processing Tank - trash tank- normal level Aeration Tank - normal level - mixing present - compressor serviced. Clarifier - sludge return operating. DBox - not opened at request / direction of owner! !!! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 07:30 AM
10/02/2023 | Alternative | Routine/Scheduled | 073-STS-95950 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank 1: At normal level Has 2" of sludge and 2" of solids -Septic Tank 2: At normal level Has 1" of solids with 4" of sludge -Recirculation Tank: At normal level Has 2" of sludge Pulled and cleaned pump, floats and filter -RSV: At normal level Has 1" of sludge Pulled and cleaned rsv -Discharge/Pump Tank 1: At normal level All floats and pump working -Discharge/Pump Tank 2: At normal level Pump and floats working properly -Media Sheets: Both chambers in good shape Sprayed off sheets Brushed and flushed laterals -Control Panel 1: Panel working properly Visual and audible alarms working Discharge pump pulling 5amps -Control Panel 2: Working properly Visual and audible alarms working Recirc pump pulling 11.51amps Discharge pulling 13.4amps -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 11:35 AM
08/11/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-51967 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
07/24/2023 | Alternative | Routine/Scheduled | 151-06-0309 | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - plastic - minor bulging noted - float sensors, pump, operating - alarm NOT functioning. BioFilter - peatmoss failed - standing effluent in center support - soil surrounding treatment module wet - indicating possible module failure. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/25/2023 | 07:00 AM
05/22/2023 | Alternative | RoutineScheduled | SD-02-220 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens" ,"Level Sensor Operation"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-577 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the filter solenoid in the drip dispersal system and the air filter for the blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
07/24/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-92384 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 90-Day Inspection Wiring issue in garage breaker panel corrected by electrician. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
06/21/2023 | Alternative | Routine/Scheduled | 093-06-0223 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | Dec 30 1899 10:06AM
06/02/2023 |  | RoutineScheduled | 124-STS-2379 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Virginia Beach | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 2000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/01/2023 |  | RoutineScheduled | 179-10-0226-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex RT tank in conjunction with your next inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
08/21/2023 | Alternative | Reportable Incident Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed WE20G05P4-21 Drip pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
08/21/2023 | Alternative | RoutineScheduled Component Maintenance | 175-08-0004 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
08/09/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - rsv, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 09:45 AM
02/13/2023 |  | Routine/Scheduled | 2013-143-0034 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 07:30 AM
03/14/2023 |  | Routine/Scheduled | 075-STS-32980 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/14/2023 | Jan 1 1900 4:49PM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/30/2023 | 10:30 AM
02/22/2023 |  | Routine/Scheduled | S 800-14-0128 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 12:09PM
05/09/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 2000 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Unit #3 - Brand new Advantex AX20RT installed infront of large septic tank for newly added RV sites to SWEETWATER RV PARK. Installer completed install today and loogs good and graded well. We came for start up today. Turned on the new Control box, Ran Recirc pump and tested floats. All good, Alarm sounds. Set setting as per Orenco to handle rated flow. Recirc pump setting 5min 18 sec off time and 1 min on time, 1min30sec overide off, 1 min on override, Min override time 60 min, High alarm delay 35 min- Set time and date, System is now fully operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 09:30 AM
01/06/2023 |  | Routine/Scheduled | 07-163-0120 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 9:30AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/03/2023 | Alternative | Routine/Scheduled | 093-06-0183 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | Dec 30 1899 10:00AM
11/27/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | annual maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out -Discharge/Pump Tank: Water level normal. Tested and confirmed that discharge pump is operating properly. Tested and confirmed that discharge float sensors are operating properly. Discharge pump has exceeded life expectancy. Discharge floats have exceeded life expectancy. Splice connections are made inside the tank. -Peat Moss: Structural integrity of tank appears to be intact. Structural integrity of tipping bucket appears to be intact. Checked and confirmed tipping bucket is functioning properly. Raked and tilled peat moss. Peat moss is in good condition. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | Dec 30 1899 12:55PM
09/21/2023 | Alternative |  | 15-160-0158 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | [9 empty] | [] | [] | [18 empty] | - our office has made numerous attempts to reach Ms. Seref regarding maintenance and maintenance agreements since May - unable to proceed with required inspections until we hear from customer | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/21/2023 | 12:00 AM
12/15/2023 | Alternative | RoutineScheduled | 027-STS-17798 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/15/2023 | 12:00 AM
07/17/2023 | Alternative | Routine/Scheduled | 550-STS-6587 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 2:00PM
03/23/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [8 empty] | 03/28/2023 | Sample Chamber | 12.000000 |  |  | 14.200000 |  |  |  |  | Replaced Blower Switch only | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Dec 30 1899 11:35AM
07/18/2023 | Alternative | Routine/Scheduled | 159-07-230 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Serviced Pura-Flo. Pump, floats, and alarms all good. Peat moss is good - raked it out. Lots of roots in all 4 pods. Cleaned filter in the septic tank. The septic tank does not need pumping. The timer is set to 2 minutes on 2 hours off. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | 12:00 PM
05/11/2023 |  | Reportable Incident | 05-120-0329A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | Excavated distribution box - replaced header lines - removed several feet worth of roots from absorption lateral as noted in previous inspection report. Restored system to proper operation - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | Jan 1 1900 10:30AM
11/27/2023 | Alternative | Routine/Scheduled | 07-163-0225 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | annual maintenance: -Septic Tank: At normal level Has 3" of solids with 3" of sludge Pulled and cleaned rsv -Recirculation Tank: At normal level Has 6" of sludge Pulled and cleaned pump, floats and filter Pump and floats are aged -Discharge/Pump Tank: At normal level Has 2" of sludge Pulled and cleaned pump Pump and floats are aged -Media Sheets: Lid and strut intact Sheets in good shape Brushed and flushed laterals, sprayed off sheets -Control Panel: Panel is from 2007 Working properly Recirc pulling 12.03amps Discharge pulling 12.35amps -Distribution Box: Dbox just below grade In good shape At normal level -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | Dec 30 1899 12:38PM
10/19/2023 | Alternative | RoutineScheduled | VAG400175 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/19/2023 | 12:00 AM
07/03/2023 | Alternative | RoutineScheduled | 2019-143-0008 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/03/2023 | 12:00 AM
01/02/2023 |  |  | 06-113-249 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/02/2023 |  | 2.540000 |  |  | 1.100000 |  |  | Will be sent separately |  | BOD: 2.54 TSS: 1.10 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2023 | 12:00 AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0054-SWT | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens"] | ["Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend treating the area around the Puraflo modules for ants. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
02/24/2023 |  | RoutineScheduled | 03-137-0274 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/25/2023 | 12:00 AM
01/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | Best 1 | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/06/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Fuji | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
08/03/2023 | Alternative | Pump-Out Only | 08-172-0028A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | EcoPod |  | Pump | Pressure | Drip | Not Applicable |  | SludgeScum Accumulation | SludgeScum Accumulation | N/A | [16 empty] | Pumped Out | Completely pumped out the sludge in the pump tank. Pumped sludge in the ecopod unit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/03/2023 | Dec 30 1899 2:01PM
10/14/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 1300 | BioMicrobics MicroFast |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 6" of accumulated solids in septic tank. 22" of solids in treatment unit. 4" of solids in discharge pump tank. Cleaned blower air filter. Adequate aeration. Cleaned drip manifold spin filter. Flushed drip field through air releases. Tested floats, pump and alarms. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 07:03 PM
09/13/2023 | Alternative | RoutineScheduled |  | Madison | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Rappahannock-Rapidan | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | aerator replaced 10/2/23 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/13/2023 | 12:00 AM
11/06/2023 | Alternative |  |  | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Battletown Environmental Consulting, LLC | 1942001135 | Robert | Charnley | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/08/2023 | Alternative |  | 177-06-0287-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled | 041-STS-261377 | Chesterfield | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chesterfield | Septic Pro of Virginia | 1942001780 | Eric | Tambourine | 1.000000 | 1300 | Norweco Singulair 960-500 | Norweco HKBFR | Pump | Gravity | Discharge | UV | 300.000000 | ["BlowerCompressorAerator Operation","Disinfection","SludgeScum Accumulation","Attached Growth Medium"] | ["BlowerCompressorAerator Operation","Disinfection","SludgeScum Accumulation","Attached Growth Medium"] | NO | Musty | Cloudy | 7.200000 | 3.400000 | 50.000000 | [10 empty] | Will be sent separately | Pumped Out | Lab samples were not collected at this time due to high settleable solids/low dissolved oxygen in the HKBFR and pump station. We believe the solids are residual from the original COSS. Solids were removed from the septic compartment, HKBFR, and pump station. Samples will be collected on or near 2/27/24. The aerator aspirator was cleaned. The UV was coated with scum, cleaned. Wire was loose at UV circuit board, reconnected and returned to function. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 01/17/2024 | 12:00 AM
08/29/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0062 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Completed annual inspection and maintenance. All ARV valve box lids were covered by grass, took a bit to find them. Zone 2 check valve would not seal, caused a high drip rate on the other 2 zones (due to double dosing). Dug up and replaced zone 2 check valve, retested rates. Recommend a pumping of the Microfast septic tank early next summer (5 years since the system has been in operation). Sampling will be due as well. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/10/2023 |  | RoutineScheduled | 14-100-0282 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 17.000000 | 12750 | ECOFLO |  | Pump | Gravity | Mound | Not Applicable | 2400.000000 | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | YES | [17 empty] | CLEANED FILTER. PEAT LOOKS GOOD IN ALL 4 ECOFLOS. PUMPS AND ALARM WORK. REHUNG ALARM FLOAT. PUMPED AT THE FOLLOWING ADDRESSES: 8254 SEASHELL DRIVE 8248 SEASHELL DRIVE 8281 SEAGULL DRIVE 8261 SEAGULL DRIVE 8273 SEAGULL DRIVE 8285 SEAGULL DRIVE | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/17/2023 | 09:15 AM
06/05/2023 | Alternative | RoutineScheduled | 154-18-0177 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 1500 | Pura Sys |  | Pump | Gravity | Pad | Not Applicable |  | [] | [] | NA | Musty | Clear | [14 empty] | Inspected | Sludge Scum - Septic 12", Pump Chamber 4" D-Box Re-Timed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
04/27/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 6" of solids in recirculation portion of treatment unit. 12" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 07:03 PM
04/17/2023 |  |  | 07-142-0150 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 12:00 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-10-0229-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 07:22 AM
07/12/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  |  | None | None | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 03:09 PM
03/30/2023 | Alternative | Reportable Incident | 073-STS-105152 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced failing DBox with new 8 port concrete DBox Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 06:30 AM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | 182-09-0015 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 09/11/2023 |  | 5.000000 | [5 empty] | Will be sent separately | Inspected | filter clogged sandfilter clogged Replaced sandfilter pump | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
05/17/2023 | Alternative | Routine/Scheduled | 800-02-0490 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Dec 30 1899 9:30AM
01/05/2023 |  | RoutineScheduled | 175-02-0518 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 02:21 PM
01/31/2023 |  | Follow-Up | 550-STS-6632 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/31/2023 |  | 4.000000 |  | 1.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 9:25AM
10/11/2023 | Alternative | Reportable Incident | 033-06-0026-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Other"] | ["Other"] | [17 empty] | Inspected | repaired broken pipe | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 01:00 PM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0436 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Numerous problems encountered. One tank lid missing and no hardware or locks to secure the lids. Lid was later located and proper hardware/ locks added. Tank was actually in high level and the blower was not running (locked up), but the control panel was not indicating any alarms. Alarm floats had been raised, presumably to reduce the number of alarms. A steady of inflow was seen coming into the tank (1 reason for alarms) and was later traced to 3 running toilets. All floats were narrow angle mercury floats which are too sensitive for turbulent effluent. Two of the floats had failed. Installed new mechanical float switches and adjusted to proper levels. Replaced the j-box terminal strip with grounds (existing one was badly corroded). Another operator erroneously installed a Zoeller E161 (wrong pump) and placed it on the bottom of the tank where it would be prone to sucking up waste and debris and pushing sludge to the filterbed. Installed a Goulds 1DW51C1EA (per plans) and braced the piping to support the weight of the pump (suspended, as per plans). Installed new Gast blower and new air filter. Observed heavy aeration in spots. Tank needs to be pumped and manifold/ diffusers replaced. Sanitary tee and drip leg missing from tank. Rodent guards missing from vent pipes on filterbed. Owner has tentatively agreed to these additional maintenance needs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
03/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2024 | 05:34 PM
04/05/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-14089 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/18/2023 |  | Routine/Scheduled | 550-STS-6507 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 10:25AM
07/11/2023 | Alternative | RoutineScheduled |  | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | sand filter | Gravity | Pressure | Discharge | Chlorination |  | [] | ["Auxiliary Filter","Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/02/2023 | 08:30 AM
09/18/2023 | Alternative | Reportable Incident | 147-11-0036 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | 9/18 Alarm Call: -Found system already in higher level due to ground water. Pulled and cleaned the aspirator, discharge pump and filter. The discharge pump was pulling 40amps and causing the breaker in the house to trip. Dennette approved for us to replaced the pump under manufacturer warranty and paid the warranty exchange fee. Installed the new p20 pump and confirmed everything was working without any issues. Also removed the breaker panel cover and confirmed everything was tight and had proper power. 9/27 Supervisor Visit: -Customer stated alarm was going off but was silenced and had not light Found discharge tank above normal Level Panel in silence and bulb burnt out Pump screen was clean and discharge filter was clean. Checked that water was making it to drip field by removing vacuum breaker. Water Sprayed about 10ft high. Was able to return system to normal level before departure Pump was just pumping slow bc field is extremely over loaded | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/05/2023 | Dec 30 1899 3:26PM
07/28/2023 | Alternative |  | 18-100-0018 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
04/12/2023 |  | Routine/Scheduled | 085-STS-33173 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. The septic tank needs to be pumped out and pump the sludge from the Clearstream when doing so. The Clearstream needs a 12" x 20" riser and lid. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | Jan 1 1900 11:00AM
08/14/2023 | Alternative | RoutineScheduled | 027-STS-15561 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 14 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/14/2023 | 12:00 AM
04/17/2023 |  | RoutineScheduled | 177-STS-89493 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
10/18/2023 | Alternative | Routine/Scheduled | 09-118-0045 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank Pump station: At normal level Pump and floats working properly -Discharge/Pump Tank: At normal level Pump functioning properly Has 2" of sludge -Aeration: At normal level Has about 13" of sludge may need pumping next year -Air Pump/Blower: Blower is working Pulled and cleaned filter -Control Panel: Panel is working properly, is a couple years old -Distribution Box: Dbox located by the tractor shed At grade and at normal level No signs of root intrusion -Drain Field: No signs of surfacing or blowouts | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 11:35AM
02/05/2023 |  | Routine/Scheduled | 041-STS-259928 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/05/2023 | Jan 1 1900 10:30AM
05/22/2023 | Alternative | RoutineScheduled | SD-10-315 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | 05:00 PM
03/14/2023 | Alternative | RoutineScheduled | SD-14-263 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Annual inspection. Recommend moving bush/tree that is growing right up against the septic tank. Roots could cause a problem. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 12:49 PM
10/09/2023 | Alternative | RoutineScheduled Component Maintenance | 182-18-0025 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
02/13/2023 |  | RoutineScheduled | 07-113-265 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Drip | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Auxiliary Filter","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 12 Dechlorine | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 12:00 AM
07/14/2023 | Alternative | RoutineScheduled | 075-STS-33993 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Advantex |  | Pump | Gravity | Trenches | UV |  | ["None"] | ["Auxiliary Filter"] | NA | Musty | Clear | 6.000000 |  |  |  | Temp 25c, Nitrate 1.5/18 | [9 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | Dec 30 1899 9:30AM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance | SD-06-27 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Noticed extra copper showing on neutral connection in control panel. Pushed loose wire up into terminal strip and tightened the screw. Owner had septic issue a couple of weeks ago and ended up pumping the septic tank. (Local pumper, possibly Septic Clean in Manassas). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/19/2023 | Alternative | Routine/Scheduled | 800-11-0009 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 12:05PM
11/10/2023 | Alternative | RoutineScheduled Component Maintenance | SD-14-87 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 3.09 amps. Media clogged, needs chemical cleaned. will send proposal. Recommend installing a sanitary T in D-box to slow down flow and to make it more even. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
08/03/2023 | Alternative | Pump-Out Only | 06-142-0456 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 750.000000 |  | Attached Growth Medium | NO | [17 empty] | Used vacuum truck to remove spent peatmoss biofilter media for Old Dominion Onsite - ODO is the service provider for the property - contracted with Millers Services for Vacuum Truck Services. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | Dec 30 1899 9:30AM
08/31/2023 | Alternative |  |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/05/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | New air blower installed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/26/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Cleaned recirculation pump basket filter. 10" of solids in discharge pump tank. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/24/2023 | 07:03 PM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance | SD-13-153 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
11/30/2023 | Alternative | RoutineScheduled | VAG408315 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.910000 |  |  |  |  | 11/30/2023 |  | 37.000000 |  |  | 6.100000 |  |  |  |  | BOD over limit, sludge at 80%- recommended pumping. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/15/2023 | 04:20 PM
11/15/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 10:06 AM
06/12/2023 | Alternative | RoutineScheduled | 132-06-0053 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Discharge | Chlorination | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES |  |  | 7.300000 | 6.700000 |  |  |  | 06/12/2023 | Pump Chamber | 9.000000 | 2.200000 |  | 7.430000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 12:00 AM
04/08/2023 |  | RoutineScheduled | 067-STS-38687 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | BioMicrobics MicroFast |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | First Quarter 2023 inspection. 8" solids in septic tank. 12" solids in MicroFast septic tank. 12" in treatment unit. 0" solids in discharge pump tank. Aeration is adequate. No sign of smell that has been an issue. Cleaned blower air filter. There is no pump out required at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 07:03 PM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/10/2023 | Alternative | Routine/Scheduled | 041-STS-257860 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/10/2023 | Dec 30 1899 4:18PM
01/17/2023 | Alternative | RoutineScheduled | SD-13-490 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Ecopod | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 01/17/2023 | Sample Chamber | 9.000000 | [5 empty] | Attached to this report |  | Septic-4"sludge 0"scum/ Ecopod-6"sludge/ Pump Tank-3"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-5235 ETM-1172h 39m/ Peak-2366 ETM-165h 12m/ Water Meter- 356,491.46/ No breakout or spongy areas on the drip field and dosing properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/05/2023 | Alternative | Initial Visit |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - told the owner to check for running toilets. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1 minute every 2 hours. Need to take samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Dec 30 1899 2:45PM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20175 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. Needs new UV unit. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/15/2023 | 01:44 PM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend replacing discharge pump chamber lid. Peat is showing signs of its age. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/13/2023 | Alternative | Routine/Scheduled | 166-02-472 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | 9/13 Annual Maintenance: -Septic Tank: Normal level 5in of sludge and less than 1" of solids Pulled and cleaned filter Riser is leaking -Discharge/Pump Tank: Normal level Pulled and tested floats working properly however floats are aged Pump pulled 7.6 amps Direct disconnect had 120v No signs infiltration -Peat Moss: Dispersal trays and tipping bucket are intact Raked peat moss out Peat moss completely saturated and broken down 9/18 Install: -Installation of 6"-12" Riser on the Septic Tank -Install A300 Filter 9/18 Install and pump: -Pumping of system for Peat Change -Install A300 filter 9/21 Peat Replacement: -Replacement of Ecoflo Biofilter - includes: - Purchase & delivery of new Biofilter (specialty peat moss) - Pumping of Septic Tank - Removal of existing Biofilter using a specialty Vacuum Truck - Disposal of existing Biofilter - Installation of the new Biofilter | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | 03:02 PM
11/17/2023 | Alternative | Reportable Incident | 124-STS-2379 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to having some problems. Serviced system. Cleaned the filter in the Clearstream and cleaned the disc filter. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a new P-20 pump (new serial # 2203-134261), installed a new alarm float, installed a new alarm light bulb, and installed a new UV light bulb. Meet with the pumping company and pumped the Clearstream tank out and the pump tank. The timer is set to 8 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/07/2023 | 11:00 AM
08/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/13/2023 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - effluent screen serviced. BioFilter - peatmoss in good condition. Pump Basin - float sensors, pump and controls operating.DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 9:15AM
04/25/2023 |  | Reportable Incident |  | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 4.000000 | 9000 | None | None | Pump | Pressure | Trenches | Not Applicable | 4000.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | Chased addition points of leakage. Found "T" where manifold splits serving two absorption fields - 2 fernco unions present and leaking. Found Valve box - tree growing next to it - and valve leaking. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/26/2023 | Jan 1 1900 12:15PM
05/23/2023 | Alternative | Initial Visit | 073-STS-97109 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Gloucester Sheriffs office contacted us in regards to the alarm going off. We were then able to get in contact with the owners. Serviced system. Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the aerator. Re-wired floats. The UV is not working - tube assembly cut too short to attach union. Bottom button "alarm test" mutes alarm. The timer is set to 1 minute 4 seconds every 2 hours. Did not take samples. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/23/2023 | 12:00 PM
11/29/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 8.170000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 01:50 PM
03/27/2023 |  | RoutineScheduled | 181-10-0056 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 4.000000 | 4000 | Ecopod | Biomicrobics MicroFAST | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. Panel boxes all functioning properly. No apparent leaks in system or drain field area. Pumps functioning properly. Lids were properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 08:50 PM
03/28/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | pod 1 nearest driveway ponding | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
01/24/2023 |  | RoutineScheduled | 179-12-0250-SRWR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. We were getting multiple alarms and alerts for this system over the past month. While on site circuit board would not respond at all. Replaced board. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
05/10/2023 | Alternative | RoutineScheduled | 11-100-0320 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 3.000000 | 9000 | Septic Tank | EcoPod | Pump | Gravity | Trenches | Not Applicable | 3000.000000 | ["None"] | ["None"] | YES | [7 empty] | 05/10/2023 | Pump Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:30 PM
12/20/2023 | Alternative | Reportable Incident Component Maintenance | 099-STS-87654 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Pressure | Drip | UV |  | ["Control Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Recirc alarm going off due to water in junction box, vacuumed water out and drilled small hole on box above ground to help drain also replaced all wire nuts and added electrical grease to prevent corrosion. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/13/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/13/2023 | Dec 30 1899 11:06AM
06/15/2023 | Alternative | Reportable Incident Component Maintenance | 099-10-0043-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Replaced top 6" riser and lid on pump tank broken by mower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance | SD-14-260 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [7 empty] | 05/17/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 07:43 AM
08/18/2023 | Alternative | RoutineScheduled | 182-19-0082 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex RT |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | [18 empty] | Effluent filter replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 12:00 AM
07/03/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-307 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Water level in recirc tank was 6 inches below the rsv. Recirc tank needs to be pumped out due to sludge levels and tank inspected at this time. Tank possibly has a crack in it. Will follow up to video Rsv drain line. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
09/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/Ecopod Tank | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation"] | NA | [17 empty] | Septic Tank-3" sludge 1"scum/ Ecopod Tank- 3"sludge/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower is faulty and requires replacement/ UV Light is faulty and requires replacement/ Slight leak in the hydraulic unit needs repair/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-9043 ETM-1374h 58m On-9m 30s Off-3h Peak off-1h 48m/ No breakout or spongy areas on the drip field. Returned on 11/22/2023 and replaced the .75 Ecopod Blower/ Replaced and installed a new Jet UV-Light/ Repaired existing hydraulic unit, tested and components are functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
12/02/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | None |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Meters - A - 950, B -680, C - 910. Control panel was tripped out. Reset backup power supply and control panel returned to normal operation. Most likely due to power issue. Tested both discharge pumps in "HAND", both pumping. Still no gallons pumped to drain field. Owner is looking into pressure testing the force main system again to look for leaks. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/12/2023 | 07:03 PM
04/12/2023 |  | Follow-Up | 179-12-0098-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank pumped out by others prior to peat replacement. Degraded peat was removed by hand with shovels/pitch forks and new peat was installed. Peat was purchased from Wrights Ready Mix. Degraded peat was disposed at Spotsylvania Refuse. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
12/07/2023 | Alternative | RoutineScheduled | 02-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-161 | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Dispersal System Operation"] | ["Effluent Screens" ,"Dispersal System Operation"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | The peat in the Ecoflo module is no longer providing treatment. During this inspection, there was water standing in the distribution box and above the drainfield lines. Because the soil was very saturated due to recent weather events, a follow-up visit during drier weather is planned. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/01/2024 | 07:56 AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
06/26/2023 | Alternative | Routine/Scheduled | 234-17-0174 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  |  | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | Dec 30 1899 1:35PM
11/10/2023 | Alternative | Reportable Incident Component Maintenance | -STS-90228 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for homeowner stating therew is a smell and aerator is not running due to wipe getting stuck in aerator. Replaced failed aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
11/20/2023 | Alternative | Reportable Incident | 136-05-0352 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Came out for alarm call. found panel was not working and floats were aged. repaired on 11/27 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/05/2023 | 02:15 PM
08/31/2023 | Alternative | Routine/Scheduled |  | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - normal level - RSV, recirc pump, effluent screen serviced. Treatmet Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. LPP field - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 11:00 AM
02/27/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Norweco Singulair ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/01/2023 | 11:58 AM
11/01/2023 | Alternative | Routine/Scheduled | 151-11-0055 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | Ecoflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 05:40 PM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0518 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"SludgeScum Accumulation" ,"Level Sensor Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | On site for annual inspection and to investigate a high level alarm (both panels). Very heavy rain late yesterday, alarm started around 7 this morning. Minor infiltration observed at riser joints, recommend reseal all. Also observed a slow but steady drip at force main boot in pump tank. Owner checked toilets, said none running. Water level elevated in Microfast tank due to clogged media. Timer float stuck on for a few minutes during testing. Recommend replace because the next time it might stick off and cause an alarm. Symptoms suggest check valve closer to the tanks (zone 2) is not closing properly, recommend replace. The 10" valve box lid is also damaged from lawn mower. A puddle of effluent formed around zone 1 ARV when running test cycle. Need to dig up and see what is leaking. A repair proposal will be sent to the owners. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 4.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/11/2024 | 01:04 PM
07/05/2023 | Alternative | Follow-Up Component Maintenance | SD-11-18 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Replaced worn recirc PF15 pump that was struggling to put out enough water with a PF30. Big improvement in flow from the spinners (spray nozzles). Increased rest time by 1 minute due to the increased flow rate. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
07/18/2023 | Alternative | Routine/Scheduled | 234-13-5 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs to be pumped out. The timer is set to 8 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 3:00PM
01/19/2023 | Alternative | Routine/Scheduled | 166-02-147 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | 07:16 PM
07/28/2023 | Alternative | Reportable Incident | BMOE-BAWKT8 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter (ball valve on return in septic tank was stopped up). The timer is set to 8 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | Dec 30 1899 11:00AM
01/16/2023 | Alternative | Initial Visit | 127-STS-34068 | New Kent | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | The contractor called due to some problems. Serviced system. Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. There is an Orenco panel as well as the Clearstream panel on this jobsite. The Orenco panel is having problems - it is alarming and the buzzer is un-plugged. The Clearstream panel is working. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/16/2023 | Dec 30 1899 1:00PM
01/09/2023 |  | Routine/Scheduled | 550-STS-6587 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 |  |  |  | 01/24/2023 |  | 4.000000 |  | 1.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 2:45PM
10/25/2023 | Alternative |  | 033-06-0635-ST | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
09/15/2023 | Alternative | Reportable Incident | 228-18-0323 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/15/2023 | Dec 30 1899 2:00PM
07/05/2023 | Alternative | Routine/Scheduled | 175-17-0035 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  | 600.000000 | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/25/2023 | 01:01 PM
11/14/2023 | Alternative | RoutineScheduled | 019-STS-24961 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [17 empty] | Inspected | Routine inspection yearly inspection. 1 to 3 in old scum and trace new scum and 2-3" sludge in septic tank, trace sludge in recirc zone, 10 in sludge in discharge zone. System is operational. Alarm tested good. Flotas responding on control panel, Media is clean. Good spray. Cleaned effluent filter. No alarm in history - internet connected with monitoring. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
07/07/2023 | Alternative | Follow-Up Component Maintenance | 2088-04-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed public awareness sign. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 07/17/2023 | 12:46 PM
07/14/2023 | Alternative | RoutineScheduled | 166-17-040 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
05/04/2023 | Alternative | RoutineScheduled | 175-19-0168 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
02/02/2023 |  | Routine/Scheduled | 800-STS-14256 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 3:05PM
11/03/2023 | Alternative | Routine/Scheduled | 041-STS-260797 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/03/2023 | Dec 30 1899 3:56PM
03/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic and atu need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
04/16/2023 | Alternative | Routine/Scheduled | 149-STS-10455 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | Dec 30 1899 10:00AM
05/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 2000 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | Septic Tank-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ No counts or ETM readings on the control box/ Pump on time-9m Off-2h / Watermeter reading-0,962,265.4/ All 4 zone rates-5gpm/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/10/2023 | Alternative | Routine/Scheduled | 12-142-0214 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Compressor filter replaced. Tee weir and effluent filters were cleaned. Alarm responded correctly to compressor being shut down and when high water float was tested in pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | Dec 30 1899 11:13AM
08/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was not functioning upon arrival. Blower was replaced and the system should return to proper function | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/03/2023 |  | RoutineScheduled | 05-100-0828 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 2.000000 | 1000 | Ecoflo |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | Replaced Inner Part to Accordian Style Effluent Filter-Everything else functioning properly. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/06/2023 | 10:45 AM
03/14/2023 |  | Initial Visit | 107-12-0050 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 12:00 AM
06/16/2023 | Alternative | Routine/Scheduled | 149-STS-10590 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","None"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/16/2023 | Dec 30 1899 11:44AM
09/12/2023 | Alternative |  | 149-05-127 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
07/10/2023 | Alternative | Routine/Scheduled | 234-17-0051 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 10:45AM
04/14/2023 | Alternative | Routine/Scheduled | 800-11-0041 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | Dec 30 1899 2:10PM
01/20/2023 |  | RoutineScheduled | 14-113-135 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/20/2023 | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Puraflo Peat Moss |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Sludge level-Minimal scum-8" sludge in Septic tank- Pump tank - 4-6" light sludge. Cleaned Effluent filter- Opened and turned Peat moss in all 3 pods. Peat looks aged and is mostly dry on top 1 ft moist beneath turned and fluffled it. Alarm and pump are operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
07/13/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-315 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["SludgeScum Accumulation" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Peat was in good condition for its age. Timer was set to 1 hour off and 1:30 min on. Retimed pump to the designed rate. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
08/04/2023 | Alternative | RoutineScheduled | 17-160-0125 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Inspected | - repaired blower line - replaced blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 12:00 AM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator was not functioning upon arrival. It was replaced and is functioning as designed at this time. The effluent filter was very clogged and causing a high-level in the septic tank and possibly coming out the riser. Filter was cleaned and the lever returned to normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-18-0393-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/17/2023 | 09:07 AM
09/30/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Norweco |  | Pump | Pressure | Drip | Not Applicable | 175.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/01/2023 | 12:00 PM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/21/2023 | Alternative | RoutineScheduled | SD-04-176 | Culpeper | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1000 | septic | Puraflo | Gravity | Pressure | Discharge | Chlorination |  | [] | [] | YES | Pungent | Discolored | 7.000000 |  |  |  |  | 09/21/2023 | Sample Chamber | 12.000000 | 1.200000 |  | 35.000000 |  |  |  |  | Tss Failed | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/11/2023 | 10:00 AM
08/21/2023 | Alternative | Initial Visit | 107-09-0136 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2500 | Septic Tank Only | AdvantexAX20 | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filters were both cleaned. The textile sheets were sprayed off. The recirculating pump was pulled and sprayed off. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 03:05 PM
06/28/2023 | Alternative | Routine/Scheduled | 099-STS-92093 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 600 |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 09:30 AM
12/08/2023 | Alternative | Routine/Scheduled | 04-142-0407 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/08/2023 | Dec 30 1899 10:57AM
03/21/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Effluent Screens" ,"Disinfection"] | ["Effluent Screens" ,"Disinfection"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
11/07/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Blower is bad and needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/06/2023 | Dec 30 1899 10:06AM
11/02/2023 | Alternative | RoutineScheduled | 10-167-038 | Nottoway | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Retaw Engineering LLC | 1965008335 | Ginasiyo | Mutoti | 10.000000 | 60,000 | Settling Tank | Equalization/Pre-Anoxic | Pump | Gravity | Trenches | Not Applicable | 262.000000 | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | None | Clear | 6.900000 | 3.300000 | 1.000000 | 0.000000 | None | 11/02/2023 | Sample Chamber | 5.100000 | 0.000000 | 1730.000000 | 0.000000 | 32.620000 | 7.460000 | Attached to this report | Pumped Out | Date of Previous visit was incorrectly entered as 11/2/2023 instead of 10/2/2023 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | Dec 30 1899 1:40PM
08/15/2023 | Alternative | Reportable Incident | 800-STS-13197 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The Clearstream tank and the septic tank need to be pumped out. The timer is set to 2.25 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | Dec 30 1899 8:30AM
09/05/2023 | Alternative | RoutineScheduled | 175-19-0229 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Advantex |  | Pump | Gravity | Discharge | UV | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | NA | Musty | Clear | 7.800000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/19/2023 | 12:00 AM
12/20/2023 | Alternative | Initial Visit | 087-STS-6616 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Owner called due to having a yellow light on for 24 hours. There is no power to the UV. The pipe between the Clearstream tank and pump tank has settled needs to be addressed and/or fixed. There is an Orenco MVP panel (240 volts). The tanks need to be pumped and cleaned due to paint. Replaced the air house from the aerator to pressure switch and replaced the air filter. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/20/2023 | 12:00 PM
02/21/2023 |  | RoutineScheduled | 12-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/21/2023 | 12:00 AM
04/25/2023 |  | Routine/Scheduled | 234-17-475 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 11:30AM
10/13/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | septic | Puraflo | Pump | Gravity | Trenches |  |  | [] | ["Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | [18 empty] | Peat is ok. It may need replaced in the next couple years. very little use. 0 scum, 1" of sludge in septic tank. Pump tank is clean. Alarm& floats work. Field is dry. No sample box located. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 01:50 PM
11/01/2023 | Alternative |  | 033-18-0143-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/22/2023 | Alternative | Reportable Incident | 093-18-0138 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the system in high level. Checked and confirmed pump, floats, and control panel are functioning properly. Flushed and cleaned disk filter. Visually confirmed drawdown within discharge tank. Noted field return pressure was a out 8-10 psi. Cleaned vortex filter and adjusted field return pressure to about 15 psi. Field return pressure diminished after a couple minutes. Removed vortex filter and checked field return pressure with no issues. Confirmed vortex filter had became saturated with debris. Homeowner approved for a pump service on the 28th which includes a new vortex filter. I replaced vortex filter during this service and adjusted field return pressure to about 15 psi. UV system had dismounted and due to high water level and tight confines of riser I was unable to reset it. I turned off the UV system and removed it from within the discharge tank. The UV assembly is inside the homeowners garage and will need to be mounted back in the system during the pump out service 11/28: -Supervise Pump out and Refill -Meeting Ducks onsite at 9am -Meeting Davis water onsite at 10am - The UV assembly is inside the homeowners garage and will need to be mounted back in the system during the pump out service. William took it out when he responded to alarm call. William also already installed the vortex filter. -Installation of a Diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/06/2023 | Dec 30 1899 9:19AM
01/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/30/2023 | Alternative | Routine/Scheduled | S 800-16-0021 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Outlet tee appears to be intact. Not due for pump out. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Flushed and cleaned disk filter. -Aeration: Water level normal. Confirmed aeration. Not due for pump out -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 4:08PM
01/09/2023 |  | RoutineScheduled | 14-160-0165 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 0.000000 |  | Aqua Safe 500 |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Other"] | ["Other"] | NA | None | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 01:04 PM
10/19/2023 | Alternative | Follow-Up | 103-STS-95254 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm call: -Talked with customer and presented updated estimates for upgrade/repairs Repairs (10/26): -Installation of a Goulds Pump includes: - Removal & disposal of spent Pump - Manufacturer Warranty -Installation of 3 Floats Reseal the force main Pipe: - Manually excavate the exterior of the Tank up to 24" to access the force main Pipe - Parge the interior and exterior of the Tank around the force main Pipe - Backfill excavated area | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | 11:56 AM
09/26/2023 | Alternative | RoutineScheduled | 085-STS-34657 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 |  | MicroFAST |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
12/26/2023 | Alternative | Reportable Incident | 149-11-048 | King & Queen | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | ustomer stated alarm turned off two days after last visit but then came on again during last rain event I opened tank and found above normal Level It had pressure going out but not returning. I checked pump screen and filter and found them tombe dirty. Pulled and cleaned screen and Vortex filter. Put pump back in and Pump began moving water and field built pressure. There are signs of leaks in riser. I also noted the timer override float was connected and pump was running continuously I discussed with customer about disconnecting it to give drainfeild and pump a break and he said to disconnect it. 12/27/23: pumped and refilled system 12/27/23: Clearstream. Came out while it was raining to look for leaks. Found the aeration riser was leaking. Top 6" section of the discharge was leaking. The concrete around the forcemain needs to be redone and there are a couple screw holes in the bottom of the discharge riser that need to be sealed. Customer approved repairs | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/28/2023 | 08:08 AM
05/12/2023 | Alternative | Routine/Scheduled | 800-08-0118 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | Dec 30 1899 10:50AM
08/09/2023 | Alternative | RoutineScheduled | SD-11-389 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic tank | PuraFlo | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | Sulphitic | Discolored | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 08:00 AM
02/23/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 1.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/23/2023 | Alternative | Routine/Scheduled | 07-137-0030 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Cleaned effluent filter. Flushed manifold, spin filter and drip field. Brushed manifold. System appears to be operating normally. Averaged. 4 overrides per day. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | Dec 30 1899 2:57PM
10/12/2023 | Alternative | RoutineScheduled | SD-06-19 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 43.750000 | ["Attached Growth Medium","SludgeScum Accumulation","Dispersal System Operation"] | ["Attached Growth Medium","SludgeScum Accumulation","Septic Tank Baffles"] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 11:00 AM
12/03/2023 | Alternative | Reportable Incident | S 093-19-0058 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the control panel in alarm condition. Recirculation tank was a couple inches below high level. Discharge tank was in normal level. Checked floats and found that recirculation high level alarm float had failed in the "ON" position. Homeowner gave written approval to replace faulty float. Replaced recirculation high level alarm float while on site. Checked and confirmed float was functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 9:16AM
02/27/2023 |  | Reportable Incident |  | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | ["Control Operation","Distribution Pump Operation"] |  | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/29/2023 | 01:51 PM
01/16/2023 |  | RoutineScheduled | 177-STS-88914 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/02/2023 |  | Routine/Scheduled | 800-08-0190 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 1:01PM
05/04/2023 | Alternative | Reportable Incident | 061-STS-24826 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Panel alarmed twice today. Recirc tank at normal level and correct led's showing on the motherboard. The discharge tank was barely in a low level condition, but the led's indicated the top float was up and the bottom two floats down. DC voltage at terminal strip was not right for any of the discharge floats. Removed all 3 Connery float switches and installed 3 Orenco float switches instead. Added a little water back to get the tank out of low level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/10/2023 | 05:56 AM
11/13/2023 | Alternative |  | 033-13-0086-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/03/2023 | Alternative | Routine/Scheduled | 800-10-0284 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Dec 30 1899 10:50AM
11/04/2023 | Alternative | RoutineScheduled | 109-07-0907 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 18" of accumulated solids in septic tank. 10" of solids in discharge pump tank. Flushed treatment unit spray manifold. Cleaned recirculation pump solids basket filter. Sprayed solids off of treatment unit "sheets". Tested floats, pumps and alarm. Excellent treatment quality. Getting close to septic tank pump out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2024 | 07:03 PM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
03/30/2023 |  | Reportable Incident | 234-13-319 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/30/2023 | Jan 1 1900 2:00PM
11/28/2023 | Alternative | RoutineScheduled | 175-17-0348 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Ecopod ATU | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 4"scum/ Ecopod- 4"sludge 0"scum/ Pump Tank-4"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower functioning properly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-8218 ETM-1852h 47m/ High-999999 ETM-12h 24m/ Watermeter-0,701,637.48/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-14725 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 5.000000 | 6.000000 |  | -1.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 107-18-0290 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | venmo paid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
07/19/2023 | Alternative | Reportable Incident | 107-98-0188 (LEGACY ALT. SYSTEM) | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","Dispersal System Operation","Other"] | ["Control Operation","Dispersal System Operation","Other"] | NA | Septic | Discolored | [15 empty] | control box was replaced by previous owner , made new float tree replaced control box. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/19/2023 | 12:00 AM
03/24/2023 |  | Routine/Scheduled | 234-17-175 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/24/2023 | Jan 1 1900 12:05PM
09/26/2023 | Alternative | RoutineScheduled | 15-163-0054 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | EcoPod |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
02/17/2023 |  |  | 085-STS-31719 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 12:00 AM
05/15/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | NA | [16 empty] | Inspected | Septic Tank 1" scum and 6-8 "in sludge, Recirculation zone trace of scum 5"sludge and discharge 6" sludge, Cleaned effluent filter, Cleaned septic tank effluent filter, Discharge pump run time 0.5 hours and 168 cycles. Recirc pump run time 9.8 hours and 5,042 cycles count. System jjust began to trend data 13 days ago, No alarms or alerts in history. Memory is possibly corrupted. it took about 3 -4 years to trend data and go into normal mode from startup. No recent alarm in history but date is corrupted- System is fully operariotnal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/12/2023 | Alternative | RoutineScheduled | 181-05-0420 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | SEPTIC TANK ONLY | ADVANTEXAX20 | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | THE SYSTEM DID NOT NEED TO BE PUMPED. THE EFFLUENT FILTER WAS PULLED AND CLEANED. THE RECIRCULATING PUMP WAS PULLED AND SPRAYED OFF. THE TEXTILE SHEETS WERE CLEANED. THE LATERALS WERE CLEANED. THE CONTROLS WERE OPERATING AS DESIGNED. THERE WERE NO VISIBLE LEAKS IN THE LEECH FIELD. THE LIDS WERE SECURED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 01:25 PM
06/08/2023 | Alternative | Routine/Scheduled | 166-18-007 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss in good condition - raked / turne. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 01:00 PM
05/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Advantex tank needs pumped out and the sheets need to be cleaned a lot of bridging. Also trees and bushes need trimmed around tanks | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/17/2023 | 12:02 PM
09/08/2023 | Alternative | Routine/Scheduled | 228-17-0144 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 11:55AM
05/23/2023 |  |  | 13-142-0066 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecopod | [6 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | Recommended pumping the grease traps as soon as possible | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled | 109-13-0076 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge level- Septic tank 1" scum and 8" slduge- 20-30" slduge amount of sludge in treatment, Good aeration, Discharge tank 4" sludge- cleaned airfilter. Good aeration. Cleaned Effluent filter. System is operational pump run time 75hr 56 min and 921 cycles, water meter reading 216,910, Flushed filter and drip while running pump in test. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
04/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/19/2023 | Alternative | RoutineScheduled | 150-08-0252 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Septic Service | 1942001039 | Corey | Braxton | 7.000000 |  | Puraflo |  | Pump | Gravity | Mound |  |  | [] | ["Attached Growth Medium","Distribution Pump Operation","Control Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Rejected | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The cover is missing from the push to silence button and the audible alarm horn is not working. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | 08:44 AM
09/08/2023 | Alternative | RoutineScheduled | 16-120-0400AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 2750 | 1000 | 1000 | Pump | Pressure | Discharge | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Pungent | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
06/21/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-5438 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced discharge pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/21/2023 | Dec 30 1899 3:30PM
02/02/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Micro Fast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 2" scum, 12" of sludge in septic tank, 8" of loose sludge in fast side,2" of loose sludge in pump tank. Return pressure at 10 changed to 30. Drip field is grown up didn't find air valves, but did walk it and no signs of leaks. Alarms working, blowers working, Cleaned filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 12:30 PM
02/28/2023 |  | RoutineScheduled | 132-06-0056 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
06/13/2023 | Alternative | RoutineScheduled | 101-13-0186 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Wet Land |  | Gravity | Gravity | Discharge | UV | 450.000000 | [] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA |  |  | 6.800000 |  |  |  |  | 06/13/2023 |  | 28.000000 |  |  | 9.550000 |  |  | Will be sent separately |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 12:00 AM
01/24/2023 |  | RoutineScheduled | 170 92 098 | Patrick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | NONE, Low Pressure System |  | Pump | Pressure | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Annual inspection. 14" of solids in septic tank. 0" in pump tank. Low pressure lines flushed. 4" of accumulated solids in discharge pump tank. Very clear effluent. Septic tank and discharge pump tank may need to be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 07:03 PM
01/23/2023 |  | RoutineScheduled | 179-07-0276-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | ["Recirculation Pump" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection and maintenance completed. Septic/ recirc tank needs pumped out. Will provide an estimate to the owners. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
08/17/2023 | Alternative | Reportable Incident Component Maintenance | 061-STS-24855 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Intermittent alarms for about a month, Vericomm panel. Observed recirc contactor chattering when beginning an automatic cycle. Owner noticed that it never happened when running the recirc pump manually with the switch. Checked for loose wire connections at the contactor and terminal blocks, none found. Discussed with Orenco regional tech rep and agreed that most likely there was a problem with the input or output pump relay on the motherboard. Replaced the motherboard and adjusted settings to match old board. Owner to report any new alarms. Effluent was up into the riser in the septic tank. Nudged effluent filter slightly and waited for level to drop, cleaned very dirty filter. Also cleaned disc filter for the drip system. Recirc high level float was not registering in the control panel. Repaired loose wire connection in Orenco splice box. Control panel recorded just 51 discharge pump cycles in the past 30 days. This low water use has allowed drip field to firm up. No wet spots seen after test cycle, no soggy ground anywhere. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 182-15-0007 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 10/10/2023 |  | 13.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
10/30/2023 | Alternative | RoutineScheduled | 193-STS-95970 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001527 | Jacob | Hott | 1.000000 | 1250 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/12/2023 |  | RoutineScheduled | 175-14-0332 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
12/07/2023 | Alternative |  | ST-05-495 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/07/2023 |  | RoutineScheduled |  | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 02/07/2023 |  | 52.000000 | [5 empty] | Will be sent separately | Inspected | old timer upgraded blower not operating was replaced new blower, blower panel, timer | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
04/06/2023 |  | RoutineScheduled | SWP-99-768 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Corrected atu alarm by replacing diaphragms on air pump. Replaced the air filter. Owner removed ornamental grass from around tanks (yay). Atu vent now visible, but pretty close to grade. Recommend raising the vent by 7" to 8". | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
08/08/2023 | Alternative | RoutineScheduled | GNEL-AEVMDR | Mecklenburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Southside |  | 1942001570 | Eric | Tollerson | 1.000000 | 500 |  |  | Gravity | Pressure | Drip | Not Applicable | 250.000000 | ["BlowerCompressorAerator Operation","Other"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Other"] | NA | None |  | 6.100000 | 6.300000 | 60.000000 | [11 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 PM
01/06/2023 | Alternative | Initial Visit | 151-19-0048 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Aqua Klear |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - unknown if required lab samples obtained. Trash Tank - normal level Aeration Tank - normal level - mixing restored - Compressor has wiring issues but is operating. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 10:00 AM
11/30/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Flushed and cleaned effluent screen. Not due for pump out. -Discharge/Pump Tank: Water level normal. Structural integrity of tank appears to be intact. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. -Peat Moss: Structural integrity of tank appears to be intact. Structural integrity of tipping bucket appears to be intact. Checked and confirmed tipping bucket is functioning properly. Raked and tilled peat moss. Peat moss is in good condition. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. Removed root infiltration. -Drain Field: Found no signs of surfacing on dispersal field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 4:06PM
10/13/2023 | Alternative | Routine/Scheduled | 800-09-0030 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | Dec 30 1899 11:20AM
02/27/2023 |  | RoutineScheduled | 177-STS-89536 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Plumbing in the hydraulic unit is cracked and broken to the point we recommend replacing the hydraulic unit. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
06/30/2023 | Alternative | Routine/Scheduled | 03-160-0060 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 09:00 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 099-06-0342-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment nice and clear. Blower 3.96 amps. 3 trees growing on mound, marked them and spoke to customer and she agree to take them down. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:55 PM
03/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/11/2023 | Alternative | Routine/Scheduled | 093-06-0329 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | Dec 30 1899 10:45AM
10/31/2023 | Alternative |  | 001-STS-92314 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
09/22/2023 | Alternative | Follow-Up Component Maintenance | 175-13-0286 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | Follow-up visit to address deficiencies identified in June. Raised compressor base 2" to accommodate for settling, then replaced the compressor (with new air filter). Replaced the alarm horn, bulb, mute switch, and rubber boots for both switches in the atu control panel. Reattached 6" vents to the compressor housing to avoid another battle with wasps inside. Replaced the plastic lid for the zoner valve box. Note: owner says septic tank and pump tank were pumped out a few weeks after the June service call. Septic odor should be gone in a few days. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
04/12/2023 |  | RoutineScheduled | 157-03-021 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/08/2023 | Alternative |  | {FIPSCode}-STS-15815 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens","Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 04:00 PM
02/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/30/2023 | Alternative | Routine/Scheduled | NYII-AYTJT3 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 10:37AM
01/23/2023 |  |  | 124-STS-2379 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | Virginia Soils Inc, dba VSI Supply / AG Onsite | 1942001291 | Archie | Arnold | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
12/20/2023 | Alternative |  | 14-142-0051 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | 175-09-0420 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
05/02/2023 |  |  | 05-184-5001 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/02/2023 |  | 3.620000 |  |  | 14.600000 |  |  | Will be sent separately |  | BOD: 3.62 TSS: 14.6 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 12:00 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | water meter-669.13 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
09/21/2023 | Alternative | RoutineScheduled | 04-197-A18 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Pungent | Cloudy | 6.000000 | 0.000000 | [13 empty] | Aerator is not running no tables in the chambers. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/19/2023 | Alternative | Routine/Scheduled | 15-163-0004 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal level 4 in of sludge 1 in of solids No signs of infiltration -Discharge/Pump Tank: Normal level 12 In if suspended solids Tested floats and pump all working as should Return line intact and properly working Pulled and cleaned spin filter All plumbing intact and pump properly moving water No signs of Infiltration -Aeration: Normal level 14 in of suspended solids Pulled and cleaned weir Pulled and cleaned diffuser Air line intact was not working due to air pump not functioning Air line now working because or air pump replacement Recommend pumping No signs of infiltration -Air Pump/Blower: Arrived on site was in alarm due to air pump not working Replaced air pump on site functioning properly now Air pump pulled 1.4 amps -Control Panel: 120 volts coming in Audible alarm is working alarm light was not working Replaced light on site now functioning properly Pump pulled 9.7 amps Otherwise all other components working properly -Drip Field: No signs of surfacing Repair: -Installation of a rebuilt Clearstream Compressor -Replace burnt out light bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | Dec 30 1899 1:16PM
02/21/2023 |  | RoutineScheduled | 18-100-0069 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AquaSafe |  | Pump | Pressure | Mound | UV | 900.000000 | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [17 empty] | Pumped Out | Installed new sewage pump and replaced 3 control floats and wire between panel and pump station. Pumped out to be able to do the repair. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/29/2023 | 09:40 AM
06/06/2023 |  | RoutineScheduled | 133 04 1026 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | BioWheel |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | May 2023 monthly report. Total flow for month of May 2023 - 60,012 gallons. Average daily flow - 1,936 gallons | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 07:03 PM
07/13/2023 | Alternative | Reportable Incident | 234-08 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Control Operation | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Alarm Found control panel motherboard faulty - replaced while on property. Processing tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | Dec 30 1899 7:15AM
02/11/2023 |  |  | 2125-08-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | UV |  | ["Disinfection","Dispersal System Operation","Level Sensor Operation"] | ["Disinfection","Dispersal System Operation","Level Sensor Operation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/26/2023 | Alternative | Reportable Incident Component Maintenance | 179-STS-87443 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to a high level float failing sending a false alarm to the panel. Replaced high level float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
02/08/2023 |  | RoutineScheduled | SWP-04-275 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. concrete lid on septic tank starting cracking but still solid will check next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
03/29/2023 |  | RoutineScheduled | SWP-05-389 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 2-3 0-3 | 0-1 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 9.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 11:00 AM
08/25/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 3750 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Processing Tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - minor root infiltration present - removed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 1:00PM
12/05/2023 | Alternative | RoutineScheduled | VAG408395 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | 01:45 PM
02/06/2023 |  | Initial Visit |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 12:00 AM
04/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation","Control Operation","BlowerCompressorAerator Operation"] | ["Control Operation","BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [17 empty] | Septic Tank-8"sludge 6"scum/ Microfast-6"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Alarm buzzer and Off Float replaced/ Controls, pumps, floats and alarms now functioning correctly/ Blower air filter cleaned and blower is working correctly/ Counts: Pump1-177 ETM-8h 44m/ Pump2-170 ETM-8h 23m/ Peak-5/ High-7 Dose 195 Pump rate-65gpm/ No breakout or spongy areas on the drainfield and dosing correctly | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/17/2023 |  | RoutineScheduled | {FIPSCode}-STS-34576 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Flushed treatment unit spray manifold. Cleaned recirculation pump solids basket filter. Cleaned recirculation pump intake screen. 6" of accumulated solids in discharge pump tank. Recirculation pump is under powered but operational. As long as it is operational it should not be replaced. Tested floats, Pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 07:03 PM
10/13/2023 | Alternative | Routine/Scheduled | 179-14-022 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 6 in of sludge less than 1 in of solids Riser is intact However lid broken Customer doesn't want to fix at this time No signs of infiltration -Discharge/Pump Tank: Normal level Less than 1 in of suspended solids Tested floats and pump all working as should Plumbing and splice box intact Pump moving water properly No signs of infiltration -Aeration: Can actively hear the bubbles moving water properly Inspection port intact air line is intact as well -Aerator needs to be move about a foot under the deck and will need to be re plumbed - This was done at time of service -Air Pump/Blower: 120 volts coming in Everything working properly Customer wanted it moved under the deck further Moved air pump on site -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Pump pulled 9.52 amps All components properly working -Drain Field: Not signs of surfacing or blowing out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | 03:59 PM
07/19/2023 | Alternative | Routine/Scheduled | 175-STS-14861 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 1:41PM
07/11/2023 | Alternative | Initial Visit | 136-07-0183 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - 4 Modules - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 11:15 AM
03/23/2023 | Alternative |  | 101-03-0692 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Steve & Lisa | Cunningham | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | 179-11-0169-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Control Operation" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Septic tank needs pumping due to sludge levels and wipes, spoke to customer about it. Roots in D-box, removed some and added Root-?. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
01/10/2023 |  | RoutineScheduled | SWP-03-370 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/17/2023 | 01:27 PM
11/03/2023 | Alternative | RoutineScheduled | 107-01-0655 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | 12:00 AM
06/08/2023 | Alternative | Routine/Scheduled | 151-16-0045 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screens erviced. BioFilter - peatmoss spent - compacted - ponding - raked best able. Pump Basing - float sensors pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 01:00 PM
02/13/2023 |  | Reportable Incident | 036-STS-33612 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EZ Treat | [6 empty] | ["Recirculation Pump"] | ["Recirculation Pump"] | [18 empty] | Replaced bad recirc pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/15/2023 | 12:00 AM
09/08/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Fast | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | NA | [17 empty] | 0 Scum, 12" loose sludge. Pump tank clean. Alarms, blower, pump, floats all work. Field is dry. 11350 doses. 411.45 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 12:30 PM
05/03/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled | SD-04-02 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [17 empty] | Septic Tank-6"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Puraflo Peat turned in all 4 modules and is in good condition at this time/ Counts: pump-17794 ETM-17631/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/07/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [17 empty] | Service call only: Alarm - found the UV-light & Ballast were faulty/ Counts: Pump-4738 ETM-1251h 10m/ Zone1-2249 Flush-119/ Zone2-2252 Flush-120/ Peak-65/ High-30 Returned on 2/10/2023 and repaired the UV-Light ballast and bulb. System now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/25/2023 | Alternative | Routine/Scheduled | 228-05-1019 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | Dec 30 1899 3:30PM
01/12/2023 |  | RoutineScheduled | 033-10-0140-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | YES | Pungent | Cloudy | [13 empty] | Will be sent separately | Inspected | Pumping of the Septic Tank, Advantex RT Tank & distribution box was completed on January 26, 2023. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
05/22/2023 | Alternative | RoutineScheduled | 147-STS-22642 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Septic | Norweco | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Effluent Screens","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | Dec 30 1899 11:30AM
11/14/2023 | Alternative | RoutineScheduled | 182-15-0194 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Control Operation"] | ["Auxiliary Filter","Control Operation"] | [18 empty] | replaced pump and alarm buzzer | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/14/2023 | 12:00 AM
03/03/2023 | Alternative | RoutineScheduled | 061-17--017 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
03/08/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/08/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES |  | Clear | [13 empty] | Will be sent separately | Inspected | 180 Inspection with sampling | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
04/24/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Sample box has settled & cracked. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | Jan 1 1900 12:48PM
12/04/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | Dec 30 1899 12:20PM
01/16/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-186 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media showing its age but still in good conditions may be 2 more years, will check next year. septic tank needs pump out, spoke to customer about it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0403 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Met local pumper on site (Septic Clean). During pump down, observed that diffusers were coated with a red slime and aeration was sparse. Tank was washed and all sludge, slime and debris removed. PVC spring check valve installed at manifold to prevent backflow of water into the blower in the event of a high water event. Replaced the failed quick disconnect gasket (camlock). Control panel door gasket failed in 2 sections - replaced the gasket. Air pre-filter cleaned. Tank refilled with enough fresh water to flush the discharge piping and verify excellent aeration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
04/07/2023 |  | RoutineScheduled | 101-09-0138 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Pressure | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled | VAG401956 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [7 empty] | Chlorination |  | [] | [] |  | None | Clear | 7.800000 |  |  | 2.200000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/13/2023 | 01:00 PM
07/10/2023 | Alternative | Routine/Scheduled | 810-STS-4044 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Septic | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 2:55PM
06/01/2023 | Alternative | RoutineScheduled | -STS-25584 | Amelia | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 12:00 AM
12/26/2023 | Alternative | RoutineScheduled Component Maintenance | SD-10-335 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter"] | NA | Musty | Clear | [5 empty] | 12/26/2023 | Pump Chamber | 10.000000 |  |  | 4.000000 | 32.730000 |  | Will be sent separately | Inspected | On site for routine inspection and effluent sampling. Low level alarm count for the drip tank increased to 511. Will suggest replacing the RO and TE float switches (bottom 2) since it is possible they may be intermittently sticking on or off. Otherwise, the PLC would be at fault (calling for auto pump cycles when TE float switch is down) and that would require a new control panel. Nitrite-Nitrate = 30.4 mg/L, TKN = 2.33, pH (in drip tank) measured 7.5 @ 12*C. DO could not be measured accurately due to meter problem (reading "over" even after changing the sensor tip). Odor = slightly musty, nothing visible for settleable solids test. In the past 14 days, system pumped an average of 2,478.8 gals/day at 312.6 gals/dose (avg.) for a total of 34,704 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2024 | 06:16 AM
06/02/2023 |  | RoutineScheduled | 153-STS-20337 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
03/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | Dec 30 1899 12:26PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping treatment unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/03/2023 | Alternative | RoutineScheduled | 159-06-0085 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Pad | Not Applicable |  | [] | [] | YES | [17 empty] | Ground water causing high water levels in tank but nothing surfacing on ground. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 182-07-0287 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed a rebuilt blower Pumped primary tank Due to lid being clued caused lid to crackk when opening let us know if want us to install a new access point | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
11/11/2023 | Alternative | RoutineScheduled | 2008-01-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Attached Growth Medium","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 6.900000 |  |  | 1.700000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/13/2023 | 12:00 AM
04/29/2023 | Alternative | RoutineScheduled | 107-18-0302 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [15 empty] | Filter was stopped up and backing up into house | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
01/20/2023 |  | Reportable Incident | 087-STS-6682 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Biofilter Changeout - Peatmoss permitted to BioCoir. 01/20/2023 - septic tank pumped for storage for biofilter changeout 01/24/2023 - peatmoss biofilter media removed - new biocoir media installed - new spray distribution system installed. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/25/2023 | 07:00 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-161 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Removed drop box in poor shape that had been put in to replace the original Puraflo sample box that had been badly damaged. Installed new sample box and lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
07/25/2023 | Alternative | RoutineScheduled | 139-05-0105 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Delta Whitewater |  |  | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Auxiliary Filter","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Raised valve box in dripfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled | 88-184-93 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 12 Chlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/13/2023 | 12:00 AM
04/04/2023 |  | RoutineScheduled |  | Greene | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 04/04/2023 |  | 9.000000 | [5 empty] | Will be sent separately | Inspected | Blower hot not operating properly replaced with proper OEM blower | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
11/06/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1250 |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | Dec 30 1899 10:00AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Musty | Clear | 7.200000 | 2.300000 | [11 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
04/13/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | System pumped out 3 years ago. Septic zone minimal scum, 4-5" sludge- Recirc zone trace-3" sludge, Discharge Tank trace sludge- Biofilter & RSV Cleaned, Flushed and brushed manifold, sprayed off media, Media was 70% blinded- cleaned and sprayed off. Reduce household chemicals and cleaner to improve system bacteira and reduce slime. Ran system in test mode, Tested recirc floats and All functional. We will arrange to return and replace the discharge alarm float or repair as needed in near future., Recirc pump time 369.9 Hours 99999 cycles, discharge pump time 33 hours and 8040 cycles- One alert on 10-2022 in history, Hinges on lid are broken from age but lids screw when shut. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
04/18/2023 |  | RoutineScheduled | SWP-05-263 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
05/19/2023 | Alternative | RoutineScheduled | SD-12-406 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 45.000000 | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 06:45 PM
06/06/2023 | Alternative | Routine/Scheduled | 136-18-0128 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | EZ Treat Sandfilter |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Recirc Tank - float sensors, pump, and RSV serviced. Treatment Module - media pads & spray grid serviced. - Lid fractured from lawn care operations. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 08:15 AM
12/06/2023 | Alternative | RoutineScheduled Component Maintenance | 101-05-0802 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
10/30/2023 | Alternative | Follow-Up Component Maintenance | 179-STS-88745 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Follow up. Enabler float stock close, replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/03/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 04/03/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
09/08/2023 | Alternative | Reportable Incident Component Maintenance | 179-16-0380-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Control Operation"] | ["SludgeScum Accumulation" ,"Control Operation"] | NA |  | Cloudy | [13 empty] | Will be sent separately | Inspected | 9/5/23. No alarm, but grass was tall and dark green around all tank lids. All automatic pump functions had stopped, floats were not registering in control panel. Replaced F1 fuse (1 amp) beside the control panel breakers. Ran discharge pump long enough to stop effluent from seeping out of tanks. Tested panel and discussed with Orenco tech support. The panel transformer that provides 24V to the motherboard had failed, needs to be ordered. 9/7/23. Owner had a local pumper come and pump out enough to drop the effluent level to just above the low level alarms (the idea was to save some for testing). 0/8/23. Replaced 24V transformer. Pumper actually pumped a little too much to do full operation check. Floats registered in panel when lifted by hand, both pumps worked. Advised owner of situation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
03/22/2023 |  | RoutineScheduled | 2137-13-153 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Septic Tank | ATU | Pump | Gravity | Discharge | UV |  | ["Recirculation Pump","Disinfection"] | ["Disinfection","Recirculation Pump"] | NA |  |  | 7.600000 |  |  |  | E.coil-1 MPN/100mL | 04/27/2023 | Sample Chamber | 2.000000 |  | 1.800000 | 22.000000 |  |  | Attached to this report |  | Septic Tank-4"sludge 2"scum/ ATU-4"sludge 0"scum/ EZ-Treat-12"sludge (REQUIRES Pump Out) UV-Light is faulty and requires replacement/ Repair to UV-Light completed on 4/10/2023/ Sample taken on4/27/2023 Pump intake cleaned and media in good condition/ EZ-Treat spray working correctly/ Controls, pumps, floats and alarms functioning properly/ Watermeter-129240 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/02/2023 | Alternative | Routine/Scheduled | R15-180-0067 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | Jan 1 1900 1:30PM
02/27/2023 |  | RoutineScheduled | 179-06-0365-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 107-07-0093 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired alarm float and replaced bottom float on Recirc | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0075-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Control Operation"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
11/14/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | Dec 30 1899 8:35AM
07/17/2023 | Alternative | Routine/Scheduled | 151-08-0066 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 05:53 PM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/30/2023 | Alternative | Routine/Scheduled | 2013-143-0116 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Orenco Advantex |  | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Manifold flushed. Drip field and spin filter flushed. Uv bulb changed. System appears to be operating normally. Psi set back to 22psi. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 09:37 AM
07/21/2023 | Alternative |  | 101-17-0001 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Jason | Mais | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 4.000000 |  | Septic Tank #1 | Septic Tank #2 | Pump | Pressure | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Recirculation Pump"] | ["Recirculation Pump"] | YES | [7 empty] | 03/08/2023 | Sample Chamber | 25.000000 |  |  | 33.000000 |  |  | Attached to this report |  | Septic Tank #1-6" Thick scum layer recommend pump out/ Septic Tank #2-4"sludge 0"scum/ EZ-Treat Recirc. Pump Tank to Drainfield-3"sludge 0"scum/ Pump Tank to LPD Trenches-2"sludge 0"scum/ Controls, pumps, floats and alarms functioning properly/ Counts: Pumps to Drainfield/ Pump1-008536 ETM-0259459/ Pump2-008411 ETM-0259251/ Peak- N/A/ High- N/A// Pump to LPD Drainfield- Pump1-682 ETM-36h 30m/ Pump2-644 ETM-34h 31m/ Peak-115/ High-16/ EZ-Treat Counts: Pump-0179217 ETM-0787382 On-2.5m Off-10m | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/28/2023 | Alternative | RoutineScheduled | 107-06-0330 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 12:00 AM
11/28/2023 | Alternative | RoutineScheduled |  | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | Ecoflo |  | Pump | Pressure | Pad |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
03/30/2023 | Alternative |  | 003-STS-31858 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Hye | Kim | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/02/2023 | Alternative | Routine/Scheduled | 2019-143-0070 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/02/2023 | 10:37 AM
07/04/2023 | Alternative | Initial Visit | SD-02-100 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Advantex | Gravity | Pressure | Trenches | Not Applicable |  | ["Auxiliary Filter","Attached Growth Medium"] | ["Auxiliary Filter","Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | Musty | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 12:30 AM
11/18/2023 | Alternative | RoutineScheduled | 171-07-0746 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | MultiFlo ATU |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. New homeowner. 6" of accumulated solids in septic tank. Septic tank will need risers and lids when a pump out is needed. Good aeration in treatment unit. 6" of solids in discharge pump tank. Cleaned drip manifold spin filter. Adjusted on/off level of discharge pump tank as it appeared high. Set on level at 12" and off level at 6". Alarm level set at 24". Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 07:03 PM
06/20/2023 | Alternative | Routine/Scheduled | 157-05-042 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. PUmp Basin - float sensors, pump and controls operating - minor bulging noted. Biofilter - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 12:15 PM
09/25/2023 | Alternative | RoutineScheduled | 02-197-A5 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | [12 empty] | Pungent | Cloudy | 7.000000 | 0.000000 |  | 1.000000 | [11 empty] | The aerator is not running and dechlorine tables need added. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/11/2023 | Alternative |  | SP-04-472 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
12/13/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pumps are functioning properly. Checked and confirmed discharge floats are functioning properly. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly Distribution Box Condition of above Component Notes for above Component Water levels are normal. Structural integrity of distribution boxes appear to be intact Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 9:43AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/18/2023 |  | Routine/Scheduled | 550-STS-6617 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 2:50PM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0379-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. Peak:1422, peak etm-61647. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
10/10/2023 | Alternative | RoutineScheduled | -STS-93450 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/31/2023 | Alternative | RoutineScheduled | 109-STS-31084 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
05/05/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","Level Sensor Operation"] | ["Auxiliary Filter","Level Sensor Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/16/2023 | 01:01 PM
02/20/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | arcon | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
11/09/2023 | Alternative | RoutineScheduled | 181-04-0278 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 4.000000 | 4000 | Septic tank |  | Pump | Pressure | Trenches | Not Applicable | 800.000000 | ["Effluent Screens","Control Operation"] | ["Effluent Screens","Control Operation"] | YES | [17 empty] | Semi-annual inspection of LPD #4; HD ID 181-04-0278; 4 dwellings connected to the LPD system. No visible sign of malfunction within the LPD trench area. Measured septic tank sludge volumeand cleaned effluent filters at all 4 dwellings: Lot 23-8" solids; Lot 25-6" solids; Lot 28-6" solids and missing effluent filter; Lot 30-6" solids. Recommend homeowners check/replace flapper valves in all toilets. Transfer pump: 8.10 amps; LPD pump: 15.70 amps | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/01/2022 | 12:00 AM
06/26/2023 | Alternative | Routine/Scheduled | 234-15-277 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | Dec 30 1899 1:55PM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/24/2023 | 08:34 AM
03/28/2023 |  | RoutineScheduled | 179-STS-90256 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
07/24/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0127-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media looks very good. System does not need pump out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
12/13/2023 | Alternative | Routine/Scheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 350 | Best 1 |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 11:59 AM
04/18/2023 |  | RoutineScheduled | 04-184-5004 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/18/2023 | 12:00 AM
11/29/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 8.000000 | [14 empty] | Blower needs to be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/13/2023 | 02:10 PM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/24/2023 | Alternative | RoutineScheduled | 166-15-090 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | [9 empty] | ["None"] | ["None"] | [17 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 12/06/2023 | Dec 30 1899 9:34AM
02/21/2023 |  | Reportable Incident | 12-120-0218AR Disc | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Gravity | Gravity | Discharge | UV | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [5 empty] | 02/21/2023 | Sample Chamber | [7 empty] | Pumped Out | Supervised pumpout of primary septic tank as recommended during initial service visit. Sealed leaks at inlet and outlet of septic tank. Obtained samples for BOD5, TSS, TN, E-Coliform and transported to EnviroCompliance Laboratory. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 9:30AM
06/30/2023 | Alternative |  | 099-12-0071-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
03/15/2023 |  | RoutineScheduled | 177-STS-87442 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [5 empty] | 03/15/2023 |  | 57.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Broken riser on pump tank, replaced. Septic tank needs pumpout due to amount of solids mostly Broken down toilet paper. Recommend to extend gutter pipe to make sure rain water flows away from tanks. HL 3, LL 11, OVERRIDE 2. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
11/10/2023 | Alternative | Routine/Scheduled | 127-STS-32420 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Found at normal level, 12in of sludge and less than 1in of solids. -Discharge/Pump Tank: Found at normal level, less than 1in of sludge and solids. Teste floats and pump. All working as they should. -Aeration: Found at normal level, 14in of suspended solids. Treatment tank is operating as it should. -Air Pump/Blower: Pulled and cleaned air filter. Air pressure sensor working as it should. Air pump pulled 0.25 amps -Control Panel: 120 volts, audio and visual alarms working as they should. Tested timer. Pump pulled 7.19 amps -Distribution Box: Found between tree and and sitting area. Found at normal level. 5lines balanced taking water. Removed small roots while on site. -Drain Field: No signs of surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 3:01PM
10/24/2023 | Alternative | RoutineScheduled | 07-192-233 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 10 - Bio Max tablets installed 1 - NORWECO feeder tube | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/24/2023 | 12:00 AM
11/28/2023 | Alternative | Routine/Scheduled | 06-172-0244 | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/28/2023 | Dec 30 1899 11:27AM
04/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
04/14/2023 |  | RoutineScheduled | 127-STS-33404 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | EZ Treat |  | Pump | Gravity | Trenches |  |  | [] | ["Recirculation Pump","Control Operation","Level Sensor Operation","Distribution Pump Operation","Auxiliary Filter"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled | SD-99-436 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1000 | septic | multiflo | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | 6.700000 |  |  | 1.010000 |  | 12/13/2023 | Pump Chamber | 4.000000 | 0.000000 |  | 19.100000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/02/2024 | 11:25 AM
05/15/2023 |  | Routine/Scheduled | {FIPSCode}-STS-5042 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | Jan 1 1900 11:00AM
08/10/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 02:32 PM
11/02/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Puraflo peat. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/15/2023 | Dec 30 1899 2:02PM
10/10/2023 | Alternative | Follow-Up Component Maintenance | 179-17-0418-VU | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic and pump tank pumped out by others prior to peat replacement. Degraded peat was removed by hand and new peat was installed. Peat was purchased from Driller Services. Degraded peat was disposed at Spotsylvania Refuse. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
08/15/2023 | Alternative | RoutineScheduled | 12-163-0046 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Norweco |  | Gravity | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Auxiliary Filter"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
11/28/2023 | Alternative | RoutineScheduled | C04-180-0035 | Roanoke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Fast Biomicrobics |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Sludge levels-- -32" scum on top (Heavy on the wipes) and 6-10" sludge in Septic tank. May want to arrange a pump out this fall. Treatment Tank has good aeration and 3-12" thick scum on top and 3-4"- sludge trace - in Pump Tank 12" sludge. Doing good,, the treatment scum layer may need attention later this year. Good aeration in the treamtnet unit. System is pumping to drain field and drain field appears dry and unremarkable. 50psi going to drainfield, watermeter reading 1,840,520 vs 1,757,490 gallons approx 83,000 gallons this year about 227 gallons per day. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/28/2023 | Dec 30 1899 9:30AM
03/14/2023 |  | Initial Visit | 107-18-0027 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 5000 | SEPTIC TANK ONLY | EZ TREAT 10,000 GALLONS PER DAY | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","Other"] | ["Control Operation","Other"] | YES | [7 empty] | 03/16/2023 | Pump Chamber | 29.900000 |  |  | 28.000000 |  |  | Attached to this report |  | SYSTEM DID NOT NEED TO BE PUMPED. THE SEPTIC TANK FILTER WAS CLEANED. THE CONTROLS WERE OPERATING AS DESIGNED. ONE RECIRCULATING PUMP WAS NOT OPERATIONAL AND WAS REPLACED. ALL PUMPS WERE PULLED AND EFFLUENT SCREENS WERE CLEANED. THE EIGHT EZ TREAT PODS WERE SPRAYED AND CLEANED. IT WAS DISCOVERED THAT TWO OF THE EZ POD UNDERDRAINS WERE PLUMBED TO THE PUMP TANK INSTEAD OF THE RECIRCULATING TANK. THESE ITEMS WERE DUG UP AND REPAIRED ON 4/24/2023. FOUR LEAKS IN THE DRIP FIELD WERE DISCOVERED AND WERE DUG UP AND REPAIRED ON 4/4/2023. PRESSURE ON ALL SIX ZONES OF THE DRIP FIELD WERE ADJUSTED TO DESIGNATED PRESSURE. RETURN EFFLUENT TO THE PUMP TANK WAS PRESENT AFTER REPAIRS WERE MADE TO THE DRIP FIELD. LIDS WERE SECURE. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/01/2023 | 09:30 PM
01/31/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. On arrival, the control panel was indicating a high level alarm in the dosing tank. It turned out to be a false alarm as the effluent level was normal, and the alarm float failed testing. New float switch installed. Air pre-filter cleaned. Aeration is starting to diminish as evidenced by minimal aeration throughout the tank with a heavier point located at mechanical end of the tank. Will continue to monitor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
08/03/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced solenoids in hydraulic unit. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/29/2023 | Dec 30 1899 3:58AM
12/05/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-21544 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Upon arrival, I found the septic tank in high level due to a clogged effluent screen. I cleaned the effluent screen and septic tank returned to normal level. I checked the sludge levels of the septic tank and found them to be acceptable. I noted that the recirculation pump is an Orenco PF15. I adjusted the timer settings to compensate with an Orenco PF15 to accommodate for about 100 gpd flow. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 9:59AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 015-STS-337353 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
05/20/2023 | Alternative | Routine/Scheduled | 095-STS-7090 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1000 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/20/2023 | Dec 30 1899 12:00PM
12/06/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0187-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
08/14/2023 | Alternative | RoutineScheduled | 179-STS-91906 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/01/2023 | Alternative | Routine/Scheduled | 06-163-0211 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal Level 6 in of sludge Less than 1 in of solids No signs of infiltration -Recirculation Tank: Normal Level 11 in of suspended solids Tested floats and pump all working as should All plumbing intact and pump moving water properly however pump is aged Brushed and flushed biotube filter No signs of infiltration -RSV (Recirculating Splitter Valve): Pulled and cleaned -Media Sheets: Brushed and flushed laterals Flushed module until water ran clear Sprayed sheets clean -Control Panel: 120 volts coming in All visual and audible alarms functional Pump pulled 11.3 amps All components working as should however panel is aged -Distribution Box: Normal Level 4 lines all intact and taking water properly Speed balancers intact and functional -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 8:58AM
09/21/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 8.160000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 12:00 PM
04/07/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | installed new riser on septic tank. System in working condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/17/2023 | Alternative | Routine/Scheduled | 075-STS-32824 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/17/2023 | Dec 30 1899 2:41PM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/21/2023 | Alternative | Routine/Scheduled | 196-05-355 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Real Estate Inspection. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 4 Modules - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 09:15 AM
09/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/21/2023 | Alternative | RoutineScheduled | 001-STS-93063 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJI CLEAN CEN 5 |  | Pump | Pressure | Pad | UV | 300.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 5-6" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 01:25 PM
05/18/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | 12:00 AM
10/06/2023 | Alternative |  |  | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Barboursville Masonic Lodge #112 |  | Roger | Gibson | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/14/2023 | Alternative | RoutineScheduled | 061-STS-26472 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | No sample available. Refilled chlorination and dechlorination tablet feeders. All system components operational. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/27/2023 |  | Routine/Scheduled | 05-120-0762AR | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Gravity | Gravity | Trenches |  |  | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | YES | [17 empty] | The peat moss needs to be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/27/2023 | Jan 1 1900 2:46PM
05/26/2023 | Alternative | RoutineScheduled | 149-10-024 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 12:00 AM
03/02/2023 | Alternative | Routine/Scheduled | 800-STS-14487 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 10000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 14000.000000 |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [7 empty] | 03/02/2023 | Sample Chamber | [8 empty] | Routine Service - service overdue due to NO Contract in Place. Primary septic tank - recommend pumpout - primary and secondary effluent screens serviced. Processing Tank - media dosing pumps serviced, recirc pump serviced - media drapes and spray grid serviced. Pump Tank - float sensors, pumps and controls operating. All absorption fields inspected - all DBoxes intact Laboratory samples for BOD5, TSS and Total Nitrogen obtained and transported to the laboratory. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/06/2023 | Dec 30 1899 7:45AM
08/07/2023 | Alternative | RoutineScheduled | 182-09-0218 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [18 empty] | Lid to be replaced by Maintenance. Mild corrosion in Control Panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 12:00 AM
06/14/2023 | Alternative | RoutineScheduled | 150-06-0374 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 gallons | septic tank | Delta Whitewater | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear |  |  | 10.000000 | [12 empty] | Septic tank 6" fog, 4" sludge. Delta Whitewater less than 10% SS. Cleaned aerator filter. Pump, alarm, floats, controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/23/2023 | 06:05 PM
07/12/2023 | Alternative | RoutineScheduled Component Maintenance | 175-10-0297 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["Disinfection" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | 7.200000 | 15.600000 | [11 empty] | Will be sent separately | Inspected | Discharge point does not have required sign. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 07/17/2023 | 12:46 PM
10/11/2023 | Alternative |  | SD-91-80 | Clarke | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lord Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 | 1500 |  |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | LPD septic system | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/16/2023 | 10:40 AM
05/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Only one zone appears to be functioning. Could not get the system to switch zones for the remote zone valves. Filter flush solenoids do not appear to be functioning as well. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
12/10/2023 | Alternative | Reportable Incident | 08-163-0100 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the control panel was NOT in alarm condition. System was in normal level. I put system in TEST mode and found that recirculation was triggering low level alarms due to a clogged effluent screen. I cleaned the effluent screen and that corrected the issue. Checked sludge levels and found them to be acceptable. Checked and found recirculation timer settings were set aggressively so I defaulted them. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 12:39PM
01/13/2023 |  | Reportable Incident | 093-16-0045 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable | 600.000000 | Distribution Pump Operation | ["Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Reportable Discharge pump failure - new discharge pump (high head turbine) installed. Pump Tank pumped empty by Duck's Septic Service to facilitate repairs. serviced drip headworks and filters while on property. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/16/2023 | Jan 1 1900 11:00AM
04/28/2023 |  | RoutineScheduled | 181-00-0129 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Sand filter | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | The system did not need to be pumped. Both spin filters were both cleaned. The controls were operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 09:30 PM
03/03/2023 |  | RoutineScheduled | 179-06-0029-SWT | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
01/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 2000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 01/30/2023 | Sample Chamber | 16.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/20/2023 | Alternative | RoutineScheduled | SD-12-110 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Battlefield Soil And Septic LLC | 1942001084 | Josh | Johnston | 1.000000 | 1250 | Ecopod |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/21/2023 | 05:10 PM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 3.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:00PM
03/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/11/2023 |  | RoutineScheduled | 08-100-0874 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BioCoir |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | Everything is working at it should. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/12/2023 | 12:05 PM
03/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Pressure | Drip | UV |  | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | septic and atu need pumped | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/10/2023 | Dec 30 1899 9:40AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87395 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | we recommend pumping the septic tank, aerobic treatment unit and pump tank due to sludge accumulation in the tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
09/29/2023 | Alternative | RoutineScheduled | 041-STS-261089 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 2500 | 1000 | 750 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/29/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [16 empty] | Inspected | Clear effluent on top. Recirc pump and Discharge pumps both operational. Alarm operational, Septi zone 1 " scum and 4-6 " sludge, Recirculation zone 4" sludge (may need pumping next year), Pump tank Discharge trace sludge, RTU120663, Flushed and Brushed Manifold, Cleaned RSV, Cleaned Media Filter, Ran in test mode. FLoats test good. Recirc pump shows 2013.3 hours and 2759 cycles and discharge pump shows 92 min and 6799 cycles. Alarms in history 8-31-21, 1-3-22, 3-2-22 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
09/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 09/05/2023 | Sample Chamber | 4.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/01/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
10/12/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 12:55PM
10/20/2023 | Alternative | RoutineScheduled | 03-113-121 | Buchanan | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | New aerator installed | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 10/20/2023 | 12:00 AM
05/31/2023 |  | Follow-Up | 175-05-0878 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced 3 control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
05/19/2023 | Alternative | Pump-Out Only | -STS-13565 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | - inlet line is running uphill into the septic tank, recommend correcting this issue | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | 12:00 AM
05/19/2023 |  | Pump-Out Only | 228-06-0698 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | Jan 1 1900 11:00AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0100-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Hoot | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the air filter in the HP80 linear air pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
02/21/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | mow and maintain drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/14/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-22043 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [5 empty] | 08/14/2023 | Pump Chamber | 6.000000 | [5 empty] | Will be sent separately | Inspected | Annual inspection completed and first BOD sample collected. Septic tank needs pumped ASAP. Owner to make arrangements with local pumper and then run bathtub for 4 hours once tank has been emptied. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
02/10/2023 |  | Initial Visit | 2006-143-0149 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable | 750.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - Previous Service Provider = Mathews Soils - Owner admits to system NOT having service in several years! Processing Tank - requires pumpout - RSV, recirc pump & effluent screen serviced. Effluent screen heavily clogged Treatment Modules - TWO - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 09:00 AM
02/24/2023 |  | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Trenches |  | 450.000000 | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens"] | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/27/2023 | 12:13 PM
06/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
06/01/2023 |  | RoutineScheduled | 124-STS-2379 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Virginia Beach | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/18/2023 | Alternative | RoutineScheduled | 181-12-0006 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20 | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [7 empty] | 08/18/2023 | Pump Chamber | 6.400000 |  |  | 5.400000 |  |  | Attached to this report |  | The system did not need to be pumped. The effluent and spin clean filters were both cleaned. The recirculating pump was pulled and cleaned. The textile sheets were sprayed off. The BOD and TSS were within the permitted limits. The controls were operating as designed. There was return effluent returning to the pump tank so the drip field was operating as designed. There was no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 08:50 PM
03/23/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | beds 1 & 5 slight ponding | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
07/17/2023 | Alternative | Routine/Scheduled | 151-03-452 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2500 | Ecoflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 05:56 PM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 4.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Audible alarm for DF pump was not functioning. It was replaced at time of inspection. 3 Spray heads on the EZ treat unit were clogged. Lines were flushed and nozzles were replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/17/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3530 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Jan 1 1900 8:50AM
10/09/2023 | Alternative | RoutineScheduled | 94-160-0551 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | [7 empty] | [] | ["Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Septic | Cloudy | [15 empty] | - pump line is broke outside of septic tank, approx 10ft - riser needs to be replaced due to not seating properly which is causing riser to not be water tight | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/17/2023 | 12:00 AM
04/17/2023 | Alternative | Reportable Incident | 093-06-0183 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/17/2023 | Dec 30 1899 8:00AM
07/26/2023 | Alternative | Routine/Scheduled | 87-51 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  | 300.000000 | None | None | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 02:00 PM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. Drip tank was in low level alarm. All floats were down and reading "off" in control panel. Tested RO and TE floats by shortening rest time. When timer float was down, no cycle started. When timer float was up, cycle started and ended at end of run time or when RO float was dropped to off position. Raised timer float about 1-1/4" . Suspect low level condition was caused by a field flush cycle (which pumps more water in same amount of time). Drip panel high level count at 52, low level count at 505. Needed repairs are on schedule for 11/20/23. In the past 13 days, system pumped an average of 1274 gals/day at 368 gals/dose (avg.) for a total of 16,562 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
10/27/2023 | Alternative | RoutineScheduled | VAG401996 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | Constructed Wetlands |  | Pump | Gravity | Discharge | Chlorination |  | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation"] | NA | None | [16 empty] | System was not discharging at time of inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/12/2023 | 09:00 AM
12/13/2023 | Alternative | Routine/Scheduled | 19-142-0091 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Checked and confirmed spray pattern Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 9:43AM
12/02/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 4" of accumulated solids in septic tank. 4" of solids in discharge pump tank. Cleaned recirculation pump solids basket filter. Flushed treatment unit spray manifold. Sprayed solids off of treatment unit "sheets" . Excellent treatment quality. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2024 | 07:03 PM
08/01/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Auxiliary Filter","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | 12:00 AM
03/28/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs new UV Unit. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | Jan 1 1900 7:20PM
01/23/2023 |  | RoutineScheduled | 003-STS-34025 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-11-0157-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [5 empty] | 06/29/2023 |  | 10.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Recirc tank needs pumpout. Discharge pump has slowed down, might die soon. Will send proposal for pump out. Bottom trench needs a little dirt on spot where EZ flow is showing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
03/10/2023 |  | RoutineScheduled | 07-197-A12 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/10/2023 | 12:00 AM
01/06/2023 | Alternative | Reportable Incident | SD-11-98 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | DCM Septic LLC | 1942001350 | Michael | Cook | [9 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [17 empty] | Inspected | replaced floats system working propoerly now | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | 10:00 AM
03/17/2023 | Alternative |  | 124-STS-2379 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Three Rivers | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2000 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Dispersal System Operation","Attached Growth Medium"] | YES | None | Discolored | 7.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | 02:45 PM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | 10-142-0174 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Chickahominy | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend mowing the drain field to remove small trees that are growing there. The drain field should be maintained in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | Dec 30 1899 7:38AM
02/17/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 08:45 AM
09/15/2023 | Alternative | Reportable Incident | 179-STS-87483 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [17 empty] | Inspected | replaced pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:00 PM
01/21/2023 |  | RoutineScheduled | 133 11 0302 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 1" of accumulated solids in septic tank. Flushed treatment unit spray manifold. Cleaned recirculation pump basket filter. 4" of solids in discharge pump tank. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 07:03 PM
05/08/2023 |  | Routine/Scheduled | 234-17-213 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | Jan 1 1900 11:35AM
05/09/2023 | Alternative | RoutineScheduled | 133-STS-95869 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Other conventional maintenance performed | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/15/2023 | Alternative | RoutineScheduled | 109-14-0072 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | MultiFlo ATU |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 16" of accumulated solids in septic tank. Cleaned septic tank solids filter. 4" of solids in discharge pump tank. Good aeration. Excellent treatment quality. Removed solids from several treatment unit "socks". Tested floats, pump and alarms. A pump out may need to be done because of solids build-up in treatment unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/25/2023 | 07:03 PM
10/02/2023 | Alternative | Reportable Incident | 075-STS-34379 | Goochland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Fuji |  | Pump | Pressure | Drip | UV |  | ["Disinfection"] | ["Control Operation","Effluent Screens"] | YES | Musty | Clear | [14 empty] | Inspected | UV Bulb INOP - needs to be replaced Conducted Draw down and re-adjusted gallons per dose to 65 (per designing engineer), was less than 30 gallons per dose. Yard needs to be re-graded - all the runoff is being directed to the pump station tank - effluent in pump station had a muddy/dirt discoloration. Reason for visit was a high water alarm. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/02/2023 | Dec 30 1899 3:00PM
05/24/2023 |  | Routine/Scheduled | 10-120-0056AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | The treatment and trash tanks need to be pumped | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/24/2023 | Jan 1 1900 1:37PM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | 2002-93-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 7.100000 |  |  | 8.200000 | [9 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 07/07/2023 | 06:25 AM
01/13/2023 |  | RoutineScheduled | 181-01-0144 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","SludgeScum Accumulation"] | ["Auxiliary Filter","SludgeScum Accumulation"] | [17 empty] | Pumped Out | The septic/microfast tank was pumped and cleaned. The pump tank was also pumped and cleaned. The blower and spin filters were both cleaned. The controls were operating as designed. The pressure gauge was replaced and the pressure was adjusted on the drip field. There was return effluent returning to the pump tank so the drip field was operating as designed. There was no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | 05:00 PM
09/25/2023 | Alternative | Routine/Scheduled | SHUN-B8AMTZ | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 12:23PM
10/09/2023 | Alternative |  | 033-13-0143-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
09/18/2023 | Alternative | Follow-Up Component Maintenance | 179-16-0344-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 2.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Re-leveled distribution box and reconnected piping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
01/16/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2132 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 11:20AM
04/14/2023 |  | RoutineScheduled | 165-STS-333615 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] |  | NA | [15 empty] | Will be sent separately | Inspected | ET Bed trees through bed and not draining properly, Let us know if want us to repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/21/2023 | 03:35 PM
09/28/2023 | Alternative | RoutineScheduled | SWP-05-725 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-2 0-4 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 10:00 AM
05/22/2023 | Alternative | Reportable Incident | 157-09-308 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [17 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 Replaced degraded distribution box with new 8 port concrete DBox. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 07:30 AM
09/29/2023 | Alternative | Routine/Scheduled | 12-120-0201A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/29/2023 | Dec 30 1899 10:32AM
02/02/2023 |  | Routine/Scheduled | 234-14-16 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 9:00AM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
04/12/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/08/2023 | Alternative | RoutineScheduled | SD-11-370 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 02:00 PM
04/21/2023 |  | Routine/Scheduled | 228-18-0309 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/21/2023 | Jan 1 1900 7:20AM
03/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/04/2023 | Alternative | RoutineScheduled | 166-17-009 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | peat check - okay, cleaned filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank to Ecopod ATU | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-6"sludge 4"scum/ Ecopod ATU-4"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working properly, Ecopod has normal color and odor/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-3860 ETM-77h 53m/ Pump2-3916 ETM-76h 17m/ Peak-7047/ High-2438/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/05/2023 | Alternative | Routine/Scheduled | 800-STS-15633 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - Real Estate Inspection. Primary septic tank - normal level - not pumped - effluent screen serviced. Biofilter - Poly - peatmoss in good condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - concrete - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 10:45AM
03/29/2023 |  | RoutineScheduled | {FIPSCode}-STS-21755 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/29/2023 | 12:00 AM
04/24/2023 | Alternative | RoutineScheduled | 101-STS-93645 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1000 | BioCoir NS-500 |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 12:00 AM
01/09/2023 |  | Reportable Incident | 234-12-143 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/09/2023 | Jan 1 1900 7:00AM
11/22/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 2.000000 | [8 empty] | [] | [] | YES | [7 empty] | 11/22/2023 | [10 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 12:00 AM
11/28/2023 | Alternative |  | {FIPSCode}-STS-12642 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | Orenko Advantex |  | Pump | Pressure | Drip | Not Applicable | 75.000000 | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 11:30 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/19/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 45 seconds every 2 hrs 4 mins. It was raining at the time of service - could not check the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 9:00AM
01/31/2023 |  | RoutineScheduled | 08-100-0912 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Delta Envir. DF | Gravity | Pressure | Pad | Not Applicable | 300.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 02:35 PM
06/07/2023 | Alternative | Reportable Incident Component Maintenance | 175-12-0071 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Owner reported several alarms recently. Today, both tanks were in high level but no problems of any kind were found. Electronic users log indicated multiple high level alarms in the recirc tank, and 3 pump fail alerts in the discharge tank. Discharge pump amp draw and flow rate consistent with previous tests. Checked for loose connections, none found. The panel had recorded 3 discharge cycles today with run times of 2.5 min each. This was strange because the pump was programmed to run only 2 cycles (12 hours apart) for 4.5 min/ cycle. The Orenco panel will end the discharge pump cycle 30 seconds after the timer float drops out. That seems unlikely to have happened as the discharge tank was in high level. The pump, timer float switch, or motherboard could be having intermittent electrical issues. The Orenco Vericomm panel locks out the recirc pump when the discharge tank goes into high level. Because there is a long period between discharge pump cycles, the recirc tank is likely to get into high level as the owners continue to use water. To alleviate this situation, the total daily flow was divided into 3 cycles, 8 hours apart and the run time shortened to 3 minutes. Hopefully this will help reduce the number of recirc alarms being generated by discharge high level alarms. In addition, the discharge timer float and low level float were both lowered 3" to allow for more storage throughout the day (pump still covered with water). Dye tablets were provided to the owner who later said none of the toilets were found to be leaking. At this point, heavy water use or occasional running toilets are believed to be the cause of the alarms in the past month. Rain has been very light, so infiltration is not likely. (Note: as of 6/15, owner said no new alarms). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
01/31/2023 |  | RoutineScheduled | 043-STS-32350 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Cloverleaf Environmental Consulting, Inc | 1942001135 | Robert | Charnley |  |  | Advantex |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Control Operation","Septic Tank Baffles"] | ["Effluent Screens","Control Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/17/2023 |  | RoutineScheduled | 177-17-0395-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Repaired broken connection in dripfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Dont flush wipes Keep drainfield mowed and maintained and free of brush | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
10/02/2023 | Alternative | RoutineScheduled | 107-11-0248 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation","BlowerCompressorAerator Operation"] | [18 empty] | leak at air relief fixed. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/02/2023 | 12:00 AM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/22/2023 |  |  | 19-118-0017 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance | SD-02-717 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Chlorination |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Owner is going to replace concrete lids and aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/24/2023 | Alternative | RoutineScheduled | 107-03-0070 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
02/03/2023 |  | RoutineScheduled |  | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 4.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Do not flush plastic gloves | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | Dec 30 1899 11:24AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | Dec 30 1899 12:46PM
12/12/2023 | Alternative | Routine/Scheduled |  | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 8:11AM
05/01/2023 | Alternative | Routine/Scheduled | 136-16-0305 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the alarm light bulb, replaced the buzzer, and replaced the mute button. Pumped out the septic tank and pumped the trash off the top and bottom of the Clearstream tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/01/2023 | 01:45 PM
09/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:40PM
08/30/2023 | Alternative | Routine/Scheduled | 166-13-133 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank Pumped | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Pumped out the septic tank and pumped the sludge from the top and bottom of the Clearstream tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 12:00 PM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance | SD-95-527 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Completed annual inspection and routine maintenance. Effluent filter was very dirty, would benefit from an extra cleaning between annual inspections. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
02/06/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | st-unable to open owner to make handle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
10/11/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | NA | [16 empty] | Pumped Out | Pumped Both Tanks Solids & Liquids | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
07/20/2023 | Alternative | Routine/Scheduled | 08-142-0378 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced - riser below grade. Biofilter - peatmoss in fair condition - raked / turned. Pump Basin - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | Dec 30 1899 7:45AM
06/01/2023 |  | Routine/Scheduled | 06-120-0625A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/01/2023 | Jan 1 1900 10:07AM
11/03/2023 |  | Routine, Scheduled | 175-06-0035 | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | POINDEXTER, WILLIAM D | 1934000380 | WILLIAM | POINDEXTER | 1.000000 |  | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Septic tank needs pumping. Both pump chamber require excess sludge removal High amperage on Puraflo pump, pump rate okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2011 | 11:53 AM
08/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 0"scum/ Microfast ATU-10"sludge 0"scum/ Pump Tank-1"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-160 ETM-5h 26m/ Pump2-155 ETM-5h 5m/ Peak-6/ High-5/ On-2m 11s Standard Off-7h 58m/ Peak Off-6h 22m/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/19/2023 | Alternative | Pump-Out Only | 166-09-138 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Routine Pump out: -Arrived opened the septic tank pumped 1000 gallons lite solids Very heavy sludge. One hose from the truck. Customer has a Puraflo four chamber system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 04:16 PM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/28/2023 |  | RoutineScheduled | 15-152-061 | Lee | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Advantex |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | 12:00 AM
07/20/2023 | Alternative |  | 182-16-0033 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles","Recirculation Pump"] | ["Septic Tank Baffles","Recirculation Pump"] | [18 empty] | pump was clogged with trash, intake screen broken. pump seems to be compromised and not pumping as hard as it should | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/20/2023 | 12:00 AM
07/18/2023 | Alternative | Routine/Scheduled | 234-13-320 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 12:50PM
04/18/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [28 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 10:34 AM
02/08/2023 | Alternative | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Other"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/11/2023 | Dec 30 1899 2:00PM
06/07/2023 | Alternative | Routine/Scheduled | 17-142-0342 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Treatment Module - recirc - recirc pump, media drapes & spray grid serviced. Treatment Module - discharge - float sensors, pump and controls operating. Pumps to community pump station and absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 10:45AM
07/05/2023 | Alternative | Routine/Scheduled | 06-142-0053 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Riser lids severely damaged by lawn care operations and present a safety hazard !!! Processing Tank - Inlet & outlet lids severely damaged - RSV, recirc pump and effluent screen serviced. Treatment Module - module lid damaged, module corner / lip is damaged - part of module open to the weather! - Media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - lid is fractured / broken - all laterals accepting effluent. System is functioning, but damage to riser lids present a severe safety hazard. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/07/2023 | Dec 30 1899 7:15AM
11/07/2023 | Alternative |  | 033-07-0111-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/05/2023 | Alternative | Reportable Incident | 15-142-0238 | Hanover | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | [] | [] | [18 empty] | This systems blower has been bad for several months, the maintenance has not been done in over 4 years and the system is also missing 3 clean out caps that the company will not move forward with any repairs or maintenances even though they've had emergency pumping's every few months for the trash tank. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/05/2023 | 12:00 AM
06/19/2023 | Alternative | Routine/Scheduled | 128-05-325 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Chlorination | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Chlorination Feeder - serviced - tablets replaced. PUmp Tank - float sensors, pump and controls operating. Drip Field - high tide - under water - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 11:00 AM
06/02/2023 | Alternative | RoutineScheduled | 121-STS-11849 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | -onsite blower no longer functioning upon arrival - replaced blower onsite during visit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 12:00 AM
12/06/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Due for pump out. Refill not required Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Checked and confirmed UV system is functioning properly. Flushed and cleaned UV system Aeration Condition of above Component Notes for above Component Water level normal. Flushed and cleaned weir. Flushed and cleaned diffuser. Not due for pump out Air Pump/Blower Condition of above Component Notes for above Component Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Drip Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 10:19AM
05/01/2023 |  | Routine/Scheduled | 05-120-0095A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/01/2023 | Jan 1 1900 2:03PM
10/18/2023 | Alternative | RoutineScheduled | 107-19-0068 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | E-Z Treat |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
07/17/2023 | Alternative | Follow-Up Component Maintenance | 179-07-0276-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pump out. Reassembled components and water truck refilled tank back to proper levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
09/09/2023 | Alternative | RoutineScheduled | 2042-97-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | SBR |  | Pump | Gravity | Discharge | UV | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NO | Musty | Clear | 6.600000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/11/2023 | 12:00 AM
03/14/2023 |  | Follow-Up | 033-19-0062-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new Orenco UV unit & control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/20/2023 | Alternative | Reportable Incident | 124-STS-2379 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Other"] | ["Other"] | [17 empty] | Pumped Out | Replaced L280 Pump | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/13/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Floats replaced. System should begin to function correctly shortly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/02/2023 |  |  | 17-113-087 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/02/2023 |  | 5.440000 |  |  | 1.300000 |  |  | Will be sent separately |  | BOD: 5.44 TSS: 1.30 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2023 | 12:00 AM
03/31/2023 |  | Follow-Up |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip | Not Applicable | 175.000000 | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | [17 empty] | Microfast system was entirely stopped up newly installed blower was extremely hot from high water level,cleaned unit replaced 2 gauges repaired leak in field installed new blower control audible alarm out on old one | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/02/2023 | 12:00 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/26/2023 |  | RoutineScheduled | 153-STS-20271 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 02/13/2023 | 08:47 AM
01/16/2023 |  | RoutineScheduled | 179-07-0003-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
04/25/2023 |  |  | 08-113-162 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/25/2023 |  | 13.500000 |  |  | 4.000000 |  |  | Will be sent separately |  | BOD: 13.5 TSS: 4.00 SV | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | 12:00 AM
03/24/2023 | Alternative | Routine/Scheduled | 166-15-108 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and cotnrols operating. DBox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 08:00 AM
06/09/2023 | Alternative | Reportable Incident | 107-13-0118 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation","Control Operation"] | ["Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [15 empty] | replaced dispersal pump and floats | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | 12:00 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/09/2023 | Alternative | Routine/Scheduled | 06-172-0141A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Due for pump out. Refill is required for proper operation and to prevent damage to components -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. -RSV: Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drip Field: Flushed and cleaned vortex filter. Found no signs of surfacing on dispersal field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 1:28PM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/07/2023 | 12:28 PM
02/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/28/2023 | Alternative |  | 033-18-0169-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
03/04/2023 |  | RoutineScheduled | 2108-09-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 7.600000 |  |  | 1.300000 |  | 03/06/2023 | Sample Chamber | 12.000000 |  |  | 12.600000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/18/2023 | 12:00 AM
06/27/2023 | Alternative | Routine/Scheduled | 18-120-0272A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/27/2023 | Dec 30 1899 8:48AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-09-0074 SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Semi-Annual Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0212 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Control panel buzzer works but needs to be secured. Motor starters are undersized and do not provide adequate protection. One of the vent pipes was obviously broken. After starting repairs, it was discovered that the 2" force main was also broken. Removed rocks and dirt that had entered the piping (as best as possible). After repairs, ran pump to verify proper flow into the manifold. Added rodent guard to the vent pipe. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | EcoPod | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Zone 1+2 solenoids are not functioning correctly. Strongly recommend thinning out vegetation around panels and tank access. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
02/14/2023 | Alternative | RoutineScheduled Component Maintenance | 175-16-0465 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
01/23/2023 |  | RoutineScheduled | 10-173-089 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 5.000000 | 9500 | Delta |  | Pump | Gravity | Trenches | Not Applicable | 900.000000 | ["Effluent Screens","BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | Jan 1 1900 10:00AM
02/14/2023 |  | Follow-Up |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank plastic lid needs replaced cracked. The 2 gate valves need replaced no handles. And the valve box lid needs replaced there's a big hole in it. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
05/13/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | BioMicrobics MicroFast |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank - 6" solids crust, 6" f solids on bottom of tank. 14" of solids accumulation in treatment unit. 4" of solids in discharge pump tank. Good aeration. excellent treatment quality. Cleaned blower air filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 07:03 PM
08/22/2023 | Alternative | Pump-Out Only |  | York | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Trash tank pumped empty as recommended during last years service visit. Aeration tank pumped empty as recommended ruing last years service visit. Owner to fill tanks !!! - control panels left OFF, Compressor left OFF - owner advised to what level to fill aeration tank, and to turn controls ON when done. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/28/2023 | Dec 30 1899 6:15AM
05/16/2023 |  | RoutineScheduled | 175-05-0059 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0342-VU | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Control Operation"] | ["Level Sensor Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media starting to show its age but still ok. Cleaned filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/20/2023 | Alternative | Routine/Scheduled | 095-STS-7043 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/20/2023 | Dec 30 1899 10:00AM
06/20/2023 | Alternative |  | 16-183-183 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/20/2023 | [7 empty] | Will be sent separately |  | BOD: BDL TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/20/2023 | 12:00 AM
05/12/2023 |  |  |  | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
12/19/2023 | Alternative |  | 07-197-A5 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/19/2023 |  | 12.100000 |  |  | 8.000000 |  |  | Will be sent separately |  | BOD: 12.1 TSS: 8.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | EZ treat unit might need servicing in the near future | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/12/2023 | Alternative | RoutineScheduled | 2018-143-0186 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Other"] | ["Other"] | [17 empty] | Pumped Out | Installed 18" EZSet riser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/30/2023 | Alternative |  | 14-100-0361 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
03/01/2023 |  | Follow-Up | 147-13-0038 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Follow up and repairs conducted from February Inspection. Replaced riser access on trash tank, pump tank. Replaced timer enabled controls for dosing. Replaced air compressors. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/02/2023 | Jan 1 1900 8:45AM
07/11/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Annual and repairs Pumped Regrade conveyance line from house into septic tank, reseal tank and riser Riser with Lid Replace whole lid structure with hinges of advantex treatment unit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 12:00 AM
05/10/2023 |  |  | 2018-143-0234 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Purasys | [6 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
05/10/2023 | Alternative | RoutineScheduled | SD-08-194 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | EZ-Treat Recirculation Tank | Gravity | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump","Other"] | ["Recirculation Pump","Other"] | YES | [17 empty] | Septic Tank-3"sludge 0"scum/ Recirc. Tank-0"sludge 0"scum/ No pump out needed at this time/ Recirc pump intake and spray nozzles cleaned/ Controls, pump, floats and alarms functioning properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/19/2023 | Alternative | RoutineScheduled | SD-12-147 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["SludgeScum Accumulation","Attached Growth Medium","Control Operation"] | ["SludgeScum Accumulation","Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 04:35 PM
08/28/2023 | Alternative | Pump-Out Only |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - pump out of primary septic tank as recommended during a previous service visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | 06:15 AM
08/15/2023 | Alternative | RoutineScheduled | 015-STS-336054 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex RT |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | [18 empty] | Filters cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
05/05/2023 |  | Routine/Scheduled | 09-172-0198A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/05/2023 | Jan 1 1900 1:24PM
11/01/2023 | Alternative | Routine/Scheduled | 093-16-0127 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. Effluent screen is obsolete and discontinued. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. -Aeration: Water level normal. Flushed and cleaned diffuser. Checked and confirmed high level alarm float is functioning properly. Aeration tank was installed backwards. -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. -Control Panel: Checked and confirmed components within control panels are functioning properly. Checked and confirmed audible alarms are functioning properly. Checked and confirmed visual alarms are functioning properly -LPD: Field is blowing out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | Dec 30 1899 10:44AM
12/19/2023 | Alternative | Initial Visit | 800-STS-15568 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. The timer is set to 1 minute 10 seconds every 3 hours. Did not take the initial sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 2:00PM
06/12/2023 | Alternative | Follow-Up Component Maintenance | 033-16-0042-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Follow-up visit to pump septic tank/ATU and install new aspirator tip. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
07/12/2023 | Alternative | RoutineScheduled | 196-15-098 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Elite Onsite | 1942001726 | Drew | Saunders | 3.000000 | 2000 | 1000 | 1000 | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Effluent Screens","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 05:40 PM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
11/20/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | Dec 30 1899 2:55PM
11/15/2023 | Alternative | RoutineScheduled | 109-18-0297 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Routine inspection yearly inspection. Under 1 " scum and 14-16" sludge in septic tank, 6 in sludge in recirc zone, 4" sludge in discharge zone. System is operational. Alarm and floats tested good. Cleaned effluent filter, Tested pumps both good, Checked for alarms and no alarms in history. recirc pump 1445.3hrs and 19,855 cycles and Discharge pump has 38.3 hrs and 1055 cycles- 1497 days in use | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | 182-11-0221 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 09/11/2023 |  | 10.000000 | [5 empty] | Will be sent separately | Inspected | Pumped primary tank Lab sample normal | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
02/06/2023 |  |  | 2018-143-0072 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Aquaklear | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
04/11/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 04/11/2023 |  | 150.000000 | [5 empty] | Will be sent separately | Inspected | sprinkler clog cleaned bulb replaced All tanks pumped | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0209-SPWT | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Cleaned spin filter. Septic tank needs pumping due to sludge levels on treatment side, spoke to customer about it. HL-21, LL-107. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-325 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. media had a little ponding on side away from house due to tipping trade stock, augered and media drained. cleaned tipping trade and made sure it was Distibuting water equally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
08/23/2023 | Alternative | Routine/Scheduled | 12-137-0123 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NO | [17 empty] | Flushed manifold. Water level to low to flush drip field. Filters checked. System appears to be operating normally. Changed discharge off time from 90 min to 180 min. in an effort to have enough water to flush drip during next visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | Dec 30 1899 11:18AM
01/27/2023 | Alternative | Routine/Scheduled | 166-03-689 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Multiflo FTB |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level. Aeration tank - mixing present - aspirator serviced. Pump tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 10:00 AM
01/25/2023 |  | Follow-Up | PPIE-AD5HJ5 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 8.000000 |  | 45.000000 | [5 empty] | Hooked up the pressure switch on the aerator and turned the UV back on. Took 5 year BOD and Fecal samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/25/2023 | Jan 1 1900 12:00PM
03/23/2023 |  | RoutineScheduled | 06-113-019 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/23/2023 | 12:00 AM
09/08/2023 | Alternative | Routine/Scheduled | S 800-13-0259 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 11:18AM
07/28/2023 | Alternative | Routine/Scheduled | none | Giles | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Gravity | Gravity | Discharge | UV | 50.000000 | None | ["BlowerCompressorAerator Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | 6.700000 | 6.800000 |  |  |  | 08/18/2023 | Sample Tap | 12.300000 |  |  | 25.200000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/09/2023 | 05:00 PM
08/17/2023 | Alternative | RoutineScheduled | 165-STS-336632 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2000 | Septic Tank Only | AdvantexAX20RT | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | YES | [17 empty] | The system did not need to be pumped. The effluent filters were both cleaned. The spin filter was cleaned. The textile sheets were sprayed off. The recirculating and discharge pumps were both cleaned. The spray spinners in the treatment unit were cleaned. There was return effluent returning to the pump tank so the drip field was operating as designed. The controls were operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 02:35 PM
04/06/2023 |  | RoutineScheduled | 153-STS-20239 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
06/15/2023 | Alternative | Routine/Scheduled | 06-163-0007 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Best 1 |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/15/2023 | Dec 30 1899 10:41AM
07/25/2023 | Alternative | RoutineScheduled | 153-STS-19084 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [17 empty] | Septic Tank-3"sludge 0"scum/ EZ-Treat Tank Recirculation Tank-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Recirc. pump intake cleaned/ Recirc Counts: Pump-68214 ETM-262691/ Discharge Counts: Pump-213 ETM-13h 55m High-12/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 033-17-0083-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
02/13/2023 | Alternative | Follow-Up Component Maintenance | 175-15-0477 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | UV |  | ["Distribution Pump Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired air relief valve. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
03/29/2023 | Alternative | RoutineScheduled | 133-STS-100802 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced fouled diffuser. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/28/2023 | Alternative | Routine/Scheduled | 093-14-0082 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 1" of solids with 1" of sludge -Discharge/Pump Tank: At normal level Pump and floats functioning properly -Aeration: At normal level Was just pumped out but has about 12" of settled sludge -Air Pump/Blower: Air pump working properly Pulled and cleaned filter -Control Panel: Panel working properly Discharge pump pulling 12.10amps -Drip Field And headworxs: Headworx working properly Pulled and cleaned disc filter Drainfield showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 2:10PM
06/28/2023 | Alternative |  | 177-16-0092-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
05/23/2023 |  | Routine/Scheduled | 2015-143-0160 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [5 empty] | 05/23/2023 | Pump Chamber | [6 empty] | Will be sent separately | Pumped Out | Supervised pumpout of primary septic tank as recommended during last routine service. No refill required - obtained samples for BOD% & TSS to meet 5 year sampling requirement. Samples transported to EnviroCompliance / Analytics Laboratory. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 09:30 AM
04/18/2023 |  | RoutineScheduled | 165-STS-336838 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | EZ Treat |  |  | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation"] | [18 empty] | repaired broken air relief | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/25/2023 | 12:00 AM
01/30/2023 |  | RoutineScheduled | 177-13-0305-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
02/01/2023 |  |  | ST-05-599 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
04/24/2023 |  | RoutineScheduled | 182-10-0146 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.680000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:00 AM
02/24/2023 | Alternative | Routine/Scheduled | 136-08-0168 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | Serviced system - Eco-Flo. Septic tank does not need pumping. Cleaned filter in septic tank. Raked out peat. Pump and floats all working. Replaced alarm light bulb on alarm panel. The peat is going to need to be replaced in near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/24/2023 | 11:00 AM
04/20/2023 |  | RoutineScheduled | 08-113-080 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/20/2023 | 12:00 AM
09/15/2023 | Alternative | Follow-Up | 196.95.016 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced faulty float and septic riser | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/20/2023 | Alternative | RoutineScheduled | 109-STS-32162 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
02/23/2023 |  | Routine/Scheduled | 041-STS-257860 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/23/2023 | Jan 1 1900 3:11PM
07/07/2023 | Alternative | RoutineScheduled | 085-STS-34233 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump","Other"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump","Other"] | [18 empty] | Replaced UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/10/2023 |  | Routine/Scheduled | 228-18-0232 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [5 empty] | 4.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 2:20PM
01/11/2023 |  | Initial Visit | 182-15-0207 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Attached Growth Medium","Septic Tank Baffles","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Dispersal System Operation","Septic Tank Baffles","Recirculation Pump","Distribution Pump Operation"] | [17 empty] | Pumped Out | Baffle clogged. Tanks pumped. Pumps pulled and washed off. Washed Medium | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/11/2023 | 12:00 AM
04/17/2023 |  | Routine/Scheduled |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump, Effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | Jan 1 1900 7:15AM
04/05/2023 |  | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 300.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - Inspection with Local HD in regards to expanding # of bedrooms. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 3 modules - compacted - peatmoss spent - ponding - requires replacement. No standing effluent in sample port. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | 08:15 AM
01/17/2023 |  | Initial Visit | 182-11-0279 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | 12:00 AM
11/03/2023 | Alternative | Routine/Scheduled | 151-09-0003 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Less than 1" of solids with 7" of sludge Pulled and cleaned filter -Discharge/Pump Tank: At normal level Pump and floats working properly -Peat Moss: Tipping bucket working Peat in good shaped Raked out peat -Control Panel: Working properly Visual and audible alarms working Discharge pump pulling 5.6amps | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 11:21 AM
03/29/2023 |  | RoutineScheduled | 177-13-0275-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
04/21/2023 | Alternative | Routine/Scheduled | 073-STS-94546 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/21/2023 | 09:00 AM
03/28/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Manifold was repaired and riser was replaced. System should now function as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/11/2023 |  | RoutineScheduled | 177-STS-88343 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media has filamentus bacteria but not clogged and treatment is crystal clear, will check next year. Blower 2.98. HL 6, LL 27, OVERRIDE 4. "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
01/29/2023 |  | Routine/Scheduled | 149-STS-10659 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/29/2023 | Jan 1 1900 9:00AM
03/27/2023 |  | RoutineScheduled | 177-11-0030-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Effluent Screens"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Effluent Screens"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Removed roots from AX20 unit that were coming through the lid gasket. Treatment nice and clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
11/15/2023 | Alternative | Reportable Incident | S 093-19-0086 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/15/2023 | Dec 30 1899 5:30PM
09/11/2023 | Alternative | RoutineScheduled Component Maintenance | 182-05-0528 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | air supply leak and return line leak | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
10/03/2023 | Alternative | Initial Visit | 18-163-0210 | New Kent | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Installed an aerator rebuild kit. The UV is not working (probably the bulb). The timer is set to 4 minutes every 2 hours 15 mins. Did not take samples due to the UV not working and aerator not working on arrival. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/03/2023 | Dec 30 1899 9:00AM
07/31/2023 | Alternative | RoutineScheduled | 12-113-163 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/31/2023 | 12:00 AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 4 EZ treat nozzles required replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The panel is having issues. Troubleshooting and repair is scheduled. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
12/05/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-15027 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | Musty | Clear | 7.900000 | 19.000000 |  | 0.000000 | [9 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 12/18/2023 | 08:36 AM
05/05/2023 | Alternative | RoutineScheduled | 2007-143-0028 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Other"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation","Other"] | [17 empty] | Pumped Out | Replaced STEP20pump, Air release valve, and 18" EZSet Riser & Lid. Installed Microfast Blower. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled | 16-165-0130 | Northampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 7.000000 | 19.600 | Septic Tank | EZ Treat Sand-Filter | Gravity | Pressure | Trenches | Not Applicable | 6000.000000 | ["None"] | ["None"] | YES | [7 empty] | 05/10/2023 | Pump Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 11:35 AM
12/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 1:20PM
02/28/2023 | Alternative | RoutineScheduled | SD-10-247 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [8 empty] | 18296.000000 | [] | [] | [8 empty] | 02/07/2023 | Sample Tap | 10.000000 |  |  | 4.530000 | 22.180000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
12/22/2023 | Alternative |  | 101-14-0196 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Edmond E & Mary | Traille | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/12/2023 | Alternative | RoutineScheduled | VAG401199 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Singulair/Jet |  |  | Pressure | Discharge | Chlorination |  | [] | [] | [18 empty] | no discharge at this time. Post aeration | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
05/11/2023 |  | Reportable Incident |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Whitewater |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [16 empty] | Inspected | First trip back in 3 years, Routine scheduled visit, found the original discharge pump had failed for sometime, tank overflowing and not pumping to drip drainfield. Was able to replace the pump with a used Orenco pump we had on hand We replumbed and corrected a plummbed loop and added flush valves to both the return line and filter flush, a pressure gauge needs to be added .and the system should return to normal operation. One zone would return some water after flushing the other zone did not flush out, no leaks observed. The septic tank has 1 in scum and 12 " sludge, the treatment tank has 6" sludge and the discharge tank has 12 in sludge. we cleaned the airfilter and checked the zoner valve appears ok. We got water to feed to and seat the drainfield air relief valves. System needs yearly filter cleaning for good operation | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | 12:30 PM
12/12/2023 | Alternative | Routine/Scheduled | 19-142-0172 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Discharge/Pump Tank Condition of above Component Notes for above Component Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Checked and confirmed spray pattern is good Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 12:56PM
05/16/2023 | Alternative | Routine/Scheduled | 15-174-0004S | Prince George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Trash Tank - normal level Aeration tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced - chlorination unit serviced. Discharge point free of debris - rodent guard in place. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/30/2023 | Dec 30 1899 8:30AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-90105 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [5 empty] | 08/16/2023 |  | 7.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Media has filamentus bacteria but not clogging yet, will check next visit. Treatment crystal clear. Grease starting to build up in septic tank, left copy of Do's and don'ts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
01/12/2023 |  | Reportable Incident |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced N161 effluent pump & 3 control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
09/02/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of very "fluffy" solids in septic tank. The solids will compact over time. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 0" of solids in recirculation portion of treatment unit. 1" of solids in discharge portion of treatment unit. Tested floats, pumps and, alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 07:03 PM
07/10/2023 | Alternative | RoutineScheduled | 087-STS-6197 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Elite Onsite | 1942001726 | Drew | Saunders | 3.000000 | 1750 | 500 | 500 | Pump | Gravity | Trenches | Not Applicable | 350.000000 | [] | [] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 05:20 PM
09/14/2023 | Alternative | Initial Visit |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Gravity | Trenches | Not Applicable |  | [] | [] | [18 empty] | Start up done and ready for use | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 12:00 AM
01/30/2023 |  |  | 033-17-0135-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Multi-Flo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 7.510000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:15 PM
10/30/2023 | Alternative | RoutineScheduled | 109-10-0286 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20 RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | New RTU 147826 installed to replace old RTU 123226 - Septic tank Been pumped arranged by owner-In treatment- It has been pumped.- Aranged by owner- Recirc pump and Discharge pumps both operational. Cleaned effluent filter, Alarm operational, Tested float switches- all good. Ran in test mode, Good spray in box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 09:30 AM
11/03/2023 | Alternative | RoutineScheduled |  | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 8.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/09/2023 |  | Follow-Up |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pumped out septic and pump tank. Removed microfast lid. Pressure washed unit. Unit still is clogged with what looks like wipes. We put microfast lid back on for safety. Got into septic tank to pump out under microfast thru the access hole on baffle wall found septic side of tank badly cracked in multiple places. The pump tank the same badly cracked. These tanks are not safe to get in. Told home owner not to drive around them or stand on them. Told owner he needs to contact an AOSE. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
09/11/2023 | Alternative | RoutineScheduled | 175-13-0490 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 09/11/2023 | Sample Chamber | 31.000000 | [5 empty] | Attached to this report |  | Septic Tank-12"sludge 2"scum/ Microfast ATU-16"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Pump out of the Septic-Microfast Tank required/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-2646 ETM-211h 50m On-4m 49s Off-11h 55m/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/07/2023 | Alternative |  | 033-12-0003-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/11/2023 | Alternative | Routine/Scheduled | 199-02-0557 | York | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/11/2023 | Dec 30 1899 11:19AM
02/15/2023 |  | Pump-Out Only | 175-14-0082 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 | 500 | 1000 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/27/2023 | 11:30 AM
11/16/2023 | Alternative | RoutineScheduled | 11-192-077 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/16/2023 | 12:00 AM
04/24/2023 |  | RoutineScheduled | 175-02-0601 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"SludgeScum Accumulation" ,"Control Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Effluent level in Microfast tank was an inch or 2 higher than normal. Media was not clogged as viewed from the top. Recommended pump out due to very heavy scum layer and to hopefully improve treatment. Suspect owner is using one or more products that contain quats. Advised her to review labels and avoid some known harmful products. Pump tank needs pumped out as sludge level is close to the pump intake. Owner to make arrangements with local pumper. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 12/13/2023 |  | 3.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Loudoun Water | 1942001649 | Dakota | Lee | 1.000000 |  | Bio Barrier | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NO | Musty | Clear | 7.680000 | 6.900000 | 100.000000 | [10 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/25/2023 | 08:53 AM
10/13/2023 | Alternative | Routine/Scheduled | 18-120-0042 Conditional | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Recirculation Pump","Septic Tank Baffles"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/13/2023 | Dec 30 1899 4:44PM
01/03/2023 | Alternative | Routine/Scheduled | 234-13-298 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | Dec 30 1899 12:15PM
02/23/2023 |  | RoutineScheduled | SWP-04-406 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots starting to grow inside pod, added Root Destroyer on side with Roots (trees side). Will check next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
05/22/2023 |  | Follow-Up | SP-05-52 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | Installed float tree assembly and set float elevations to proper levels. Installed inlet riser on septic tank. Resealed concrete outlet riser on septic tank. Removed bushes around tanks and set to side for owner to dispose. Repaired broken handle on effluent filter. Augered peat in all pods. Sealed pump tank riser joint on inside; saw a few roots. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
08/14/2023 | Alternative | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 01:54 PM
06/22/2023 | Alternative | Routine/Scheduled | 234-15-202 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | Dec 30 1899 10:00AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/14/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1992 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Jan 1 1900 11:15AM
12/06/2023 | Alternative | Routine/Scheduled | 13-120-0218A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/06/2023 | Dec 30 1899 10:02AM
03/28/2023 |  | RoutineScheduled | 179-STS-89954 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
06/26/2023 | Alternative | Reportable Incident | 151-10-0002 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | 06/26/2023 - pumped septic tank empty for peatmoss changeout. 06/29/2023 - conducted biofilter changeout. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/30/2023 | 07:00 AM
06/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
03/07/2023 |  | Follow-Up | SWP-03-948 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank pumped out by others prior to peat replacement. Degraded peat was removed by hand with pitch forks and new peat was installed. Peat from purchased from Driller Services. Degraded peat was disposed at Spotsylvania Refuse. Pipe from sample box to distribution box runs uphill. Dial-a-flow on line 1 was off, installed a new one. Last header line out of distribution box runs uphill. All OK for now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
03/01/2023 |  | Reportable Incident | 179-14-0222-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite foe system in alarm due to failed discharge pump. Replaced failed pump. Oustaning proposal to correct settled pipes and infiltration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
03/21/2023 |  | RoutineScheduled | 02-113-265 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/21/2023 | 12:00 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-90276 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
10/20/2023 | Alternative | Routine/Scheduled | 810-STS-3980 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 8:00AM
11/27/2023 | Alternative | RoutineScheduled Component Maintenance | -STS-93791 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] |  | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The LPD cleanout is broken, allowing effluent to surface. Owner has cleared this area. Repair to be completed in the near future. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | 08:44 AM
11/04/2023 | Alternative | RoutineScheduled | 109-03-1219 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank and discharge pump tank are scheduled to be pumped out. 20" of accumulated solids in septic tank. 8" of solids in discharge pump tank. Cleaned recirculation pump basket filter. Flushed treatment unit spray manifold. Cleaned treatment unit "sheets" very thoroughly in light of the pump out pending. Excellent treatment quality. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 07:03 PM
01/12/2023 | Alternative | RoutineScheduled | 047-STS-24438 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Leak on septic tank riser. Leak on pump tank riser. Atu has 4" of mud in the outer treatment zone and 8" in the center clarifier. Strongly recommend to pump it. Bad settlement around utu tank (6"-8") no water available to hose test the rest for leaks. Advised customer to get in contact with installer to get repairs done. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 03:56 PM
02/23/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | Dec 30 1899 7:43AM
08/25/2023 | Alternative | RoutineScheduled | 069-16-0125 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
05/05/2023 | Alternative | Routine/Scheduled | 149-STS-10700 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 1000 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | Dec 30 1899 12:30PM
03/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Issues with the distribution boxes were fixed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89329 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Drip field looks way better than last visit, grass growing and no water above ground, no soft spots but kind of wet since it rained a week ago. Will keep an eye on it. RECIRC: HL-8, LL-10, OVERRIDE-1643. DISCHARGE: HL-6, LL-46, OVERRIDE-15. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-86636 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Musty | Black | [13 empty] | Will be sent separately | Inspected | We recommend excavating by hand and resealing all three risers on the pump tank. We also recommend pumping the pump tank due to scum accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
11/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Septic | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV Crystal and Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | Dec 30 1899 11:40AM
03/21/2023 | Alternative | Routine/Scheduled | 119-STS-95924 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - routine service. Trash Tank - normal level Aeration Tank - mixing present - aspirator serviced. Clarifier - effluent screen serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | 09:30 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-1014 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Needs a BOD Test. Low Peat. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/15/2023 | 01:44 PM
12/15/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | [] | [18 empty] | Septic to be scheduled for pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 12:00 AM
07/06/2023 | Alternative | RoutineScheduled | 2085-03-153 | Prince William | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Discharge | Chlorination |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES |  |  | 6.800000 |  |  |  | Ecoli 2420 MPN/100mL | 07/06/2023 | Sample Chamber | 27.000000 |  |  | 18.000000 |  |  | Attached to this report |  | Septic Tank-8"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out required at this time/ Turned peat in all 4 Puraflo Modules, peat in good condition/ Counts: Pump-013921 ETM-0022381/ Controls, pump, floats and alarms functioning properly/ Added chlorine tablets. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12:00 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/11/2023 | Alternative | Initial Visit | 18-174-0090 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Aqua Klear |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - Initial Visit - Real Estate Inspection Primary septic tank - pumped for inspection - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. Unable to locate DBox - require FOIA to be filed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 10:30AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0454-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Leak on pump tank riser and J-box. Will send proposal for repair. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
11/07/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.620000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 02:30 PM
05/03/2023 | Alternative | Reportable Incident | 093-16-0231 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an high level alarm - can hear gurgling in center tank. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Meet with the pumping company and pumped out the septic tank and pumped and cleaned the Clearstream tank. Disconnected the pressure switch on the aerator due to the pumping. The timer is set to 4 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | Dec 30 1899 11:00AM
03/31/2023 |  | RoutineScheduled | 033-07-0267-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | In conjunction with this inspection, drainfield header lines that had clogged with roots were removed & replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Upper right lines might be receiving more effluent than the rest. Recommended to homeowner to contact DSS regarding the possibility of balancing and/or flushing the lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/22/2023 | Alternative | Reportable Incident | 166-09-129 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the alarm and red light. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen.. Installed an aerator rebuild kit. The tanks have root infiltration and need to be pumped out in order to remove roots and the risers need to be sealed. Replaced one valve box with lid - needs one more. It was raining at the time of service and could not check out the drainfield or mound. The timer is set to 8 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 04:15 PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/08/2023 |  | RoutineScheduled | 067-STS-38233 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex RT |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 8" of accumulated solids in septic tank. Cleaned septic tank filter. Flushed treatment unit spray manifold. Excellent treatment. tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 07:03 PM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 061-15-394 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection completed. Airline has settled more since last year and is now leaking air at the sch 80 pvc union. Airline needs to be corrected and the pvc union replaced with a galvanized one. Air filter housing needs to be moved into the blower housing to protect it from rain. Heavy roots penetration at top seam of septic/atu tank, outlet end, are allowing groundwater infiltration and will eventually clog the media. Recommend removing shrubs that are close to the tank. Roots need to be cut off and removed, and the top seam resealed. Bottom float switch (R.O.) has failed (stuck on) and needs to be replaced. Recommend adding adjustable float collars to facilitate future float maintenance. A repair proposal will be sent to the owners. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
01/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | Dec 30 1899 8:47AM
11/14/2023 | Alternative | Routine/Scheduled | 128-13-0022 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Above normal level upon arrival due to weir being clogged 18 in of sludge 1 in of solids Riser is showing signs of leaking -Discharge/Pump Tank: Normal level Heavy sludge on the bottom of the tank Tested floats and pump all working as should however aged All plumbing intact and pump moving water properly however aged Riser showing signs of leaking -Aeration: Normal level Less than 2 in of suspended solids Pulled and cleaned weir Non serviceable air line Float functioning properly Riser showing signs of leaking -Air Pump/Blower: 120 volts coming in Pulled and cleaned filter Air pressure sensor working properly -Control Panel: 120 volts coming in All visual and audible alarms functional Pump pulled 10.22 amps -Distribution Box: Normal level 5 lines all intact and taking water properly -Drain Field: No signs of surfacing Pumping, refill, and installation of a diffuser is to be done at a later date | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 10:39 AM
02/07/2023 |  | RoutineScheduled | 099-15-0088 SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
04/11/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced AP80 compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
02/09/2023 |  | Follow-Up | 175-18-0010 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed new water meter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 10:55 AM
09/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001527 | Jacob | Hott | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/06/2023 |  | Routine/Scheduled | 234-17-0051 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 12:20PM
05/19/2023 | Alternative | Reportable Incident | 157-05-228 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | AOSS - Alarm event. Primary septic tank - normal level Biofilter - high level - Pump Basin - pump / float sensor failure - replaced all ... System requires full service / inspection of biofilter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 01:45 PM
10/11/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-20610 | Wise | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [11 empty] | Aerator running, clear, no chlorine or de-chlorine tablets. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Loudoun Environmental Treatment | 1942001460 | Raymond | Kirkpatrick | 1.000000 | 1500 | MicroFast .75 |  | Gravity | Gravity | Trenches | Not Applicable | 750.000000 | ["None"] | ["None"] | NA | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 2:15PM
02/21/2023 |  | Routine/Scheduled | 13-0140 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 8:35AM
09/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 09/26/2023 | Sample Chamber | 28.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/22/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | 12:00 AM
02/09/2023 | Alternative | Routine/Scheduled | 166-08-313 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 05:38 PM
08/19/2023 | Alternative | RoutineScheduled | S-05-111-0248 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke |  | 1942001505 | John | Burch | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["Control Operation","Level Sensor Operation","Dispersal System Operation"] | ["Control Operation","Level Sensor Operation","Dispersal System Operation"] | NA | None | Clear | 7.700000 | 5.000000 | 0.000000 | [12 empty] | Inspection visit 8-16-2023; ATU operational, pump station level was elevated. Checked function - appeared sensor was not detecting water levels accurately (no float switch system). Returned August 19th to troubleshoot level sensing system - disassembled sensing bell, cleaned and reassembled, adjusted level setting, reinstalled tubing connections. Unit began working properly - showing accurate levels. Controls now working properly and cycling though time dose periods as designed. System should return to normal levels through time dose function of the system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | Jan 1 1900 4:00PM
03/30/2023 |  | Routine/Scheduled | 234-14-313 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | Jan 1 1900 2:15PM
10/05/2023 | Alternative | RoutineScheduled | 150-07-0286 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/06/2023 |  | RoutineScheduled | {FIPSCode}-STS-22991 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/06/2023 | 12:00 AM
03/28/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. UV bulb & chord needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | Jan 1 1900 7:20PM
10/18/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 10/18/2023 |  | 5.000000 |  | 46.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | Dec 30 1899 1:00PM
01/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | Dec 30 1899 11:08AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | pumped all | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
11/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | Dec 30 1899 11:10AM
10/12/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-23367 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 047-STS-27347 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Chlorination |  | ["Attached Growth Medium" ,"Disinfection" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Disinfection"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Owner is consulting with engineer regarding conversion to UV. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
06/13/2023 |  | RoutineScheduled | 175-14-0150 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
08/17/2023 | Alternative |  | 147-09-0101 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 12:00 AM
10/23/2023 | Alternative | Pump-Out Only | 157-12-0074 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | * Arrived for pump out and refill * Pumped 1000 gallons from Aeration tank * Refilled 1000 gallons into Aeration | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 02:18 PM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/12/2023 | Alternative | RoutineScheduled | VAG408062 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Gravity | Discharge | Chlorination |  | ["SludgeScum Accumulation","Dispersal System Operation"] | ["SludgeScum Accumulation","Dispersal System Operation"] | [18 empty] | ET bed redone. Septic pumped out | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/28/2023 | 12:00 AM
05/18/2023 | Alternative | RoutineScheduled | SD-10-168 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 62.500000 | ["SludgeScum Accumulation","Attached Growth Medium","Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 05:00 PM
02/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | 107-06-0679 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 3.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Pad | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | No discharge available for grab sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-333615 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | ET BEd overgrown and leakage identified in bed. Recommend overhaul Et Bed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/23/2023 | 06:57 AM
04/27/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches | Not Applicable | 225.000000 | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 10:00 PM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Floats need replacement in pump tank to modules. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/13/2023 | 11:23 AM
12/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 11:50AM
10/30/2023 | Alternative |  | 154-06-0295 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Tom | Woolfolk | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/12/2023 | Alternative | Follow-Up | 093-STS-14632 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [20 empty] | 2.000000 |  | 25.000000 | [5 empty] | Took BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 12:00PM
06/02/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-86749 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine/ complaint inspection. Alarm was going off due to water in junction box for discharge pump tank, vacuumed water out and alarm went away. RECIRC: HL 13, LL 17, OVERRIDE 1106. DISCHARGE: HL 174, LL13, OVERRIDE 46. RETURN 39 PSI. Valve cover missing lid customer will get from home depot. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
03/07/2023 |  | RoutineScheduled | 099-10-0008-SP | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Blower was not running upon arrival. Replaced blower. Proposal to be sent to clean media in microfast tank. Drip field is failing. Home owner is working with a AOSE to located a new drainfield. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/04/2023 | 04:51 AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
10/12/2023 | Alternative | Routine/Scheduled | 041-STS-261255 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | Dec 30 1899 2:52PM
06/01/2023 |  | Reportable Incident | {FIPSCode}-STS-2863 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/01/2023 | Jan 1 1900 8:00AM
03/09/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | septic | Fast | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 0 Scum, 3" of sludge, 0 Everywhere else. Field good and dry. Changed from demand dose to time dosed 6 min 45 sec on, 2 hrs off. Blower, floats alarms, and pump are all operational. Pump cycles 537 run time 164h 35m. Lids for the risers do not fit tight, I recommend that you have your contractor fix this | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:05 PM
02/16/2023 |  |  | 179-STS-87675 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
05/11/2023 |  | RoutineScheduled | 11-172-0100A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
11/06/2023 | Alternative | RoutineScheduled | 03-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 8 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/06/2023 | 12:00 AM
02/06/2023 |  | Routine/Scheduled | 09-163-0118 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Processing Tank - Recirc - Recirc pump, media drapes & spray grid serviced. Processing Tank - Discharge - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | Jan 1 1900 7:15AM
11/11/2023 | Alternative | RoutineScheduled | 2115-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Attached Growth Medium","Control Operation","Disinfection","Level Sensor Operation"] | YES | Musty | Clear | 7.800000 |  |  | 2.100000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/13/2023 | 12:00 AM
04/13/2023 |  | Reportable Incident | 179-12-0021-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Recirculation Pump" ,"Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Owner called about alarm. Tanks not in high level, but electronic log in control panel indicated recirc high level alarms had been occurring since 3/22. Reduced local alarm delay from the default setting of 1140 minutes to 180 minutes. Found return line ARV for zone one snapped off near ground level. This allowed grit/ pebbles to lodge in the field flush valve and recirculate too much of each cycle back to the septic tank. Repaired ARV connection and flushed the return line. Removed debris from field flush valve. Tested drip rates. Replaced both zone check valves (found together at bottom of zone 1 rather than typical location of each one being located next to their respective return line ARV). Discussed switching drip manifolds from side feed to top feed, owner declined. Flush rate is well above design. Due to conditions observed during 3/8/22 repair to the force main between the pod and hydraulic unit, it is believed that the return to septic line is broken where it tees into the 4" sewer line. That connection needs to be dug up and inspected/ repaired. The plastic riser (outlet end of septic tank) appears to be leaning. This can occur when the plastic septic tank distorts after backfilling. Installer was supposed to bring risers to grade on both ends of tank, but did not. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
09/21/2023 | Alternative | RoutineScheduled | 08-100-0772 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1500 | BIOCOIR |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [16 empty] | Pumped Out | PUMPED SEPTIC TANK REPLACED N98 SEWAGE PUMP AND FLOAT REPLACED FIBER REPLACED VENT | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/01/2023 | 02:55 PM
09/05/2023 | Alternative | Routine/Scheduled | 13-163-0002 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/05/2023 | Dec 30 1899 1:54PM
09/07/2023 | Alternative | Initial Visit | 10-167-038 | Nottoway | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Retaw Engineering LLC | 1965008335 | Ginasiyo | Mutoti | 10.000000 | 60000 | Settling Tank | Equalization/Pre-Anoxic | Pump | Gravity | Trenches | Not Applicable | 0.000000 | ["Distribution Pump Operation","SludgeScum Accumulation"] | ["Distribution Pump Operation","None"] | NA | None | Clear | 7.200000 | 1.000000 | 0.000000 | 0.000000 | No | 09/07/2023 | Sample Chamber | 4.600000 |  |  | 0.000000 | 32.800000 |  |  |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/01/2023 | Dec 30 1899 6:15PM
04/05/2023 | Alternative | RoutineScheduled | 12-184-5001 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/05/2023 | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 177-11-0013-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend removing the trees growing along the upper and bottom line of the dispersal area as well as those growing at the top of the dispersal area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2024 | 07:56 AM
09/22/2023 | Alternative | Reportable Incident |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Multiflo FTB | [6 empty] | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 02:07 PM
02/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/26/2023 |  | RoutineScheduled | 179-08-0154-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Removed roots that were near the tops of the pods and applied Root Destroyer in a attempt to kill the roots growing in. Sprayed for ants in the 5th pod from left. Replaced AAA battery in the control panel, reset date & time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
05/02/2023 | Alternative | Pump-Out Only | 10-160-0079 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 3.000000 | 3000 | Whitewater | [6 empty] | [] | [] | [17 empty] | Pumped Out | Pumping & Cleaning Septic Tank, Pretreatment, and Pump Chamber (1000 gallons each) JOB SCOPE: Pumped/cleaned septic tank; septic system is functioning at this time but not as designed as there are components that are recommended to be repaired/replaced. - in process of repairing blower | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/03/2023 | 12:00 AM
10/23/2023 | Alternative | RoutineScheduled | 18-142-0253 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | SBR Geomat |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
04/26/2023 |  | Routine/Scheduled | 228-14-0013 | Virginia Beach | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [16 empty] | Replaced aerator and diffuser. UV is not working. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/26/2023 | Jan 1 1900 8:00AM
07/18/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
07/20/2023 | Alternative | Routine/Scheduled | 166-17-0168 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level - Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Riser Access for the 3 compartment tank located slightly below grade due to landscaping! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 07:30 AM
02/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator control panel was replaced and the system appears to be functioning as designed at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
08/24/2023 | Alternative | RoutineScheduled | 05-113-031 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 5 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/24/2023 | 12:00 AM
07/19/2023 | Alternative | RoutineScheduled | 91-100-0414 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | SAND FILTER |  | Pump | Gravity | Pad | Not Applicable | 300.000000 | [] | [] | [18 empty] | EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 01:10 PM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
11/02/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [18 empty] | roots removed from pump tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 12:00 AM
02/01/2023 | Alternative | Reportable Incident | SD-11-18 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm in recirc tank. Observed a small, but steady flow of water from the house #4493. House currently vacant. Advised property manager to send their maintenace man by to check for running toilets, etc. The tenant at #4485 (shared septic) had already checked his toilets. The recirculation pump flow was noticeably reduced due to a badly clogged spinner nozzle (inlet end of tank). Replaced the spinner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/31/2023 | Alternative | RoutineScheduled | 085-STS-31563 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
03/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The septic/ atu microfast tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
07/10/2023 | Alternative | Routine/Scheduled | 228-18-0232 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 3:55PM
12/13/2023 | Alternative | RoutineScheduled | S16-180-0008 | Roanoke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Fast Biomicrobics |  | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Sludge levels-- -trace scum/ 12" sludge in Septic tank. 12" in treatment zone. Treatment Tank had no aeration and blower was hot (locked up), found the air line had disconnected and due o pressure bent the pipe, Returned 12 20-23 to replace and repair the blower, system returned to normal after. Replaced the main air header line due to the bent pipe to make and glue the fitting tight to blower and no leak exhist anymore. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/28/2023 | Dec 30 1899 9:30AM
08/28/2023 | Alternative | Reportable Incident | 124-STS-2379 | Goochland | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Rejected | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3250 | 1250 | 1000 | [5 empty] | [] | ["Attached Growth Medium","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Cloudy | [16 empty] | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 08/28/2023 | 12:00 AM
10/13/2023 | Alternative | Reportable Incident | 12-113-205 | Buchanan | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | Aerator down. Left loaner aerator. 5 - Blue Crystal tablets installed 15 - Bio Max tablets installed | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 10/13/2023 | 12:00 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | NeeComponents marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalitiesds floats in pump to module tank. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Floats need replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/29/2023 | 12:05 PM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0471 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0387 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
12/19/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 1:35PM
01/23/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/27/2023 | 07:00 PM
04/05/2023 |  | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Hoot |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor service. Pump Tank - sensor probe operating, pump and controls operating. Splitter Valve - serviced. DBox - 2 - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | Jan 1 1900 8:15AM
03/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/24/2023 | Dec 30 1899 8:34AM
04/10/2023 | Alternative | RoutineScheduled | 13-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/10/2023 | 12:00 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/28/2023 | Alternative | RoutineScheduled | 073-STS-96140 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 12:00 AM
11/30/2023 | Alternative | Reportable Incident | 196-11-040 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced failed compressor, cleaned filters, system check - okay | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
01/17/2023 |  |  | 033-07-0111-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/31/2023 | Alternative | RoutineScheduled | 182-14-0296 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Repair pump line, replace pressure gauge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 12:00 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/17/2023 |  | Initial Visit |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  | Gravity | Pressure | Drip | Not Applicable |  | [] | [] | [18 empty] | Operating as designed but needing corrections by installer. Recirc plumbing at union doesn't line up and is leaking. (Union possible cross threaded and difficult to turn). There isn't any fall between incoming and outgoing in septic tank. Vertical support in septic would not stay in slot and falling down in tank. Vent pipe should be straightened to prevent accumulating water and restricting air flow | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:00 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/05/2023 | Alternative | RoutineScheduled | 17-172-0455A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | Advantex |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
04/29/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. 0" of accumulated solids in discharge pump tank. Flushed treatment unit spray manifold. Cleaned recirculation pump solids basket filter. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 07:03 PM
05/23/2023 |  | Initial Visit | 133 09 0386 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Control Operation","Recirculation Pump"] | ["Control Operation","Recirculation Pump"] | NA | [17 empty] | Initial startup visit. Verified correct wiring and operation of floats, pumps and alarm. Set recirculation pump timers and override timers. Set recirculation pump flow rate. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 07:03 PM
02/28/2023 |  | RoutineScheduled | SWP-04-488 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1250 | 0-3 | 0-0 0-0 2 pump tanks | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 5.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | 11:00 AM
02/07/2023 |  | Routine/Scheduled | 550-STS-6679 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | Jan 1 1900 7:30AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/13/2023 | Alternative | RoutineScheduled | 171-17-0062 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Discharge | UV |  | ["Auxiliary Filter","Disinfection","Recirculation Pump"] | ["Auxiliary Filter","Disinfection","Recirculation Pump"] | NA | [17 empty] | Annual inspection. 14"of accumulated solids in first portion of septic tank. 22" of accumulated solids in septic tank. Septic tank solids filter very clogged and restricting flow to treatment unit. Cleaned septic tank solids filter. The septic tank should be pumped out. Flushed treatment unit spray manifold. Cleaned recirculation pump intake screen. 12" of solids in recirculation portion of treatment unit. 14" of solids in discharge portion of treatment unit. Recirculation and discharge portions of treatment unit should be pumped out when septic tank is pumped out. UV bulb teflon sleeve discolored preventing proper light transmittance for disinfection. The Teflon sleeve needs to be replaced to allow proper disinfection. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 07:03 PM
06/16/2023 | Alternative | RoutineScheduled | 015-STS-333663 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | 12:00 AM
03/22/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System was in alarm when we arrived. Found recirc pump clogged with wipes. Found header line very green dug up d-box found i speed leveler on line 1 was off. It appears that effluent is getting out around the pipes. D-box needs reparged. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
11/07/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] |  | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | Dec 30 1899 10:06AM
08/08/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Blue Ridge | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Septic tank and Treatment tank pumped out and refilled. Filter cleaned. Dug up and repaired conveyance between septic tank and treatment tank which had settled and raised the outlet tee. Now has 1" of fall between the tees. Recirc splice box was full of water and the alarm float was not connected anymore, this was repaired. System should return to normal operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/09/2023 | 07:44 AM
12/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0212-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Bio Barrier | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Ran camera down header lines and header lines are blocked with roots. Proposal to be sent to repair header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/05/2023 |  | RoutineScheduled |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 3.000000 | 4000 | Septic | White Knight | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["SludgeScum Accumulation","Effluent Screens","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 10:30AM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
04/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | AP80 compressor is bad and needs replaced. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 12:48 PM
12/18/2023 | Alternative | RoutineScheduled | 107-08-0123 | Augusta | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | FAST clogged. scheduled for repair 1/16/24 and pumping of tanks. Blower replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/03/2024 | 12:00 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 107-16-0101 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/03/2023 |  | 91.000000 | [5 empty] | Will be sent separately | Inspected | Primary tank pumped Repaired alarms on both panel | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
08/14/2023 | Alternative |  | {FIPSCode}-STS-1948 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/14/2023 |  | 10.100000 | [5 empty] | Will be sent separately |  | BOD: 10.1 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/14/2023 | 12:00 AM
03/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0990 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Whitewater ATU | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
02/13/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
07/11/2023 | Alternative | RoutineScheduled | 003-STS-32956 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Pressure | Discharge | UV | 450.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES |  |  | 6.900000 | 8.200000 |  |  |  | 07/11/2023 |  | 13.000000 |  | 108.600000 | 5.120000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 12:00 AM
02/15/2023 | Alternative | Routine/Scheduled | 159-13-0120 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 2000 | Clearstream | Clearstream | Pump | Gravity | Trenches | Not Applicable | 1000.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - recommend pumping - Secondary septic tank - normal level - effluent screen serviced. Flow Equal Tank - float sensors, pump and controls operating. Aeration #1 - normal level - mixing present - compressor serviced. Aeration #2 - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | 07:45 AM
01/20/2023 |  | RoutineScheduled | 177-14-0047-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
08/28/2023 | Alternative | Reportable Incident |  | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [17 empty] | Alarm event - compressor failed over weekend - was noted to be showing signs of failure during last service visit - compressor replaced - system placed back into operation. Due for full service December 2023. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/31/2023 | 08:00 AM
11/20/2023 | Alternative | RoutineScheduled Component Maintenance | 177-10-0019-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the aerobic treatment unit due to sludge accumulation in the tank. It may be advisable to pump the septic tank at the same time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
05/15/2023 |  | Reportable Incident |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | COSS - Maintenance - GMP2019-02 Replaced sewer line from foundation to septic tank. Installed new inlet baffle Parged tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 06:30 AM
07/21/2023 | Alternative | Reportable Incident | 800-03-0502 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/21/2023 | Dec 30 1899 8:00AM
11/07/2023 | Alternative | Routine/Scheduled | 136-14-0238 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal Level 15" of sludge and 2" of solids No signs of infiltration -Discharge/Pump Tank: Normal Level 15" of suspended solids All floats and pump are functioning properly however they are Aged Plumbing is outdated Pump and float connections are in shrink connections -Aeration: Normal Level 12" of suspended solids Could visually see treatment happened -Air Pump/Blower: Air blower is pulling 3.17amps Pulled and blew out air filter. -Control Panel Discharge: Notes for above Component 120v All audible and visual alarms are functioning properly Pump pulled 9.78amps -Distribution Box: Concrete distribution box above grade in good condition with 3 lines taking water. -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 11:36 AM
01/27/2023 |  | RoutineScheduled | 179-STS-91961 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 01/27/2023 | [10 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/31/2023 | Alternative | RoutineScheduled | 137-STS-25555 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Pressure | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
02/20/2023 |  | RoutineScheduled | 101-14-0257 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Recirc Sand Filter |  | Pump | Pressure | Drip | Not Applicable | 145.000000 | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation","Recirculation Pump","Auxiliary Filter","Effluent Screens"] | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation","Recirculation Pump","Auxiliary Filter"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 01:15 PM
10/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/15/2023 |  | RoutineScheduled | 05-113-031 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/15/2023 | 12:00 AM
07/18/2023 | Alternative | Follow-Up Component Maintenance | ST-02-195 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed top seam of Recirc tank at root penetrations. Tank pumped out by Marshalls in order to remove roots and locate actual root penetrations. Resealed distribution box as best as possible. Applied root kill around distribution box. No warranty against roots. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/24/2023 | Alternative | Routine/Scheduled | 15-120-0187A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Not due for pump out -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level low. Control panel indicates low usage. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly -Drip Field: Flushed and cleaned vortex filter. Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | Dec 30 1899 9:49AM
02/17/2023 |  | RoutineScheduled | 099-STS-89510 | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | There is still effluent coming to the surface in the drip dispersal area. Owner called with alarm that was partially due to a constant return of water from the drip system. Engineer approved adding a spring-loaded check valve. Parts have been ordered. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
09/18/2023 | Alternative | RoutineScheduled | 128-10-016 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system in alarm on arrival due to tripped breaker. returned system to normal working conditions. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/06/2023 | Alternative | RoutineScheduled | 08-197-A9 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEAN H2O MACHINE |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets installed 6 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/06/2023 | 12:00 AM
06/23/2023 | Alternative | Reportable Incident Component Maintenance | 179-06-0417-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite due to tricheck coming unglued. Reglued tricheck. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
11/21/2023 | Alternative | Routine/Scheduled | 136-93-0576 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level No riser access There is a power feed running beside the Inlet lid Has 6" of sludge less than 1" of solids -Discharge/Pump Tank: At normal level Plumbing is aged and has some brass checks Pump and floats working properly -Control Panel: Panel working properly Pump pulling 11.09amps Visual and audible alarms working -LPD: Showing no signs of surfacing Globe valve located in a handmade wooden well | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 03:41 PM
03/31/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2673 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Jan 1 1900 3:00PM
02/15/2023 |  | Routine/Scheduled | {FIPSCode}-STS-21544 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump |  | Trenches | Not Applicable | 250.000000 | ["Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [17 empty] | Effluent filter was clogged. Septic tank effluent pH needs to be tested. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/16/2023 | Jan 1 1900 8:20AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 107-06-0564 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced visual alarm bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
02/13/2023 |  | Follow-Up | 13-120-0417 VU | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | None | None | NO | Musty | Clear | [5 empty] | 02/13/2023 | Sample Chamber | 3.000000 |  |  | 4.500000 |  |  |  |  | 5 year sampling results. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 7:30AM
07/19/2023 | Alternative | Initial Visit | 115-STS-96372 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Pumped out the septic tank. The timer is set to 2 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 11:50 AM
03/20/2023 |  | RoutineScheduled | 179-18-0070-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Septic tank had a spike in growth from last year. Homeowner will look into different products being used in the house. Tank was pumped out the next day to restart the treatment. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
02/17/2023 |  | Follow-Up | 149-STS-20262 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV Bulb. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
02/09/2023 |  | RoutineScheduled | 177-16-0175-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
03/05/2023 |  | Reportable Incident | 228-14-0398 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/05/2023 | Jan 1 1900 1:00PM
08/09/2023 | Alternative | Routine/Scheduled | 18-120-0136AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/09/2023 | Dec 30 1899 4:45PM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
02/24/2023 |  | RoutineScheduled | 175-03-0287 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 | 2375 | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
03/01/2023 |  | RoutineScheduled | 02-163-0141 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 12:00 AM
02/16/2023 | Alternative | RoutineScheduled | 05-160-0339 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 |  | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NO | Septic | Discolored | [15 empty] | - recommend tank be pumped and cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | 12:00 AM
02/03/2023 |  | Routine/Scheduled | 234-17-322 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | Jan 1 1900 11:40AM
12/14/2023 | Alternative | Routine/Scheduled | 09-137-0210 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Flushed and cleaned laterals. Checked and confirmed spray height. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Distribution Box Condition of above Component Notes for above Component Water level normal. Structural integrity of distribution box appears to be intact Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 10:08AM
05/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 | 1250 |  |  | Pump | Gravity | Pad | Not Applicable |  | ["Other"] | ["Control Operation","Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation"] | YES | [17 empty] | needs new concrete lid for pump tank cracked and brittle. falls apart when you pick up | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/14/2023 | 12:00 AM
11/06/2023 | Alternative | RoutineScheduled | 133-STS-105354 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 7.600000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 02:30 PM
05/19/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Distribution Pump Operation","Level Sensor Operation"] | ["Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | Service call only: Found Zoeller E-189 pump and off float was faulty. Replaced both at the club house. Counts: Pump1-17600 ETM-3510h 44m/ Pump2-28967 ETM-2694h 3m/ Peak-8934/ High-1989/ Off-4h On-17m | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/05/2023 | Alternative | Routine/Scheduled | 550-STS-6314 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Dec 30 1899 8:10AM
02/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation","Dispersal System Operation"] | [] | NA | [17 empty] | Septic Tank-12"sludge 2"scum/ Microfast-16"sludge (Pump out required) Pump Tank-1"sludge/ Blower air filter cleaned and blower working properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-3494 Pump run-261h/ Hand -4/ High-19/ Override-11/ Watermeter-17,504.2/ No breakout or spongy areas on the drip field/ K-Rain Zoner is broken and requires replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
07/19/2023 | Alternative | RoutineScheduled | 02-163-0446 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Advantex |  | Pump |  |  |  |  | [] | ["Attached Growth Medium","Recirculation Pump","Control Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 12:00 AM
03/15/2023 |  | Follow-Up | SWP-03-67 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Added inlet riser on septic tank and sealed pump tank wedge lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
02/22/2023 |  | Routine/Scheduled | 800-05-0191 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | Jan 1 1900 8:00AM
01/25/2023 | Alternative | Routine/Scheduled | 115-STS-96591 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Purasys |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | Musty | Clear | [5 empty] | 01/25/2023 | Sample Chamber | [8 empty] | 180 day post install inspection. Primary septic tank - normal level Processing tank - sludge return - operating. Processing Tank - aeration - mixing present - compressor serviced. Processing Tank - discharge - pump, float sensors, & controls operating. DBox - intact GeoMat Pad - intact - no surfacing noted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | 11:30 AM
06/20/2023 |  | Reportable Incident | 179-07-0363-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1500 | 1-2 0-2 0-0 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 7.000000 | [11 empty] | Inspected | replaced panel with upgraded model. system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 11:00 AM
12/12/2023 | Alternative | RoutineScheduled | 150-06-360 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | sludge checked, system check okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/27/2023 | Alternative | RoutineScheduled | 154-15-0128 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
01/09/2023 |  | RoutineScheduled | 18-160-0126 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1000 | Aqua Safe Precast | Aqua Safe 600 | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | ["Other"] | ["Other"] | NA | None | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 02:00 PM
01/26/2023 |  | Routine/Scheduled | 093-03-0087 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 4:00PM
12/14/2023 | Alternative | RoutineScheduled Component Maintenance | SD-08-60 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. Back wash valves working good. Will check next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-02-143 | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Control Operation" ,"Dispersal System Operation" ,"SludgeScum Accumulation"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Septic | Black | [13 empty] | Will be sent separately | Inspected | The alarm light and horn are not responding. There appears to be effluent surfacing from the lower drainfield line. As noted previously, we recommend removing the trees growing near the distribution box. Once that is done, we can uncover the distribution box and attempt to remove any roots that may be clogging the lines. We also recommend pumping the Advantex recirculation tank due to the sludge accumulation in the tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | 08:44 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | One of the pumps is not functioning. Lots of scum in pump chamber. Recommend pumping all tanks. Drainfield is waist high grasses. Recommend mowing and keeping it shorter, but there were no signs of failure in the field. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
04/24/2023 |  | RoutineScheduled | 14-120-0113A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["Effluent Screens","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 12:00 AM
03/11/2023 |  | Reportable Incident | 228-04-0674 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo | [6 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump with Zoehler 152 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/11/2023 | Jan 1 1900 3:00PM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping ATU | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Zone return valve opens intermittently while dosing, but does not appear to be an issue. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/05/2023 | Alternative | Reportable Incident | SWP-03-379/SWT-04-225 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-3 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 4.000000 | [11 empty] | Inspected | replaced discharge pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 10:00 AM
07/15/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/08/2023 | 12:00 AM
06/23/2023 | Alternative | Routine/Scheduled | 150-07-051 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effleunt screen serviced. Treatment module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | 01:00 PM
01/19/2023 |  | RoutineScheduled | 179-18-0449-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Control Operation" ,"Disinfection"] | ["Septic Tank Baffles" ,"Recirculation Pump" ,"Level Sensor Operation" ,"Disinfection" ,"Control Operation" ,"Attached Growth Medium"] | NA | None | Clear | [5 empty] | 01/19/2023 |  | 6.000000 |  | 1.800000 |  |  |  | Will be sent separately | Inspected | Routine inspection. Sample taken. Leak on pump tank inlet riser (12" ribcore extension). Leak on pump tank outlet riser (jbox gasket). Fixed Leak on gate valve by putting O-ring back in place and making it tight. All "R" counts back to zero. 34 psi. RECIRC: HL 0, LL 9, OVERRIDE 1. DISCHARGE: HL 2, LL 7, OVERRIDE 0. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
09/25/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced pump, pump float and override float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/25/2023 | Dec 30 1899 7:30AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Strongly recommend clearing the mounds. The vegitation is starting to get larger and thicker closer to the mounds. Machines should not be used and it should be cleared by hand. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | Dec 30 1899 4:23AM
02/21/2023 |  | Initial Visit | 015-STS-333235 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | 12:00 AM
04/17/2023 | Alternative | RoutineScheduled | SD-12-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/08/2023 | Alternative | Routine/Scheduled | 800-STS-14289 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | Dec 30 1899 11:30AM
12/13/2023 | Alternative | RoutineScheduled | 2128-10-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.140000 |  |  |  |  | 12/14/2023 |  | 2.000000 |  |  | 4.800000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/28/2023 | 01:15 PM
04/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/14/2023 |  |  | 2006-143-0347 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1250 | 1250 | 1000 | Pump | Pressure | Mound | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Attached Growth Medium"] | YES | Pungent | Clear | 7.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 11:00 AM
05/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 2125 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled | 09-192-262 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | PURFLO |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 12:00 AM
09/10/2023 | Alternative |  | 101-14-0476 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Troy jenkins jr | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/13/2023 | Alternative | RoutineScheduled Component Maintenance | 196-07-244 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend filling in eroded areas and removing the large tree/bush that appears to be growing in the upper middle part of the dispersal area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89976 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The dispersal area for the septic system is across the creek. and is currently not accessible. This area should be maintained in a mowed condition to prevent roots from growing into the darinfield lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/28/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1983 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | Jan 1 1900 11:40AM
02/07/2023 |  | Routine/Scheduled | 04-120-0485AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the aerator. Changed the diffuser in the Clearstream. The timer is set to 3 minutes every 1.5 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | Jan 1 1900 11:30AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 11:24 AM
06/12/2023 | Alternative | Routine/Scheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Pressure | Trenches |  | 300.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 10:41 AM
06/01/2023 | Alternative | Routine/Scheduled | 166-16-144 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Serivce Primary septic tank - normal level - effluent screen serviced. Biofilter - peatmoss in good condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 11:15 AM
02/01/2023 |  | RoutineScheduled | 110-Discharge-6299 Wilderness Rd. | Bland | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Septic Tank Baffles","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 4 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/01/2023 | 12:00 AM
09/21/2023 | Alternative | RoutineScheduled | 02-197-A5 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 6.000000 |  | 0.000000 | [11 empty] | This system needs to be in John Ramsey I have sent Charlie the paperwork | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/05/2023 | Alternative | Routine/Scheduled | 10-120-0179AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | Dec 30 1899 10:13AM
11/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930322 | Shane | Majewski | 1.000000 |  |  |  | Pump | Gravity |  | Not Applicable | 750.000000 | ["None"] | ["None"] | NA | [17 empty] | system mal-functioning- problem appears as poor installation of system purchase date of new home Jan 2022 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/27/2023 | Dec 30 1899 12:45PM
08/10/2023 | Alternative | RoutineScheduled | 2019-143-0048 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/30/2023 |  | RoutineScheduled | 177-07-0442-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Level Sensor Operation" ,"Distribution Pump Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Annual inspection. Effluent level in pump tank was only about 7" deep due to extra pump cycles occurring from a failed timer enabler float switch (stuck on). Replaced the float switch. During drawdown test, heavy spray was observed coming from the side of the brass check valve. Pulled pump out with some difficulty (top of pump was pretty rotten which allowed the lift rope to pull free). Upon closer inspection, the entire pump was very corroded and owner agreed to replace it. Also replaced the check valve, about 5' of pipe, and most of the pvc fittings. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/29/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | 12:00 AM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20509 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
06/13/2023 | Alternative |  | 101-17-0443 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | William | Alexander | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/12/2023 | Alternative | RoutineScheduled | 107-02-0926 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
06/26/2023 | Alternative | Routine/Scheduled | 550-STS-6635 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | Dec 30 1899 12:25PM
03/17/2023 |  | RoutineScheduled | 179-18-0297-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Treatment looks very good. Blower amps 2.9. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
11/16/2023 | Alternative |  | 08-184-5003 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/16/2023 |  | 2.130000 |  |  | 2.000000 |  |  | Will be sent separately |  | BOD: 2.13 TSS: 2.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 079-STS-31232 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/31/2023 |  | 28.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
02/09/2023 | Alternative | Routine/Scheduled | 136-01-069 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - Plastic - fractured - requires replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/13/2023 | 08:00 AM
09/01/2023 | Alternative | Routine/Scheduled | 12-190-004 | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None |  | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | Dec 30 1899 10:30AM
04/28/2023 |  | Initial Visit | VAG408348 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST ATU | Constructed Wetlands | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation"] |  | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/07/2023 | 10:30 AM
02/17/2023 |  | Pump-Out Only | 234-13-320 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [28 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | Jan 1 1900 10:00AM
03/10/2023 |  | Pump-Out Only | 147-11-0066 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 | 500 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
05/01/2023 |  |  | 193-STS-92823 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
10/06/2023 | Alternative | Routine/Scheduled | 041-STS-259444 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Fuji |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/06/2023 | Dec 30 1899 11:06AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Zone return valve opens intermittently while dosing, but does not appear to be an issue. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/07/2023 |  | RoutineScheduled | 02-197-122 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 12:00 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/05/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump chamber wall appears to be compromised. Homeowner is looking into process of repair. Dwelling in not occupied. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
04/04/2023 | Alternative |  | 061-17-315 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
01/17/2023 |  | RoutineScheduled | 153-STS-20275 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | UV |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [17 empty] | Septic-4"sludge 2"scum/ Recirc side-3"sludge 0"scum/ Drip Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Recirculation pump (Step-20) not working and requires replacement/ Controls, pumps ( After replacement of Step-20) floats and alarms functioning properly/ EZ-Treat orifices cleaned/ Counts: EZ-Treat pump-74082 ETM-414870/ Discharge High-46/ Pump-2869 ETM-410h 26m/ Watermeter-116635.032/ No breakout or spongy areas on the drip field and dosing properly. Step-20 EZ-Treat was replaced. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/14/2023 | Alternative | Follow-Up Component Maintenance | 179-STS-90050 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Degraded peat was removed by hand and new peat was installed. Peat was purchased from Driller Services. Degraded peat was disposed at Spotsylvania Refuse. Added root destroyer to all pods. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
06/08/2023 | Alternative | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Loudoun | Hott's Septic Service LLC | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | [8 empty] | 06/08/2023 | Sample Chamber | 3.000000 | [5 empty] | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/08/2023 | 12:00 AM
01/09/2023 |  |  | 179-19-0123-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/19/2023 | Alternative | RoutineScheduled | 166-14-137 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/09/2023 | Alternative | Reportable Incident Component Maintenance | 175-05-0108 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Owners said septic odor started after atu blower was off for a few days due to tripped breaker. Blower working fine today and has been since breaker was reset. Domed lid of atu tank was found to be leaking last December. Has not impacted system lately due to lack of significant rain. Atu vent was also found to be a point of groundwater infiltration as it was nearly completely buried in mulch. Added about 8" to the vent today to allow for proper ventilation and to stop it from leaking in heavy rain. Sealed both concrete lids with silicone caulk to help contain any septic odors. Recommend pump-out of the atu tank. Owners to make arrangements. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
04/11/2023 |  | RoutineScheduled | 179-STS-91626 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [6 empty] | Drip |  | 10200.000000 | [] | [] |  |  |  | 7.650000 | 1.400000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 03:10 PM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-91782 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | NA | None | Clear | [5 empty] | 07/18/2023 |  | 42.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Blower 2.82 amps. Wipes and grease starting to accumulate in septic tank, gave customer copy of Do's and don'ts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
10/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Loudoun Environmental Treatment | 1942001460 | Raymond | Kirkpatrick | 1.000000 | 1500 | Microfast .75 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
04/11/2023 |  | Reportable Incident | 159-09-171 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Repaired the broken airline. The timer is set to 8 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/11/2023 | 05:15 PM
03/21/2023 | Alternative | Routine/Scheduled | 136-04-812 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration Tank - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | 10:00 AM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-87934 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Recirc contactor has been setting of a alarm. Changed alarm delay to prevent this false alarm per orenco. Homeowner will contact me directly if alarms continue. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
12/27/2023 | Alternative | RoutineScheduled Component Maintenance | 182-02-0418 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | sandfilter intake clog repaired bad contactor on recirc replaced | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
08/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0326-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
04/11/2023 | Alternative | RoutineScheduled | 115-02-0503 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank |  | Pump | Pressure | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-2-4" Scum & 12" Sludge in Septic tank. Pump Tank - Trace of sludge. Checked Pump runs good. Alarm operates. Clear Effluent. Drainfield inspection caps look good on the valve boxes on the LDP drainfield Valve covers and the drainfield appears dry. 14 vavles located and about 6 ends caps located opened and flushed. Owner may look for the other buried end caps in the mulched flower beds, we flushed out the lines we opened and located. Appears fully opperational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 09:30 AM
01/19/2023 |  | RoutineScheduled | 175-17-0098 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Effluent level in MicroFast is high. It has been determined conveyance line needs to be lowered to pump tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/13/2023 | 08:47 AM
07/20/2023 | Alternative | Reportable Incident | 151-14-0096 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - they had a running toilet. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Fixed the grade on the pipe in the Clearstream. The timer is set to 6 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 09:00 AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | new home possibly over supply line notified Kent Shelton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/20/2023 |  | Routine/Scheduled | 085-STS-32029 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/20/2023 | Jan 1 1900 9:26AM
03/27/2023 | Alternative | RoutineScheduled | S16-180-0073 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Aqua Safe |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 8" of accumulated solids in septic tank. 30" of solids in treatment unit. 36" of clear water in treatment unit. Good aeration. Cleaned blower air filter. Tested alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 7:03PM
12/19/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was not hooked up from install and has not been treating at all. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/30/2024 | 01:28 PM
01/17/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip | Not Applicable | 125.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 07:00 AM
04/21/2023 |  | Reportable Incident | SWP-04-762 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to bad wire connection that could not be accessed due to junction box being buried and having a wood frame around it. Homeowner dug around the riser. Added 2 new risers to bring it to grade and installed new interior junction box and redid all wire connections. Homeowner did clear all small trees on the drainfield, | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0106 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
08/23/2023 | Alternative | Routine/Scheduled | 08-137-0078 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NO | [17 empty] | Manifold flushed and brushed. Rsv cleaned. Forcemain drained. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | Dec 30 1899 2:11PM
02/08/2023 |  | RoutineScheduled | 033-18-0204-SP | Caroline | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Distribution Pump Operation" ,"Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | The linear air pump for your aerobic treatment unit is not working and should be replaced. As noted on last year's inspection, the distribution box is cracked and should be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | 12:05 PM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/10/2023 | Alternative | Routine/Scheduled | 136-97-0856 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 5in of sludge 1 in of solids Pulled and cleaned filter Filter housing intact No riser on septic tank -Discharge/Pump Tank: Normal level 3 in of suspended solids Pulled floats and tested pump all working as should Plumbing intact No signs of infiltration -Peat Moss: Four peat chambers modules Peats moss in all modules are spent completely and holding water Two of four modules are cracked Inspection port holding 12" of water -Control Panel: 120 colts coming in All visual and audible alarms functioning properly Discharge pump pulled 5.6 amps Underground Consultation 10/18: -Puraflo modules are cracked Puraflo pad is holding water | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 02:07 PM
02/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/29/2023 | Alternative | RoutineScheduled | SD-10-116 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | 12:00 AM
02/16/2023 |  | RoutineScheduled | 175-15-0503 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | 7.100000 | 21.400000 |  | 0.000000 | [9 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 03/01/2023 | 02:21 PM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/17/2023 | Alternative | RoutineScheduled | 18-160-0027 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [8 empty] | 05/17/2023 | [7 empty] | Attached to this report | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | 12:00 AM
11/13/2023 | Alternative | Follow-Up | 16-160-0003 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | - REPLACED EXISTING PUMP WITH NEW LIBERTY EFFLUENT PUMP | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/17/2023 | 12:00 AM
02/28/2023 | Alternative | RoutineScheduled | 17-177-1043 | Pulaski | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | Delta E50 |  | Gravity | Pressure | Drip | Not Applicable | 250.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Replaced Spin Filter, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/02/2023 | 12:00 AM
11/27/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 01:07 PM
05/10/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | Dec 30 1899 11:40AM
03/15/2023 | Alternative | RoutineScheduled | 159-02-403 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [null] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
10/19/2023 | Alternative | Reportable Incident |  | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. Effluent filter installed or maintained | Pending Review | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | YES | [16 empty] | Inspected | Repaired a broken recirulation line leaking effluent on ground. Smell should disapate and system return to normal operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/21/2023 | 09:30 AM
03/31/2023 |  | Routine/Scheduled | 18-142-0327 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Processing Tank - Recirc - recirc pump, media drapes & spray grid serviced. Processing Tank - discharge - float sensors, pump and controls operating. Pumps to community absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Jan 1 1900 8:00AM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Aerator not functioning | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
01/27/2023 | Alternative | Routine/Scheduled | 157-04-308 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. BioFilter - Root clogging of biofilter media present - recommend biofilter changeout - raked / turned best able. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 10:00 AM
07/24/2023 | Alternative |  | 05-125-081 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/24/2023 |  | 12.100000 |  |  | 2.700000 |  |  | Will be sent separately |  | BOD: 12.1 TSS: 2.70 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/24/2023 | 12:00 AM
01/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Ecoflo peat needs replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
12/22/2023 | Alternative | Routine/Scheduled | 09-160-0230 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/22/2023 | 10:30 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-334219 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | filter clog septic tank lid damaged rlenco | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
03/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 182-17-0114 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
08/01/2023 | Alternative | RoutineScheduled | VAG408462 | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Gravity | Discharge | Chlorination |  | ["None"] | [] | [18 empty] | No discharge at this time | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/02/2023 | 12:00 AM
06/12/2023 | Alternative | Reportable Incident Component Maintenance | 179-10-0079-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Bionest | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm. Effluent was up into the risers. House had been vacant for a period, then lost power. When power was restored, the control panel alarmed for high level. H-O-A (hand off auto) pump switch was found in the "off" position. Unknown for how long or why it was off. Also, the 4th breaker in the panel was tripped for the little recirc pump in the atu. Reset it and pump ran ok. This has happened before, reason has yet to be determined. Disc filter had a bit of suction on it when removed for cleaning (vacuum from siphoning?). Since this is a continuous flush system, the pump rate cannot be measured when the effluent level is to the point where more effluent is pouring into the pump tank from the septic tank. It is recommended that a flow meter be added to overcome this and to provide a crude measurement of water usage (crude because it will include the flushed effluent which returns to the tank - but crude is better than nothing!). This system does use an override float to trigger the pump until the high level condition is pumped down. No way to know how often this happens. (Note: owner said alarm light turned off within 24 hours). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
07/10/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  |  |  | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [18 empty] | pods could use added peat | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | 12:00 AM
03/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0334 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
01/26/2023 |  | Routine/Scheduled | 07-120-0301A | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | The peat moss needs to be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/26/2023 | Jan 1 1900 3:46PM
08/04/2023 | Alternative | RoutineScheduled | 05-125-105 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/04/2023 | 12:00 AM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-0354-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Control Operation"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The system is functioning, however, the audible alarm horn is not functioning. Replacement is recommended | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/01/2023 | 07:38 AM
05/24/2023 | Alternative | RoutineScheduled | S-04-111-0026 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Whitewater ATU |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Septic tank minimal scum and clear trace of sludge, treatment tank minimal scum and 20" trace and Pump tank 6" trace. Cleaned blower airfilter, Owner purchased new blower to replace rebuilt unit, System has good aeration. and system is in normal operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
03/14/2023 | Alternative |  | 150-19-0062 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 12:00 AM
08/17/2023 | Alternative |  | 04-100-1221 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | See Attachement | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
03/23/2023 |  |  | 2006-143-0083 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [18 empty] | Recommend pumping in 3-6 month | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
12/19/2023 | Alternative | RoutineScheduled |  | Page | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Discharge | UV |  | ["BlowerCompressorAerator Operation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles"] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/19/2023 | 12:00 AM
11/20/2023 | Alternative |  | 14-183-127 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/20/2023 |  | 3.380000 |  |  | 10.000000 |  |  | Will be sent separately |  | BOD: 3.38 TSS: 10.0 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/20/2023 | 12:00 AM
01/24/2023 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 75.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 03:30 PM
09/25/2023 | Alternative | Routine/Scheduled | 04-142-0297 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | Cleaned effluent filter. Raked Peat. Tested floats and pump. System appears to be operating normally. There are some roots coming through the riser on the septic tank and around the force main of the pump tank, we used the hydroprobe to test watertightness and found no leaks at this time but could be a problem in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 1:06PM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/24/2023 | Alternative | RoutineScheduled | 14-100-0282 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 17.000000 | 12750 | ECOFLOS |  | Pump | Gravity | Mound | Not Applicable | 2400.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | LARGE SEPTC TANK SLUDGE JUDGE TEST REVEALED 3-4" OF SLUDGE FROM THE BOTTOM EVERYTHING WORKING AS IT SHOULD REPLACED PEAT | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/17/2023 | 10:55 AM
12/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-13-0167 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/24/2023 |  | Initial Visit | VAG408105 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Discharge | Chlorination |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation","Dispersal System Operation"] | [17 empty] | Pumped Out | no discharge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
03/31/2023 | Alternative | Routine/Scheduled | 136-15-0068 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner contacted us due to a smell - pumped the septic tank and pumped the Clearstream tank. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Disconnected the pressure switch on the aerator due to the pumping. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | 12:30 PM
06/25/2023 | Alternative | RoutineScheduled | SD-03-177 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2100 | septic | Advantex | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/29/2023 | 08:50 AM
08/01/2023 | Alternative |  | 12-113-145 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/01/2023 |  | 4.620000 |  |  | 2.400000 |  |  | Will be sent separately |  | BOD: 4.62 TSS: 2.40 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/01/2023 | 12:00 AM
10/31/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20276 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Replaced UV bulb while on site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-60372 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There were bees in the control panel at the time of our inspection. The system appears to be functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
03/10/2023 | Alternative | Routine/Scheduled | 196-17-0029 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - dosing - float sensors, pump and controls operating. Biofilter - peatmoss ponding & fair condition 2 years? - raked / turned. Pump Basin - discharge - float sensors, pump and controls operating. DBox - itnact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 10:00 AM
04/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | LPD needs rebalanced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/24/2023 |  | Reportable Incident | 175-02-0474 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Repaired force main in tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/04/2023 | Alternative |  | SD-05-594 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1800 | septic | Whitewater | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | 07:40 AM
08/28/2023 | Alternative | Routine/Scheduled |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Advanced Septic |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service - AquaSafe ATU Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Valving intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | 09:00 AM
08/29/2023 | Alternative | Pump-Out Only Pump-Out Only | 069150292 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank Pumped | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 2.000000 | [8 empty] | ["Other"] | [] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled | 107-14-0324 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
12/05/2023 | Alternative | Routine/Scheduled |  | Petersburg | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/05/2023 | Dec 30 1899 12:15PM
12/21/2023 | Alternative | RoutineScheduled |  | Henry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | MicroFast ATU |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Three compartment grease trap - 1st section - 4" crust, 12" in bottom, second section - 3" crust, 10" on bottom, third section - 0" crust, 4" on bottom. Septic tank - skim crust, 20" on bottom. MicroFast septic tank = 4" crust, 12" on bottom. Cleaned tank solids filter, very dirty. MicroFast treatment unit solids accumulation - skim crust, 12" of solids on bottom. Adequate aeration. Pump tank - 0" crust, 1" of accumulated solids on bottom. Tested floats, pump and alarms. Cleaned blower air filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2024 | 07:03 PM
02/03/2023 |  | RoutineScheduled | 12-195-224-DIS | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/03/2023 | 12:00 AM
09/07/2023 | Alternative | Routine/Scheduled | 550-STS-6767 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 11:25AM
09/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | See attachment | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
04/05/2023 |  | RoutineScheduled | 151-05-372 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | [18 empty] | Needs access riser to septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:00 AM
09/01/2023 | Alternative | Routine/Scheduled | 159-05-121 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - main house - normal level - effluent screen serviced. Secondary septic tank - guest house - normal level. Pump Tank - Main House - float sensors, pump and controls operating. Pump tank - guest House - float sensors, pump and controls operating. BioFilter - peatmoss in good condition - raked / turned. PUmp Tank - discharge - float sensors, pump and controls operating. Dbox - plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 07:45 AM
04/05/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | ["Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 04/05/2023 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected | Replaced alarm float Replaced UV Assembly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
09/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | Dec 30 1899 3:25PM
07/20/2023 | Alternative | Routine/Scheduled | 800-04-0179 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | Dec 30 1899 1:55PM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/05/2023 | Alternative |  | 033-06-0565-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | System was in pump alarm status. Pulled out pump (from treatment tank) and removed wipes from the pump intake. Reinstalled pump and pumped the system down to normal levels. Cleaned effluent (spin) filter and the air pre-filter, replaced the filter element for the canister filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
09/12/2023 | Alternative | Routine/Scheduled | 07-160-0304 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 03:45 PM
09/01/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-89947 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
02/21/2023 |  | RoutineScheduled | 177-11-0121-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Broken riser on septic tank, Replaced. Recirc tank needs pumping due to solids. Will send proposal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
04/05/2023 | Alternative | RoutineScheduled | 94-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/05/2023 | 12:00 AM
09/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 6.000000 |  | Septic Tank | Septic Tank #2 | Pump | Pressure | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [7 empty] | 09/21/2023 | Sample Chamber | 4.000000 |  |  | 4.000000 | 1.370000 |  | Attached to this report |  | Septic Tank #1-8"sludge 6"scum/ Septic Tank #2- 0"sludge 1"scum/ EZ-Treat Recirc. Tank #1- 3"sludge 0"scum/ EZ-Treat Tank #2-4"sludge 0"scum/ EZ-Treat Tank #3- 4"sludge 0"scum/ Pump Tank to LPD Trenches-2"sludge 0"scum/ No pump out needed at this time/ Recirculation pumps intake cleaned/ Controls, pumps, floats and alarms are functioning properly/ Counts: Cc1-0015119 ETM-0023397/ Cc2-0017441 ETM-0023298/ Pumps to LPD Trenches: Pump1-793 ETM-161h 21m/ Pump2-753 ETM-153h 38m/ Peak-21/ High-21/ No breakout or spongy areas on the LPD Trenches. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/31/2023 |  |  | 08-192-262 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/31/2023 | [7 empty] | Will be sent separately |  | BOD: BDL TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/31/2023 | 12:00 AM
12/29/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
03/07/2023 |  | RoutineScheduled | {FIPSCode}-STS-3859 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
03/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/20/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | Control Operation | Control Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/03/2023 | 10:15 AM
11/28/2023 | Alternative | RoutineScheduled | 175-16-0433 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ-Treat Recirculation Tank | Pump Tank | Pump | Pressure | Drip | UV |  | ["Recirculation Pump","Disinfection"] | ["Recirculation Pump","Disinfection"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ EZ-Treat-4"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ UV-Light sleeve cleaned and functioning properly/ Controls, pumps, floats and alarms are functioning properly/ Pump intake cleaned/ EZ-Treat spray nozzles clear and media in good condition/ Counts: Pump-661 ETM-80h 43m On-9m 35s (zone 1) On-10m (zone 2) Off 3h/ High counts-10/ Watermeter-0,097,598.2/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/10/2023 |  | RoutineScheduled | 195-STS-26164 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Control Operation","Auxiliary Filter","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/10/2023 | 12:00 AM
08/11/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 | 1000 | 1000 | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 12:00 AM
08/31/2023 | Alternative |  | SD-10-247 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
01/17/2023 |  | RoutineScheduled | 179-STS-91626 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 7000.000000 | [] | [] |  |  |  | 7.990000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 08:45 AM
02/06/2023 | Alternative | Reportable Incident | 061-STS-21156 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | EZ Treat Sandfilter |  | Pump | Gravity | Trenches |  |  | ["Dispersal System Operation","Level Sensor Operation"] | ["Dispersal System Operation","Level Sensor Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/10/2023 | 04:12 PM
11/15/2023 | Alternative | RoutineScheduled | 115-09-0199 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 4000 | Biomicrobics Fast 0.5 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","BlowerCompressorAerator Operation"] | ["Effluent Screens","BlowerCompressorAerator Operation"] | NA | Musty | [15 empty] | Inspected | Yearly inspection Sludge levels- 1-2" Scum layer and 14" in. sludge in EQ/surge Septic tank - Fast Treatment zone - observation port OK, 24-18" sludge- ok. Alarm functional, System includes 6 pumps,, all operational. Cleaned blower air filter. Good Aeration from Blower, Observation of treatment trough from 6" Vent pipe when opened. System is fully operational. Alt. Dosing Pumps- Pump #1 cycles 225 and 375hrs 19min run time , Pump #2 224 cycles and 1287hrs 12 min- | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
04/21/2023 | Alternative | RoutineScheduled | 115-14-0234 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Control Operation"] | ["Effluent Screens","Control Operation"] | YES | [16 empty] | Inspected | Sludge levels-Scum layer 2-3" in. and 6" in. sludge in Septic tank -Recirc zone minimal scum and 20" Sludge and Discharge zone has minimal scum and 10" Sludge in Discharge zone of tank, Entire System pumped 2 years ago. Cleaned effluent screen/media. System had no power on arrival and we found a tripped breaker in the basement of home , it returned to normal operation when reseting the breaker. Both Pumps are functional. Alarm functional, FLoats switches test ok.. All 3 floats test good. Srayed off media. Computer has not time or date and History is all 000's but systmem is operational, RAM maybe coruppted on the circuit board due to age. Reset the time and date.Pump run time 000 cycke counter has 9378 but maybe not accurate.. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/30/2023 | 09:30 AM
01/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
09/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/21/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/21/2023 | Dec 30 1899 9:55AM
08/05/2023 | Alternative | RoutineScheduled | -STS-20150 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Sand Filter | Pump | Pressure | Discharge | Chlorination | 500.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | Musty | Clear | 7.800000 |  |  | 1.200000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/12/2023 | 12:00 AM
02/01/2023 | Alternative | Routine/Scheduled | 151-05-003 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - effluent screen serviced. BioFilter - peatmoss in extreme poor condition - recommend biofilter changeout. Pump Basin - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | 09:15 AM
03/31/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air release valve was repaired. System should resume proper function | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/12/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 12:00 AM
08/22/2023 | Alternative | RoutineScheduled | 175-05-0830 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | Septic Tank-12"sludge 2"scum/ .5 Microfast ATU-14"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Pump out highly recommended for the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ UV-Light sleeve cleaned and functioning properly/ Counts: Pump-7327 ETM-1128h 37m/ Zone1-3534 @ 3.8 gpm Zone2-3506@ 3.8 gpm On-9m 30s Off-2h 50m / High level-0/ Watermeter-0,437,663.6/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 |  | Routine/Scheduled | 800-STS-14655 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Post Install Inspection - Lab Samples NOT obtained. Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - pump, media drapes & Spray grid serviced. Processing Tank - discharge - pump, float sensors, controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 10:45AM
02/01/2023 | Alternative | RoutineScheduled | SD-01-573 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
06/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-017543 ETM-0028750/ Pump2-017554 ETM-0028128/ Turned and fluffed peat in all 8 Puraflo Modules / Peat in good condition/ No breakout or spongy areas on the Pad site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/06/2023 | Alternative | Routine/Scheduled | 147-03-0084 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 12:30PM
06/10/2023 | Alternative | RoutineScheduled | 91-100-0788 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 300.000000 | [] | [] | [18 empty] | REPLACED XT ALARM. PEAT LOOKS GREAT. EVERYTHING WORKING AS IT SHOULD. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/27/2023 | 01:00 PM
08/30/2023 | Alternative | RoutineScheduled | 181-07-0055 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 3.000000 | 3500 | Biomicrobics MicroFAST |  | Pump | Pressure | Trenches | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. No apparent leaks in system or drain field area. Septic system did not need to be pumped. Control panels, alarms, blower and pump all functioning properly. Lids were properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/16/2023 | 09:45 AM
06/05/2023 | Alternative | RoutineScheduled | SD-13-54 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | MircoFast | Geo Flo Drip | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Attached Growth Medium"] | NO | [7 empty] | 06/20/2023 | [8 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 04:40 PM
09/11/2023 | Alternative | Reportable Incident | 800-08-0040 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/11/2023 | Dec 30 1899 8:30AM
07/13/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1000 | Advantex RT |  | Pump | Pressure | Drip | Not Applicable | 50.000000 | ["Distribution Pump Operation","Effluent Screens"] | ["Distribution Pump Operation","Effluent Screens","Control Operation"] | YES | Musty | Clear | [15 empty] | The system is operating as intended and is in general conformance with the health department | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 08:30 PM
01/23/2023 | Alternative | Routine/Scheduled | 151-15-0027 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration Tank - mixing present - compressor serviced. Absorption field - Deep install. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 08:45 AM
02/03/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-61643 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 12:00 AM
02/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/17/2023 | 10:44 AM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90108 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There is effluent coming to the surface in multiple places in the drip dispersal area. We are copying your builder on the report so that he can contact the system designer for further evaluation and repair options. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/01/2023 | 07:38 AM
08/10/2023 | Alternative | RoutineScheduled | 150-06-356 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/05/2023 | Alternative | Routine/Scheduled | 041-STS-260123 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NO | [17 empty] | Manifold brushed and flushed. Rsv cleaned. System appears to be operating normally. Pump is drawing a lot of amps and may be on the way out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Dec 30 1899 4:21PM
11/24/2023 | Alternative | Reportable Incident | 151-04-435 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Ecoflow. Discharge in high level. Pump and floats were replaced in August. Found floats working but pump was humming. Pulled the pump and found 3 peices of the driveway gravel lodged in the turbine locking the pump up. After removing the pump worked fine and pumped the chamber empty. Informed Drew on what's going on and we cannot figure out how driveway gravel got in there. Told him if it happens again we can pump the chamber out with a pump truck | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 09:42 AM
08/22/2023 | Alternative | RoutineScheduled | SWP-04-595 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-4 | 0-0 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 6.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 10:00 AM
07/12/2023 | Alternative | Routine/Scheduled | 234-17-138 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 9:55AM
11/08/2023 | Alternative | RoutineScheduled | SD-13-63 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 58.800000 | ["Effluent Screens","Dispersal System Operation"] | ["Dispersal System Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/08/2023 | 03:50 PM
05/26/2023 |  | RoutineScheduled | 033-07-0363-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-1 | 0-1 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Level Sensor Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | YES | None | Clear | [14 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/26/2023 | 11:00 AM
11/03/2023 | Alternative | RoutineScheduled Component Maintenance | 175-14-0311 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | NA | Septic | Cloudy | [13 empty] | Will be sent separately | Inspected | On site for annual inspection and to address atu alarm. Replaced failed blower and a 90* pvc elbow that was deformed. Treated effluent is cloudy, probably in part due to the failed blower. But the media does appear to be clogged. Will reevaluate at next site visit. Effluent surfaced in zone 2 and in headworks during a test cycle. Out of time to diagnose. Returned 11/6 and replaced faied drip tube to flex pipe adapter. Dug back on outside of headworks, inlet end, and confirmed the effluent was from the force main. Owner is a licensed plumber and will continue digging to find where the pipe (or fitting) is damaged. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
07/27/2023 | Alternative | RoutineScheduled | 17-160-0026 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000gal | Ecoflo | [6 empty] | [] | [] | [18 empty] | - completed inspection - replaced blower onsite | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | 12:00 AM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/12/2023 |  | Routine/Scheduled | 2018-143-0109 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/12/2023 | 08:23 AM
04/20/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | First Yearly Inspection- of recent installed system. Septic tank trace scum layer and 4" sludge layer, Recir zone trace sludge, discharge zone trace sludge- High water noticed on recirc zone but good level on discharge side, level corrected after running in test mode. Alerts in historyy began 3-18-23and came 3 times daily, possible toilet flapper leaky, Recirc pump run time 305.5 hours 25,578 cycles and 3.5 hours discharge and 106 cycles | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
04/10/2023 |  | RoutineScheduled | 179-06-0295-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The shed and fence are on the drainfield. There does not appear to be any impact on the system at this time, but this could be an issue in the future. Also, the dogs digging around the tanks have exposed a section of conduit. We recommend this be covered. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
06/20/2023 | Alternative |  | 167-STS-16735 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/20/2023 | [7 empty] | Will be sent separately |  | BOD: BDL TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/20/2023 | 12:00 AM
01/05/2023 |  | RoutineScheduled | 177-STS-90044 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Control Operation"] | NA | None | Clear | [5 empty] | 01/05/2023 |  | 3.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. RECIRC: HL 0,LL 3. DISCHARGE: HL 5, LL 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
05/08/2023 |  | Reportable Incident |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/12/2023 | 02:11 PM
01/13/2023 |  | Routine/Scheduled | 196-08-293 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Routine - Biofilter changeout. 01/13/2023 - septic tank pumped empty - effluent screen serviced. 01/18/2023 - Biofilter changeout conducted. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/19/2023 | 07:30 AM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 179-19-0067-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | 139-07-0203 | Greene | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 07/14/2023 |  | 87.000000 | [5 empty] | Will be sent separately | Inspected | Repaired audible alarm | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["Other"] | ["None"] | YES | [17 empty] | Needs Audible Alarm | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/31/2023 | 12:00 AM
02/13/2023 | Alternative | Initial Visit | 093-03-0221 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 24.000000 |  | 1.000000 | [5 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. There is visible wetness on the drainfield - most likely from rain - once it dries need to keep an eye on it. The timer is set to 4.75 minutes every 1 hour. Took initial BOD and Fecal samples. NOTE : BOD sample was a tad high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | Dec 30 1899 4:00PM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 179-09-0114-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | EZTreat pump needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0107 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [null] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
01/12/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 01/12/2023 |  | 15.000000 | [5 empty] | Will be sent separately | Inspected | Panel was off corrected Lab sample normal | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
06/19/2023 | Alternative | Reportable Incident | 151-03-414 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | 06/08/2023 - Real Estate Inspection Conducted - Septic tank pumped. 06/19/2023 - replaced distribution box with new 8 port concrete DBox. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 11:45 AM
08/11/2023 | Alternative | RoutineScheduled | 107-02-0722 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
01/27/2023 |  |  | 11-120-0217AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3000 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | None | Clear | 7.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | Jan 1 1900 8:00PM
03/24/2023 |  | RoutineScheduled | SP-05-393 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Clogged up filter, cleaned and water level back to normal. Media starting to show its age but still ok. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
04/18/2023 |  |  | 03-120-0612A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2200 | 1200 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","Recirculation Pump"] | YES | Musty | Clear | 7.000000 |  | 7.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | Jan 1 1900 2:30PM
09/14/2023 | Alternative | RoutineScheduled | 12-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 4 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/14/2023 | 12:00 AM
12/19/2023 | Alternative | RoutineScheduled | 182-03-0006 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.140000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:45 AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
02/09/2023 |  |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Microfast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | 0scum and 6" of sludge in Septic tank, middle has some loose sludge. blower working, filter cleaned alarm working on blower.. High water alarm working, Field looks good no leaks. turn return pressure down to 35 psi. Timer set for 8 min on 3 hrs off. 3412 hrs run time, | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | 02:00 PM
03/28/2023 | Alternative | Routine/Scheduled | 151-02-377 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 10:45 AM
03/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
02/10/2023 | Alternative | Pump-Out Only | 136-05-0352 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped septic tank empty - resealed leaking riser. Replaced Aeration stone & airline due to age. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 09:30 AM
10/31/2023 | Alternative | RoutineScheduled | 151-17-002 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service | 1942001034 | Kent | Cuthbertson | 4.000000 | 45000 | 15000 | 15000 | Pump | Gravity | Trenches | UV | 18952.000000 | ["None"] | ["None"] | YES | [8 empty] | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 03:00 PM
11/27/2023 | Alternative | RoutineScheduled | 115-14-0300 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge level 1-2" scum and 10-12" Sludge in Septic tank zone & 8-10" Sludge in Recirc tank. Clear Effluent on top. Owners added mulch this year to cover the system and looks good, Biofilter was very dirty and fully clogged. Had alarmed due to clog. we cleaned and flushed the system. Pump is functional, alarm functional, Brushed Manifold, Cleaned RSV and Ran is test mode. System is fully operational at this time. Connected the system phonie lines at the home to verizon for the online monitoring to activate. system has active monitoring now. Recirc pump run time 2532.6 hrs and 88,655 cycles. Buzzer in control panel is muted and may need replacement due to age. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/28/2023 | 05:30 PM
07/27/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-87229 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear |  | 5.790000 |  |  |  | 07/27/2023 | Sample Chamber | 2.000000 | [5 empty] | Will be sent separately | Inspected | Cracked pump line was repaired on 8/2/2023 BOD: <2 DO: 5.79 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
10/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 2000 | Septic | Micro fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 10/24/2023 | Sample Chamber | 10.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/12/2023 | Alternative | Reportable Incident | 166-12-192 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: -Customer stated alarm on orenco panel was goingnoff Opened system and found at normal level Tested and confirmed that all floats and pump were functioning properly Found uv bulb to be burned out Pulled and cleaned pump screen, Vortex filter, and weir while on site. Gave customer estimate for uv bulb and she approved Repair 10/18: --Installation of an Ultraviolet Disinfector Bulb | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/24/2023 | 03:54 PM
06/19/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Multi-Flo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
03/27/2023 | Alternative | RoutineScheduled | 121-STS-12043 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Retrofast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | [] | NA | Septic | Discolored | [14 empty] | Inspected | - recommend septic tank be pumped/cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/13/2023 | 12:00 AM
10/06/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 3.000000 |  | Septic | MicroFast | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | YES | [17 empty] | 0 Scum And 3" of sludge in grinder pump tank, Floats, alarm, both grinder pumps working. 0 scum and 0 sludge in other tanks . Flushed the effluent filter. pump tank clean, transducer, pumps , blower all working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 12:45 PM
10/25/2023 | Alternative | Routine/Scheduled | 157-09-0174 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the alarm float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/25/2023 | 01:30 PM
07/14/2023 | Alternative | Routine/Scheduled | 234-18-003 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | Dec 30 1899 9:15AM
01/05/2023 |  | RoutineScheduled | AVEA-9URLC7 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 02:21 PM
02/15/2023 |  | Follow-Up |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Control Operation","Dispersal System Operation"] | ["Control Operation","Dispersal System Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/17/2023 | 10:41 AM
02/17/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced (4) yellow control floats. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Dec 30 1899 12:26PM
08/25/2023 | Alternative | Routine/Scheduled | 166-87-128 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Sandfilter, Non-recirculating |  | Pump | Pressure | Mound |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 05:40 PM
06/16/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | Thick scum layer, A lot of loose sludge in sludge judge. No accurate reading with the access. Treatment side is dirty. Recommend pumping with in the year. Transducer, blower, alarm are operational. 112 h 9m Runtime for pump with 10700 doses. Field dry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 12:00 PM
01/06/2023 | Alternative | Routine/Scheduled | 151-12-0133 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | 04:49 PM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Whitewater ATU | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
10/18/2023 | Alternative | RoutineScheduled | 08-197-A12 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-400 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected | A new drip dispersal pump & spin filter were installed today. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
09/28/2023 | Alternative | RoutineScheduled | 149-17-0025 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 12:00 AM
06/20/2023 | Alternative | RoutineScheduled | 154-05-0918 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 09/25/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/03/2023 |  | Follow-Up | 02-197-A2 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco |  |  |  |  | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 | ["Disinfection","BlowerCompressorAerator Operation"] |  |  | Pungent |  |  | 0.000000 | [13 empty] | System needs pumping, aerator replaced, and tablets in place. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/04/2023 | 12:00 AM
06/23/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-90518 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:26 AM
05/09/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | Musty | Clear | [5 empty] | 05/09/2023 |  | 5.000000 |  | 1600.000000 |  |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
08/08/2023 | Alternative | Routine/Scheduled | 093-STS-15228 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 1:32PM
01/09/2023 |  | Initial Visit | 007-STS-23663 | Amelia | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Piedmont | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Contractor contacted stating the owner was having problems with the toilets gurgling. Serviced system. Installed a new control panel with a new circuit board. Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The aerator should be raised. The inlet tee in the septic tank can not be accessed - needs to be addressed. The timer is set to 2.5 minutes every 1 hour. Could not take initial samples due to there not being enough water. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/09/2023 | Jan 1 1900 10:30AM
03/29/2023 |  | RoutineScheduled | 179-11-0091-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend moving the saplings growing on the bottom of the lower mound and the top of the upper mound. We also recommend installing two new air release valve housings & lids. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
03/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Puraflo peat needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | Dec 30 1899 12:26PM
01/26/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired blower air line. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/13/2023 | Jan 1 1900 8:47AM
09/22/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-15912 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/22/2023 | 12:00 AM
07/24/2023 | Alternative | RoutineScheduled | 087-STS-6314 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/02/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | No scum or sludge. Just had the tank pumped. Floats, Alarm, Pump is operational. Peat is good. It was replaced 2 years ago. D box uncovered bc of wet area in drainfield, The last two line taking most of the water. Reset the levelers to distribute evenly. Line 3 not taking as much as the others. owner is going to have the line jetted and camara'd. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 07:00 AM
08/07/2023 | Alternative | Reportable Incident Component Maintenance | 061-16-027 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarms on Monday, then the next Sunday. Ran test cycle to confirm flow rate and observed effluent flowing back through weep hole after pump had stopped. Removed pump and replaced faulty check valve. No other problems found at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
11/21/2023 | Alternative |  | 09-183-029 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/21/2023 |  | 7.450000 |  |  | 4.400000 |  |  | Will be sent separately |  | BOD: 7.45 TSS: 4.40 SV | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/21/2023 | 12:00 AM
11/10/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | Dec 30 1899 9:30AM
08/09/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-1358 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/09/2023 | Dec 30 1899 11:00AM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0194-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
01/20/2023 |  | Routine/Scheduled | 07-163-0120 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | Jan 1 1900 8:45AM
09/28/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [28 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 01:47 PM
11/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0175-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Leak on both risers, recommend to seal and check inlet lids as well. Fence on top of headers, recommend to camera snake to make sure they were not hit. After repairs are done recommend to auger pods and check levels on manifolds. Will send proposal for repairs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
06/16/2023 | Alternative | Reportable Incident | 109-STS-31814 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 3000 | Multi Flow |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [14 empty] | Inspected | Dose Pump 7.6A - Distribution Pump 10.6A - Aerator 2A Sludge Scum - Septic 14", Dosing Chamber 2", ATU 2", Pump Tank 0" 3 Breaks in Drip Tubing Repaired | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/16/2023 | 11:00 AM
09/06/2023 | Alternative | RoutineScheduled | 181-14-0116 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was pulled and cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 03:50 PM
04/13/2023 | Alternative | RoutineScheduled | SD-13-346 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation"] | [] | NA | [17 empty] | Septic-12"sludge 6"scum/ Microfast-18"sludge 0"scum/ Pump Tank-3"sludge 0"scum/ ALL Tanks require pump out due to sludge levels/ Controls, pump, floats and alarms functioning properly/ Blower air filter cleaned and blower working correctly/ Counts: mPump-002437 ETM-0015037 On-3m 53s Off-11h 56m/ No breakout or spongy areas on the drainfield/ Noted: Small trees on the drainfield require removal. Owner stated he has addressed the tree issue and tanks to be pumped out soon. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/11/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/11/2023 | Dec 30 1899 8:00AM
05/01/2023 |  | RoutineScheduled | SP-05-120 | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] |  | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The Peat in the Puraflo modules has deteriorated. Additionally, because there is standing water in the sample chamber, the pad may be nearing the end of its useful life. We recommend contacting an Alternative Onsite Soil Evaluator (AOSE) for repair and/or system replacement options. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/01/2023 | 06:29 AM
04/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-0142-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
12/13/2023 | Alternative | Reportable Incident |  | Frederick | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Norweco Singulair ATU | [6 empty] | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [18 empty] | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 01/29/2024 | 12:39 PM
04/05/2023 | Alternative | Routine/Scheduled | 128-15-0018 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | 07:30 AM
10/30/2023 | Alternative | Follow-Up |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Pressure | Drip | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 12:00 AM
08/08/2023 | Alternative | Reportable Incident Component Maintenance |  | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | System was in high level for several days due to very slow drip rate. Cleaned the dirty disc filters, finger screen, backwash valves, zone return valve, and Simtech pump screen, then did a bleach flush of the drip tubing. After all of that, the drip rate improved from .7 to 3.25 gpm and backwash valves were opening and closing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/22/2023 |  | RoutineScheduled | 175-17-0351 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Removed recirc pump and cleaned the intake. Cleaned 1 spray nozzle in EZ Treat pod. Treatment looks good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
09/15/2023 | Alternative |  | 085-STS-35367 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
04/10/2023 |  | Pump-Out Only |  | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 3000 | EZ Treat Sandfilter | EZ Treat Sandfilter | Pump | Pressure | Pad | UV | 1000.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Pulled 1500 gallons from primary septic tank for storage - serviced effluent screen - 100% clogged! Advised maintenance company that system REQUIRES service - let contract lapse! Service tech to be scheduled following contract renewal negotiations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | Jan 1 1900 7:30AM
07/24/2023 | Alternative | Routine/Scheduled | 18-120-0534AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Inspected | Real Estate Inspection - Routine Service. Primary septic tank - pumped empty and inspected. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - concrete - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | Dec 30 1899 7:30AM
07/14/2023 | Alternative |  | 177-STS-90120 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump chamber lid should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/13/2023 | Alternative | RoutineScheduled | 154-03-1024 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | Whitewater ATU |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
06/06/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [6 empty] | Distribution Pump Operation | Distribution Pump Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/06/2023 | 01:18 PM
04/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
09/15/2023 | Alternative |  |  | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
05/16/2023 |  | RoutineScheduled | 175-02-0500 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Blower panel and control panel were in alarm due to circuit breaker being tripped on blower panel. Reset and blower ran, but rather raspy for the first minute. Blower most likely headed towards bearing failure. Replaced blower after discussion with owner. Pump tank had gotten into high level due to pump lock-out relay activated by blower being off. Microfast septic tank needs pumped out (treatment zone is very difficult to get clean if the sludge gets any deeper), owner to make arrangements. Fallen trees and saplings have been removed from drainfield, but one remaining 5" diameter tree needs cut down to grade. Grass is almost waist-high and needs cut. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
04/13/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic zone 1" scum on top 8" sludge- Recirc zone 4-6" sludge, Discharge Tank 4" Fine sludge trace - Biofilter cleaned and was very dirty -sprayed off media-the build up blinded about 70%. Keep minimal use of antibiotic soaps, chemicals, sanitizers and cleaners. Cleaned RSV and flushed pump and cleaned/brushed manifold and ran system in test. Tested pumps, All are functional;Recirc pump time 3651.7 Hours 34813 cycles, discharge pump time 218.5 hours and 11930 cycles- - System appears fully operational - No alarms and minimal alerts this past year in history | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
04/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/28/2023 | Alternative | Reportable Incident | 073-STS-102139 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Maintenance - VDH Permit 136-23-0046 - GMP2018-02 Existing septic tank pumped empty and removed. Installed new Infiltrator plastic septic tank in same general location. Installed new 4" Conveyance Line. Installed new 8 port concrete distribution box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 10:00 AM
08/16/2023 | Alternative | Routine/Scheduled | 06-160-0003 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Ecoflo |  | Pump | Pressure | Drip | Not Applicable | 223.000000 | None | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/16/2023 | 11:00 AM
12/12/2023 | Alternative |  | 93-184-5002 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/12/2023 |  | 4.010000 |  |  | 1.400000 |  |  | Will be sent separately |  | BOD: 4.01 TSS: 1.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
06/29/2023 | Alternative | Follow-Up |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | [] |  |  |  | 7.950000 | 6.480000 | 36.000000 |  |  | 06/29/2023 | [5 empty] | 86.850000 |  |  |  | Flow meter not working - parts ordered. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/13/2023 | 02:30 PM
01/06/2023 |  | RoutineScheduled | 18-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/06/2023 | 12:00 AM
03/28/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Manifold was repaired and riser was replaced. System should now function as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/06/2023 | Alternative | Pump-Out Only | 04-160-0138 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Microfast | [6 empty] | [] | [] | [17 empty] | Pumped Out | Pumping & Cleaning Septic Tank (1500 gallons) JOB SCOPE: Pumped/cleaned septic tank; septic system is functioning at this time but not as designed as there are components that are recommended to be repaired/replaced. - recommend inlet line be repaired/replaced (80ft, 18in) - recommend tray in Microfast unit needs to be repaired/replaced - recommend alternative repair: 02-13-23 Annual Inspection of Alternative Septic System This system is functioning but not as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Components are recommended to be repaired/upgraded. - recommend pumping/cleaning septic tank - inlet line is underwater and needs to be corrected, recommend pumping/cleaning tank to see if that will resolve issues - it was noted in last report that riser is buried and broke and recommended to bring to ground level, riser needs to be brought up to ground level for future maintenance services and broken piece replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/07/2023 | 12:00 AM
07/01/2023 | Alternative | RoutineScheduled | 109-08-0226 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned recirculation pump solids basket filter. Flushed treatment unit spray manifold. Cleaned clogged spray heads. Sprayed solids off of treatment unit sheets. Tested floats, pump and alarm. The passive charcoal air vent should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 07:03 PM
12/19/2023 | Alternative | Follow-Up | 09-197-A6 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | [33 empty] | No tablets | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
05/01/2023 |  | Routine/Scheduled | 06-120-0161A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - requires pumpout - no riser to grade! Secondary septic tank - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 5 modules - Peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Jan 1 1900 7:15AM
08/05/2023 | Alternative | RoutineScheduled | 107-06-0008 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
10/20/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 12:30PM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/06/2023 | Alternative | RoutineScheduled | 182-05-0201 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 12:00 AM
07/17/2023 | Alternative | RoutineScheduled | 11-152-100 | Lee | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Recirculation Pump","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Recirculation Pump","Septic Tank Baffles","Level Sensor Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled | 150.16.0123 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 2.000000 | 2500 | BioMicrobics MicroFast |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation"] | NA | Musty | Cloudy |  |  | 50.000000 | [11 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/21/2023 | 11:15 PM
05/30/2023 | Alternative | RoutineScheduled | 181-05-0189 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | NO | [16 empty] | Pumped Out | The MicroFast and pump tanks were both pumped and cleaned. The blower and spin filters were both cleaned. The blower was not working at the time of inspection so a new blower was installed. The controls were operating as designed. There were no visible leaks in the drip field. There was return effluent returning to the pump tank so the drip field was operating as designed. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/06/2023 | 10:45 PM
12/13/2023 | Alternative | Routine/Scheduled | 127-STS-35092 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 12:30PM
06/21/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DSS repaired issues with junction boxes. The system should return to functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/26/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 10:52 AM
10/27/2023 | Alternative | Reportable Incident | 136-02-117 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: Diaphrams are torn on air pump. Arrived on site camera the sewer line and found a spot that is really corroded and jagged. Set up underground consult. Made recommendations for air pump customer approved rebuild kit. Completed repairs onsite. Tested upon completion | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 08:32 AM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0015-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Sludge levels change a lot sinc3 last year due to customer using liquid softeners, spoke to her and she said they will stop using it. Vacuumed water from both junction boxes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance | 177-19-0044-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 2.000000 |  | Enviro-Flo | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the Orenco riser lid on the first septic tank and replacing the union on the second recirculation pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
06/03/2023 | Alternative | Routine/Scheduled | 041-STS-261420 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/03/2023 | Dec 30 1899 10:00AM
10/11/2023 | Alternative | RoutineScheduled | SD-12-285 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 55.000000 | ["SludgeScum Accumulation","Dispersal System Operation","Level Sensor Operation","Attached Growth Medium"] | ["SludgeScum Accumulation"] | YES | Sulphitic | Clear | [15 empty] | Ponding Present | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/24/2023 | 12:00 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank full. Pump appears to be functioning on hand but not under control of the panel. Homeowner is scheduled for pumping and repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
05/10/2023 |  | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/19/2023 | 01:11 PM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20512 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
08/23/2023 | Alternative | Follow-Up | 166-13-133 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Installed a new Salcor UV light bulb, installed a new Salcor UV tube, and installed a new Salcor UV ballast. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/23/2023 | 12:00 PM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
04/18/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | Dec 30 1899 4:23AM
06/05/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [9 empty] | Level Sensor Operation | Level Sensor Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 01:29 PM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
10/09/2023 | Alternative | RoutineScheduled | 154-06-0730 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 11:55 AM
03/03/2023 | Alternative | RoutineScheduled | 139-05-0354 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | EcoFlow |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
06/08/2023 | Alternative | Routine/Scheduled | 095-STS-6407 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The pressure switch on the aerator is not hooked up - needs to be addressed. The septic tank needs additional risers on it to be properly inspected in the future. The timer is set to 2.75 minutes every 1 hour. It was raining at the time of service and could not check out the drainfield or mound. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | Dec 30 1899 3:00PM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/14/2023 | Alternative | Follow-Up | 2018-143-0086 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Purasys |  | Pump | Gravity | Pad | Not Applicable |  | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [17 empty] | Replaced the propeller. system should return to normal operation | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/14/2023 | 12:34 PM
02/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
12/13/2023 | Alternative | RoutineScheduled Component Maintenance | 154-07-0549 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Roots are growing inwards around the base of the riser on the septic tank. If you get an alarm during periods of heavy rain, please let us know. It may be necessary to excavate and reseal the riser. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
04/15/2023 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Ecoflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | 03:07 PM
05/31/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [8 empty] | 05/17/2023 | Sample Tap | 32.000000 |  |  | 23.400000 | 47.000000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
04/24/2023 |  | RoutineScheduled | 133 16 0251 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Septic zone 2-3" scum 6-10" sludge- Recirc zone 6" sludge, Discharge Tank 8-12" sludge -Effluent filter cleaned- spray manifold-had weak spray on arrival and good even spray after servicing. We cleaned the sprayer nozzles and sprayed off media. Checked FLoats switches and alarm all are good. Ran system in test mode. All is functional. Pulled recirc pump and cleaned inlet screen was clogged with sludge, Flushed off the inlet screen on recirc pump. Recirc pump run time 2236.9 hours and 71131 cycles and discharge pump 333.8 hours run time and 3415 cycles. System in connected to monitoring. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
08/17/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-4810 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets installed 10 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/17/2023 | 12:00 AM
04/25/2023 |  | Routine/Scheduled | 550-STS-6566 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 2:05PM
04/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
09/08/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-5576 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 10:05AM
02/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Note: Peat in poor condition, BOD taken on 9/21/22 was 32 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/15/2023 | Dec 30 1899 1:34PM
06/24/2023 | Alternative | RoutineScheduled | 2042-97-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | SBR |  | Pump | Gravity | Discharge | UV | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NA | Musty | Clear | 6.900000 |  |  |  |  | 07/03/2023 | Sample Chamber | 2.000000 |  |  | 6.000000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/12/2023 | 12:00 AM
10/31/2023 | Alternative |  | 139-03-0056 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Anthony & Sara | Wiedl, Jr. | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/18/2023 |  | Routine/Scheduled | 234-15-47 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 1:10PM
06/02/2023 |  | RoutineScheduled | 101-18-0296 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | AquaSafe |  | Gravity | Gravity | Trenches | Not Applicable | 500.000000 | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
02/28/2023 |  | RoutineScheduled | 132-01-0245 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast |  | Gravity | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
03/13/2023 | Alternative | Initial Visit | VAG408093 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  |  | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [18 empty] | pumping required....to be scheduled by customer. Post aeration in place at one time | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/13/2023 | 12:00 AM
07/22/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Distribution Pump Operation","Level Sensor Operation"] | ["Distribution Pump Operation","Level Sensor Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | 02:45 PM
11/03/2023 | Alternative | Routine/Scheduled | 03-172-0060A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | A real estate inspection was performed. Septic Tank: -Depth to the top of the Septic Tank 0-12" below grade -Condition of Lid: Intact -Does tank require pumping? No -Tank Level Normal operating level -Condition of Inlet Tee Satisfactory -Effluent Filter present? No -Riser present? Yes -Was Septic Tank pumped? No -Size of the Septic Tank 1250 gallons -Sludge Judge Levels 4" -Condition of Outlet Tee Satisfactory -Septic Tank - Additional Notes Septic tank last pumped out on 10/04/2023 Recirculation Tank: -Depth to the top of the Recirculation Tank 12-24" below grade -Condition of Lid: Intact -Does tank require pumping? No -Riser present? Yes -Was the Recirculation Tank pumped? No -Sludge Judge Levels 9" -Recirculation Tank - Additional Notes Noted root infiltration around base of risers. -Effluent Filter present? Yes Discharge Tank: -Depth to the top of the Discharge Tank 24-36" below grade -Riser present? Yes -Was the Discharge Tank pumped? No -Does tank require pumping? No -Sludge Judge Levels 0 -Condition of Lid: Intact Recirculating Splitter Valve (RSV): -Was RSV pulled & cleaned at time of service? Yes Media Sheets: -Was the media serviced at time of inspection? Yes -Condition of Spray Grids: Satisfactory -Overall function of the Media: Satisfactory Control Panel: -Was the control panel powered at time of inspection? Yes -Overall function of Control Panels Satisfactory -Were alarms tested at time of inspection? Yes Distribution Box: -Depth to the top of the Distribution Box 0-12" below grade -Type of Material: Concrete -Condition of Lid: Intact -Distribution Box found: at normal operating level -Condition of Distribution Box: Satisfactory -Number of Drain Lines 6 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 9:08AM
01/11/2023 | Alternative | Reportable Incident | 151-16-0131 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles"] | ["Dispersal System Operation","Septic Tank Baffles"] | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Installed access riser on septic tank - replaced effluent screen. Replaced DBox with new 8 port concrete DBox Spliced to existing header lines Spliced to existing Conveyance Line. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/12/2023 | 07:15 AM
03/17/2023 |  | RoutineScheduled | 169-STS-27127 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ATL |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled | 179-12-0308-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Clearstream | Clearstream | Gravity | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection and replaced defuser. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
03/18/2023 | Alternative | RoutineScheduled | SD-14-334 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic/trash | aquasafe | Gravity | Pressure | Drip | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 08:40 AM
09/07/2023 | Alternative |  | 036-STS-32778 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 099-11-0033-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media has filamentus bacteria but is not clogged and treatment is clear. Will check next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
06/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | replaced blower panel Added media cleaner | This AOSS should now return to normal function after having provided the above state routine maintenance | 07/06/2023 | 08:40 AM
09/08/2023 | Alternative | Reportable Incident | 149-05-131 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | 02:56 PM
08/17/2023 | Alternative | Reportable Incident |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | Attached Growth Medium | [18 empty] | Removed spent biofilter media and replaced with new. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 08:45 AM
05/04/2023 |  |  | 07-113-265 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/04/2023 |  | 6.250000 |  |  | 5.730000 |  |  | Will be sent separately |  | BOD: 6.25 TSS: 5.73 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/04/2023 | 12:00 AM
01/12/2023 |  | RoutineScheduled | 099-13-0097-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["SludgeScum Accumulation" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Replaced failed timer in panel. Pump tank needs to be pumped out due to sludge levels. Recomend pumping out septic tank as levels are close to be required and someone is flushing paper towels down the drain. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
12/21/2023 | Alternative | RoutineScheduled | 115-12-0199 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | NA | Musty | [15 empty] | Inspected | Sludge Levels- under 1" scum layer and 10 in sludge in septic tank-recirc zone 10", discharge zone 10" sludge, Pumped last year- Cleaned effluent screen, pumps are functional, alarm functional, sprayed off media, tested floats-all good. No Alarms this past year in history. Recirc pump 1851.2hours and 93773 cycles and discharge pump has 511 hours and 43,999 cycles- | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:30 AM
01/15/2023 |  | RoutineScheduled | 177-06-0536-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Puraflo 4 Mod |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Auxiliary Filter"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Auxiliary Filter"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/05/2023 | 12:00 PM
03/05/2023 |  | Routine/Scheduled | 041-STS-260545 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1500 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/05/2023 | Jan 1 1900 11:00AM
12/20/2023 | Alternative | RoutineScheduled Component Maintenance | SD-07-213 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | The peat in the Puraflo modules is settling and beginning to break down. It is likely that peat replacement or the installation of a different treatment system will be recommended in the near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
03/09/2023 |  | RoutineScheduled | 175-12-0276 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
02/06/2023 |  | Reportable Incident | 179-06-0225-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | [7 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [17 empty] | Inspected | replaced float in pump tank on/off | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 09:00 AM
10/27/2023 | Alternative | RoutineScheduled Component Maintenance | 177-19-0083-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 11/09/2023 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected | Please keep dirt back from all lids and especially back of the square lid for proper opening Water softner discharge needs to be seperate of septic | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
02/10/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 10:20 AM
07/13/2023 | Alternative | RoutineScheduled | 087-STS-6218 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Other"] | ["Other"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 12:00 AM
09/29/2023 | Alternative | Routine/Scheduled | 151-07-0316 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/29/2023 | 06:07 PM
11/07/2023 | Alternative | Reportable Incident Component Maintenance | 033-06-0114-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system having a blower alarm. Replaced failed blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
01/05/2023 |  | Routine/Scheduled | 228-14-0493 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 8:05AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/15/2023 | Alternative | RoutineScheduled | 109-18-0297 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Routine inspection yearly inspection. Under 1 " scum and 12" sludge in septic tank, 4 in sludge in recirc zone, 12 in sludge in discharge zone. System is operational. Alarm and floats tested good. Cleaned effluent filter, Tested pumps both good, Checked for alarms and no alarms in history. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
01/31/2023 |  | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2250 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens"] | YES | None | Clear | 7.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 11:30 AM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/25/2023 | 08:45 AM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0073-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Control Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
01/26/2023 |  | RoutineScheduled |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 750.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/28/2023 | 12:00 AM
09/16/2023 | Alternative | RoutineScheduled | SD-02-768 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | Puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/17/2023 | 02:05 PM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0159-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex RT tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump tank #2 needs pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/27/2023 |  | Routine/Scheduled | 810-STS-3963 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | Jan 1 1900 12:05PM
03/08/2023 |  | Follow-Up | SWP-01-575 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Excavated by machine to repair broken plumbing in lower zone. Installed new checkvalves and air release valves. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
09/16/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Delta, DF Series |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 18" of accumulated solids in septic tank. 22" of solids in treatment unit with a 4" crust. 5" of solids in discharge pump tank. Cleaned blower air filter. Tested alarms. Adequate aeration. All tanks need to be pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | 07:03 PM
04/03/2023 |  | Reportable Incident | 179-16-0367-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 2.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarn due to a failed timer. Manufacturer covered timer under warranty. Replaced timer. If issues with this panel continues we recomend replacing the panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
04/20/2023 |  | RoutineScheduled | SWP-04-418 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
03/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2024 | 12:23 PM
03/01/2023 |  | RoutineScheduled | 2120-08-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Effluent Screens"] | ["Disinfection" ,"Effluent Screens"] | YES |  |  | 6.900000 | 16.800000 |  | 0.000000 |  | 03/01/2023 |  | 68.000000 |  | 430.000000 | 48.000000 |  |  | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 05/02/2023 | 04:23 AM
06/20/2023 | Alternative | RoutineScheduled | 17-142-0179 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
06/20/2023 | Alternative | RoutineScheduled Component Maintenance | 033-18-0219-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 08:37 AM
09/29/2023 | Alternative | Reportable Incident | 109-06-0117 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Other conventional maintenance performed | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Completed routine inspection and filter cleaning after the repair. We returned this day with Foutz Septic to replace the root bound plastic D box with new cement d box, repair header lines, removed root intrusion in ground and around tank, removed 10 trees, tagged other trees for removal and replaced the control panel post. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/30/2023 | 09:30 AM
12/11/2023 | Alternative | Routine/Scheduled | 199-05-0124 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out. Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Noted signs of groundwater infiltration within discharge riser Aeration Condition of above Component Notes for above Component Water level normal. Flushed and cleaned weir. Checked and confirmed high level alarm float is functioning properly. Noted root infiltration within aeration riser. No quick disconnect union for airline and unable to service diffuser as a result. Due for pump out. Refill is required for proper operation and to prevent damage to components Air Pump/Blower Condition of above Component Notes for above Component Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Distribution Box Condition of above Component Notes for above Component Water level normal. Structural integrity of distribution box appears to be intact. Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 12:49PM
06/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 06/27/2023 | Sample Chamber | 41.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 2"scum/ Microfast ATU-4"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-269 ETM-22h 11m/ Pump2-252 ETM-21h 1m/ Peak-7/ High-10/ On-4m 30s Standard off-9h 55m Peak off-7h 55m/ No breakout or spongy areas on the drainfield and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/20/2023 |  | RoutineScheduled | 179-08-0115-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
04/17/2023 | Alternative | Routine/Scheduled | S 093-19-0086 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Dec 30 1899 11:37AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | House is not occupied at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
02/20/2023 |  | RoutineScheduled | -STS-20164 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | NO | Musty | Clear | 6.800000 |  |  | 1.400000 |  | 02/21/2023 | Sample Chamber | 3.000000 |  |  | 1.300000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/06/2023 | 12:00 AM
03/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Was unable to inspect cp it is an interior and no one was home. Also home owner needs to make sure that he mows the drain field area. We inspected but getting tall. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
10/09/2023 | Alternative | RoutineScheduled | 177-STS-89454 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/14/2023 |  |  | 03-142-0422 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/24/2023 | 12:00 AM
11/16/2023 | Alternative | Routine/Scheduled | 150-09-0143 | King William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The Clearstream tank needs to be pumped and cleaned. There is visible wetness on the drainfield. Only could locate one vacuum breaker. The timer is set to 9 minutes every 1 hour. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/16/2023 | 08:00 AM
12/15/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo | [6 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [16 empty] | Pumped Out | Replaced pump and floats | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/15/2023 | Dec 30 1899 10:30AM
06/28/2023 | Alternative | Routine/Scheduled | 099-STS-92360 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 10:00 AM
12/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Discharge | UV |  | ["Attached Growth Medium","Disinfection"] | ["Attached Growth Medium","Disinfection"] | YES |  |  | 6.090000 |  |  |  | Ecoli 21 MPN/100mL and DO=106.1% | 01/04/2024 | Sample Chamber | 24.000000 |  |  | 18.000000 |  |  | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Pump Tank to Puraflo Modules-2"sludge 0"scum/ No pump out needed at this time/ Puraflo Peat was turned and in good condition at this time, no ponding/ Jet UV-Light bulb and cord is faulty and requires replacement/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-7423 ETM-66h 45m/ Pump2-7370 ETM-66h 7m/ Peak-11/ High-13 Returned to replace the UV-Light bulb and cord. Repair complete, DO and PH samples taken on 12/29/2024, all other samples taken on 1/4/2024 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/15/2023 | Alternative | RoutineScheduled | 119-STS-100550 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | YES | [16 empty] | Exempt | Charcoal filter changed Installed new buzzer on alarm panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Alarm was on upon arrival. Audible had been unplugged and was plugged back in. Recirculation float was stuck down. The system should return to proper operation now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/01/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 |  |  |  | Gravity | Pressure | Drip | Not Applicable | 300.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
05/11/2023 | Alternative |  |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 2750 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Attached Growth Medium","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | YES | Pungent | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/11/2023 | Dec 30 1899 9:55AM
11/16/2023 | Alternative | RoutineScheduled | 00-192-14 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 4 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/16/2023 | 12:00 AM
01/09/2023 |  | RoutineScheduled | 099-STS-89498 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Off float stock close, replaced. Blower 3.0 amps. PEAK counts 12, Etm 1h17m. HL 9, ETM -OM. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
03/07/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/15/2023 | Alternative | RoutineScheduled | 12-120-0220A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Pura Flow |  | Pump | Pressure | Mound | Not Applicable |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
03/28/2023 |  | RoutineScheduled | SP-05-606 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Water quality not as good as last year notice some trash as cigarette butter in tank and alot or regrowth. Media is not clogged completely but water level is higher than normal, will check next year. Removed small roots that was growing in septic tank if it grows in again we are going to have to dig up that corner of tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
10/13/2023 | Alternative | Routine/Scheduled | 033-18-0218-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Orenco Advantex |  | Pump | Gravity | Pad | UV | 100.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Uv bulb changed. Filter cleaned. Manifold flushed. Averaged 5 overrides per day. System appears to be operating normally. Filter was clogged. Septic tank needs a pump out. There are some low areas around the pad that need to be filled to promote runoff. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 10:32 AM
09/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Septic Tank #1 | Septic Tank #2 | Pump | Pressure | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [7 empty] | 09/06/2023 | Sample Chamber | 21.000000 |  |  | 28.000000 |  |  | Attached to this report |  | EZ-Treat to Drainfield: Septic Tank #1-6"sludge 6"scum/ Septic Tank #2-4"sludge 0"scum/ EZ-Treat Recirculation Tank-3"sludge/ Pump Tank to Drainfield-2"sludge/ Pump Tank to LPD Drainfield-2"sludge/ No pump out needed at this time/ Recirc pump intake cleaned/ Controls, pumps, floats and alarms are functioning properly Counts: Pumps to Drainfield: Pump1-008789 ETM-0260313/ Pump2-008660 ETM-0260096/ Pumps to LPD Drainfield: Pump1-764 ETM-40h 54m/ Pump2-723 ETM-38h 49m Peak-121 High-17/ EZ-Treat Pump: Pump-0195461 ETM-0872630 On-2.5m Off-10m/ No breakout or spongy areas on either drainfields. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/28/2023 | Alternative | Routine/Scheduled | 071-STS-11572 | Giles | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Aqua Safe |  | Pump | Pressure | Discharge | UV |  | None | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | Clear | 6.800000 | 7.400000 |  |  |  | 08/18/2023 | Pump Chamber | 2.200000 |  |  | 2.800000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | 05:00 PM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/26/2023 | Alternative |  |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2250 | 1250 | 1000 | Pump | Gravity | Mound | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Pungent | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | 12:00 AM
12/28/2023 | Alternative | Initial Visit | VAG408446 | Highland | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Sand Filter | Gravity | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The sand filter was in good visible condition without any visible leaks. The wet lands bed was in good condition without and visible leaks. There were chlorine and de-chlorine tablets present at the time of inspection. The out fall pipe was covered with debris so it was cleaned off. There were no samples drawn because there were no discharge at the time of inspection. This cabin is vacant for most of the year. The lids were secured. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/17/2024 | 04:10 PM
07/31/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 02:30 PM
02/03/2023 |  | Pump-Out Only | 234-15-216 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | Jan 1 1900 8:00AM
09/20/2023 | Alternative | RoutineScheduled | 107-02-0577 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | 12:00 AM
08/24/2023 | Alternative | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensor, pump and controls operating. Drip Field - headworks serviced. - field overgrown | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | Dec 30 1899 2:30AM
01/04/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/21/2023 |  | RoutineScheduled | 075-STS-31475 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | EZ Treat |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:00 AM
03/27/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [18 empty] | pumped out 6/13/2023 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/13/2023 | 12:00 AM
11/07/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  | 600.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/08/2023 | 10:48 AM
03/28/2023 | Alternative | RoutineScheduled | 159-07-0041 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 2.000000 | 1250 | Ecoflo |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | 12:00 AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/17/2023 |  | Routine/Scheduled | NYII-ATHMSE | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Jan 1 1900 2:10PM
05/10/2023 | Alternative | RoutineScheduled | 08-160-0183 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [] |  | Septic | Dark Brown | [14 empty] | Inspected | - recommend tank be pumped/cleaned - air is not making it to tank from the aerator, a repair is needed to correct this issue | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/22/2023 | 12:00 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/09/2023 | Alternative | RoutineScheduled | 101-08-0028 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | EcoFlow |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 04:25 PM
12/05/2023 | Alternative | RoutineScheduled | 139-05-0211 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Pump | Pressure | Drip |  | 150.000000 | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 11:00 AM
06/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001527 | Jacob | Hott | 1.000000 | 1875 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled | 182-05-0053 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation","Recirculation Pump","Distribution Pump Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation","Distribution Pump Operation"] | [17 empty] | Pumped Out | Blower and damaged air pipe replaced. Pump replaced | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/19/2023 | 12:00 AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 107-05-0384 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance | 175-05-0624 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/20/2023 | 12:57 PM
12/18/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [16 empty] | Pumped Out | Replaced pump with Zoehler 152, on/off float and alarm float. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/18/2023 | Dec 30 1899 10:00AM
03/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent pump had failed. It was replaced and the system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/07/2023 | Alternative | RoutineScheduled | 121-STS-11948 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001094 | David | King | 2.000000 | 1500 | BioMicrobics Microfast 0.5 |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Cleaned effluent screens, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/12/2023 | 12:00 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/11/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
03/24/2023 |  | Routine/Scheduled | {FIPSCode}-STS-4871 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/24/2023 | Jan 1 1900 12:35PM
04/01/2023 | Alternative | Routine/Scheduled | 04-160-0497 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/01/2023 | 12:15 PM
06/02/2023 |  | RoutineScheduled | 124-STS-2379 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Virginia Beach | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/31/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
02/23/2023 |  | RoutineScheduled | 099-14-0006-SP | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | UV light has malfunctioned and is allowing effluent to bypass the drip dispersal system. Owner is working with an engineer on proper removal or replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
05/22/2023 |  | RoutineScheduled | 175-01-0641 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Delta ATU to Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-5"sludge 0"scum/ ATU-0"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, floats and alarms functioning properly/ Pump is demand dose, no counts or ETM readings on the panel/ No breakout or spongy areas on the LPD Trenches and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/27/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 11:51 AM
02/04/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Delta Whitewater, DF Series |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned septic tank filter. Cleaned blower air filter. Treatment unit solids - 2" crust, 1" on bottom. 4" of solids in discharge pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 07:03 PM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0107 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | Musty | Clear | [5 empty] | 07/19/2023 |  | 34.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
12/28/2023 | Alternative | Reportable Incident | 095-STS-5979 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Clearstream. System was no longer in Alarm and everything functioning properly. Found lots of solids build up in the aeration tank causing the float to come up. Septic tank also has 14" of sludge in it. Customer approved to pump and refill the septic tank and skim the aeration tank. Also approved a case of bio one that needs to be added and case dropped off. Customer will be in the outer banks for a little while | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | Dec 30 1899 9:16AM
07/10/2023 | Alternative | RoutineScheduled | 175-15-0521 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | NA | [17 empty] | Septic Tank-4"sludge 12" scum/ Microfast ATU-0"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ Pump out required on the Septic-Microfast Tank due to scum layer/ Blower air filter cleaned and blower working correctly/ UV-Light sleeve cleaned and light working properly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-11949 ETM-3709h 44m/ Peak-2 ETM-2h 22m On-18m 45s Off-2h 41m/ Watermeter-0754321.1/ Noted: Wet area on the drip field/ Found check valves in zones 1 & 2 were faulty and replaced/ Returned on 08/04/2023 to follow up on the wet area and found area is now dry. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-486 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend replacing the EZ set riser lid of the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | 182-17-0221 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | EcoPod | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Water Meter- 300.3 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
08/28/2023 | Alternative | Reportable Incident |  | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | [9 empty] | N/A | [16 empty] | Pumped Out | Pumped septic tank and sewer line for repair - reportedly the sewer line to a reported AOSS was never connected! !!! No information presented as to type of AOSS, components, etc. to properly complete report. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/31/2023 | 06:30 AM
02/27/2023 |  | RoutineScheduled | 02-195-150 SR | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Advantex |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation","Control Operation","Dispersal System Operation"] | ["Attached Growth Medium","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | 12:00 AM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 12/19/2023 |  | 3.000000 | [5 empty] | Will be sent separately | Inspected | Lab normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
04/18/2023 |  | Initial Visit | 107-11-0155 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Recirculation Pump","Septic Tank Baffles","Dispersal System Operation","Auxiliary Filter"] | [18 empty] | Septic needing to be pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | 12:00 AM
02/02/2023 | Alternative | RoutineScheduled | 115-16-0136 | Campbell | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 3500 | Septic Tank | EZTreat | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [7 empty] | 02/02/2023 | Pump Chamber | 140.000000 | [5 empty] | Attached to this report |  | The system did not need to be pumped, however The flea market has recently installed a commercial dishwasher and keeps the grease so hot that it is flowing from tank to tank. The grease is causing grease build up in the treatment pods. this is causing the BOD and TSS to be outside of the permitted limits. After a consultation with the land owner, we are in the process of consulting with a PE on how we can go about fixing this problem. The system, however is operating how it was originally designed. The Septic tank filter was pulled and cleaned. The controls were operating as designed. The treatment pods were sprayed off and cleaned. There were no visible leaks in the leech field. The lids were secured. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/25/2023 | 11:55 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/06/2023 | Alternative | RoutineScheduled Component Maintenance | SD-08-219 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Pump is 15 years old and appears to slowing down a bit (accurate flow-rate measurement is difficult with the drainback hole). Pump should be upsized slightly when it gets replaced to ensure that it delivers a few gpm over the 28 gpm minimum required for 4 Puraflo pods. Peat is in good shape for its age. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
06/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | [7 empty] | 06/22/2023 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected | Replaced discharge pump lab sample normal | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
11/02/2023 | Alternative | Routine/Scheduled | 800-02-0490 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 8:30AM
08/16/2023 | Alternative | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 3000.000000 | [] | [] |  |  |  | 7.350000 | 5.070000 | 18.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:30 PM
01/18/2023 |  | RoutineScheduled | 18-125-131 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 12 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/18/2023 | 12:00 AM
04/11/2023 |  | Routine/Scheduled | 13-118-0011 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 90.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | UV bulb was changed. The Advantex manifold was flushed. Spin emitters were not functioning properly. Emitters were disassembled and cleaned. The intake screen of the recirculation pump was clogged with hair. One of the emitters was still not functioning properly and must be replaced. System is not processing sewage properly because of excess use of bleach and adding Ridex. Emitter was replaced. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/11/2023 | Jan 1 1900 12:56PM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0007-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Septic tank needs pump out due to solids. Blower 2.76 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
01/05/2023 |  | RoutineScheduled | 08-172-0081A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | MicroFAST |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 9:25AM
03/23/2023 |  | RoutineScheduled | 09-113-091 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/23/2023 | 12:00 AM
11/03/2023 | Alternative | RoutineScheduled | 019-STS-24199 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic tank under minimal scum -5-6" sludge, recirculation zone 8" trace sludge and discharge zone 6-10" light trace of sludge. System does not need pumping at this time. filter was clean, Checked floats, alarm and wiring, All Test ok, recir pump 626.4 hours and 46,401 cycles and discharge pump has 60.6 hrs and 700 cycles. system is good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
04/28/2023 |  | Initial Visit | VAG408349 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST ATU | Constructed Wetlands | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection"] |  | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/07/2023 | 10:30 AM
06/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001527 | Jacob | Hott | 1.000000 | 2000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/29/2023 |  | RoutineScheduled | 107-07-0300 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled | 09-184-5002 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/27/2023 | 12:00 AM
05/11/2023 | Alternative |  | 099-15-0019-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
10/16/2023 | Alternative | RoutineScheduled | 107-17-0040 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | pump line has settled putting pressure on pipe in tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
12/09/2023 | Alternative | RoutineScheduled | 109-05-0335 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 11" of accumulated solids in first section of septic tank. 12" of accumulated solids in second section of septic tank. Cleaned septic tank solids filter. 0" of solids in recirculation portion of treatment unit. 3" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Cleaned drip manifold spin filter. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2024 | 07:03 PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | SD-13-340 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
12/20/2023 | Alternative |  | 085-STS-31763 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 12:00 AM
08/29/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-4829 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 1:15PM
11/27/2023 | Alternative | Routine/Scheduled | 08-120-0250A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | annual maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Aeration: Water level normal. Confirmed aeration. Not due for pump out -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. -Control Panel: Checked and confirmed components within control panels are functioning properly. Checked and confirmed audible alarms are functioning properly. Checked and confirmed visual alarms are functioning properly. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | Dec 30 1899 12:51PM
11/17/2023 | Alternative | RoutineScheduled | 04-197-A15 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/17/2023 | 12:00 AM
12/16/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-11802 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | ISF | Gravity | Pressure | Discharge | Chlorination |  | [] | [] | YES | Musty | Cloudy | [15 empty] | No Discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/02/2024 | 11:20 AM
12/05/2023 | Alternative |  | 89-113-155 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/05/2023 |  | 2.180000 | [5 empty] | Will be sent separately |  | BOD: 2.18 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
06/21/2023 | Alternative | Routine/Scheduled | 157-84-180 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Purasys |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 10.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 05:39 PM
07/21/2023 | Alternative | RoutineScheduled | 175-08-0274 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank to Delta DF-60 ATU | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 0"scum/ Delta DF-60 ATU-3"sludge/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-46101/ Pump Run Time Hours-7511/ Hand-56/ Override-127/ High-268/ Watermeter-162044.3/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/10/2023 | Alternative | RoutineScheduled | 181-14-0085 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","SludgeScum Accumulation","Effluent Screens"] | ["Auxiliary Filter","SludgeScum Accumulation","Effluent Screens"] | YES | [16 empty] | Pumped Out | The MicroFast and pump tank were both pumped and cleaned. The blower and spin filters were both pulled and cleaned. The treatment unit was in good operating condition. The discharge pump was pulled and cleaned. There was return effluent returning to the pump tank from the drip field, so the drip field was operating as designed. The controls were operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 02:00 PM
03/22/2023 | Alternative | Routine/Scheduled | 07-160-0143 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 267.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/22/2023 | 12:30 PM
05/26/2023 | Alternative | Routine/Scheduled | 234-18-88 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level Aeration Tank - normal level - NO mixing present - compressor has blown diaphragms. Pump Tank - float sensors, pump and controls operating. U.V. - bulb and housing serviced. Drip - headworks serviced - vacuum breakers damaged - | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/05/2023 | Dec 30 1899 12:00PM
08/03/2023 | Alternative | RoutineScheduled | 18-192-146 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 - Blue Crystal tablets added 10 - Bio Max tablets added | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/03/2023 | 12:00 AM
04/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/20/2024 | 08:56 AM
07/05/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-5576 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | Dec 30 1899 7:30AM
04/11/2023 |  | Pump-Out Only |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | 06:30 PM
12/07/2023 | Alternative | Routine/Scheduled | R16-180-0103 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Gravity | Gravity | Discharge | UV |  | None | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | Dec 30 1899 11:30AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0057-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 2.96 amps. Water level little higher than normal due to filamentus bacteria most likely will need chemical clean next year. Treatment crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
06/01/2023 |  | RoutineScheduled | 2004-143-0335 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NO | None | Clear | [15 empty] | Peat media will require replacement in the near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 2000 | BioMicrobics Fast |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic Tank - 1" scum / 6" Sludge minimal paper floating, Fast treatment tank- unit -Has no access - -Sounds like proper aeration from the vent tube. Blower ALarm is good - Cleaned blower Air filter - Very dusty, 9 amp on blower start - Alarm test sounds alarm. Pump Tank - Float switches function properly. System appears fully operational, no bad odors detected. Fast system has no access ports. System appears to not need pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
05/19/2023 | Alternative | RoutineScheduled | 154-17-0280 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/28/2023 | 12:00 AM
05/16/2023 |  | RoutineScheduled | 175-05-0628 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
05/17/2023 | Alternative | Routine/Scheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1125 | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip |  | 600.000000 | ["Control Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Control Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | YES | [16 empty] | Pumped Out |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/29/2023 | 11:52 PM
11/30/2023 | Alternative | RoutineScheduled | 182-05-0061 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.610000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 02:00 PM
09/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 3.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 3:10PM
06/19/2023 | Alternative | Routine/Scheduled | 136-17-0374 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service - Owner notes that he had leaking toilet fixture (Repaired) that had the system in alarm condition for about 1 week! Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating - evidence of recent high level. Drip field - headworks serviced - several areas of "wetness" present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 11:30 AM
01/09/2023 |  | RoutineScheduled | 175-14-0400 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
04/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/06/2023 |  | RoutineScheduled | 153-STS-20307 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
10/05/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend flushing and balancing the lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/31/2023 | Alternative | Routine/Scheduled |  | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced Pump Tank - float sensors, and controls operating - discharge pump has been replaced by "others" and is a "wellTrol well pump" not designed for septic applications. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 11:00 AM
01/31/2023 |  | RoutineScheduled | 179-STS-89394 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Initial inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
02/03/2023 |  |  | 08-142-0120 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Delta Whitewater | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
05/25/2023 | Alternative | Initial Visit | 128-08-064 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Remote Absorption Field - not under contract | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 01:30 PM
10/12/2023 | Alternative |  | 179-STS-92443 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/10/2023 |  |  | 033-06-0033-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
10/01/2023 | Alternative | Routine/Scheduled | 041-STS-261313 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1000 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/01/2023 | Dec 30 1899 10:00AM
11/13/2023 | Alternative | Pump-Out Only | 121-STS-12411 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | AQUASAFE / DIRECT DISCHARGE | [6 empty] | [] | [] | [17 empty] | Pumped Out | Pumping & Cleaning Alternative Septic Tank (1000 gallons) JOB SCOPE: Pumped/cleaned septic tank; septic system is functioning at this time but not as designed as there are components that are recommended to be repaired/replaced. - outlet line higher than inlet line, recommend repaire/replacement - recommend pumping/cleaning of Aquasafe unit | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/14/2023 | 12:00 AM
10/12/2023 | Alternative |  | 179-STS-91836 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 |  | RoutineScheduled | 175-14-0269 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation"] | ["Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Recirc trough is underwater again and covered by a fuzzy, tan growth. This is surprising since media was chemically cleaned and tank pumped out last April. Recommended to owner that influent samples for BOD,TSS, and FOG be collected to rule out that incoming wastewater strength is excessively strong. The effluent is still clear, just not at the level it should be. The audible portion of the atu panel has failed. Parts are evidently not available so complete panel will need to be replaced with an updated model. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 177-14-0086-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
06/01/2023 | Alternative | Reportable Incident | 136-15-0014 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Distribution Pump Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial visit Primary septic tank - normal level - pumped 2 weeks prior - effluent screen serviced - broken and requires replacing / upgrade. BioFilter - concrete - peatmoss spent - requires replacing. Pump Basin - pump failure - replaced - float sensors & controls operating. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/07/2023 | 11:00 AM
11/10/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | Dec 30 1899 10:40AM
08/14/2023 | Alternative |  | 09-125-077 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/14/2023 |  | 10.600000 | [5 empty] | Will be sent separately |  | BOD: 10.6 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/14/2023 | 12:00 AM
05/04/2023 |  | RoutineScheduled | 145-03-0033 (LEGACY ALT. SYSTEM) | Highland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NO | [17 empty] | The system did not need to be pumped. It was scheduled for a routine pumping and was requested to be pumped at the real estate closing. The blower was not running at the time of inspection so the blower was replaced. The controls were operating as designed. There were no visible leaks in the drip field. There was return effluent returning to the pump tank so the drip field was operating as designed. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/03/2023 | 12:15 PM
01/23/2023 |  | Initial Visit | 182-13-0085 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Presby |  |  | Gravity | Trenches |  |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [17 empty] | Pumped Out | adjust timers in dbox | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 12:00 AM
01/03/2023 |  | Routine/Scheduled | 234-17-311 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | Jan 1 1900 1:40PM
05/15/2023 | Alternative | RoutineScheduled | 115-05-0226 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | [15 empty] | Inspected | Sludge level-Trace scum and 14" sludge in Septic tank - Trace of sludge in Pump tank. Float switches tested operational. Peat Looks dry yet moist and okay for age- not been used yet this season thus dry. Peat level is lower and is worn/aged -Peat was clumped, broken up and turned in both sides with more roots in the top half. Ttipping tray was normal. Raked all 4 quadrants. Alarm and pump are operational. Cleaned Effluent filter. Blackwidow spirders sprayed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
04/03/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 2-3 0-1 | 0-0 | [5 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 9.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 09:00 AM
04/08/2023 |  |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 21000.000000 |  |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
04/27/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The trees were removed from the ends of the lines. DSS verified that the lines were not impacted. The system appears to be functioning as designed at this time. Recommend homeowner monitor that area and notify if there are any changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | LPD |  | Pump | Pressure |  | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic Tank 1-3" scum layer on top and about 8" sludge layer on bottom- Pump tank has 6" sludge. We check and opened the LPD drain lines caps one the lpd lines. Counted 10 caps. Level is good, floats test good. Pump and alarm are operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
02/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/26/2023 |  | Initial Visit | 183-STS-10185 | Sussex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the red light. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and cleaned the diffuser in the Clearstream. Changed the filter in the aerator. Fixed the alarm in the Clearstream - it was opened. The septic tank needs additional risers on it to be properly inspected in the future. The timer is set to 1.5 minutes every 2 hours. Did not take initial sample. There is visible wetness on the drainfield - most likely from rain - once it dries need to keep an eye on it. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/26/2023 | Jan 1 1900 9:30AM
11/09/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 1.000000 | 1069 | FujiClean CEN7 |  | Gravity | Gravity | Trenches | Not Applicable | 50.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | Musty | Clear | 6.900000 | [13 empty] | Inspected | Serviced the FujiClean system per manufacturer's O&M manual, measured 16" sludge in chamber 1 and 6" in chamber 2; cleaned blower air filter; absorption trench area showed no signs of a malfunction. Recommend that the treatment tank be pumped out within the next 6 months | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/26/2023 | 12:00 AM
02/28/2023 |  | RoutineScheduled | 179-07-0058-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Root infiltration on pump tank wedge lid, recommend taking care of this before problem become bigger. Inspection done after rain and no water was infiltrating. Proposal will be sent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
03/30/2023 |  | RoutineScheduled | 89-113-155 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/30/2023 | 12:00 AM
05/17/2023 | Alternative | Pump-Out Only | 13-160-0090 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Microfast | [6 empty] | [] | [] | [18 empty] | Pumping & Cleaning Microfast Pretreatment Tank (1500 gallons) JOB SCOPE: Pumped/cleaned tank; septic system is functioning at this time but not as designed as there are components that are recommended to be repaired/replaced. - inlet line is completely underwater, recommend further evaluation due to the high levels in tank CUSTOMER DOES NOT WANT TO PROCEED WITH REQUIRED MAINTENANCE/INSPECTION OF SEPTIC SYSTEM AT THIS TIME | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/18/2023 | 12:00 AM
05/08/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A septic system inspection of a conventional gravity. This system is in the front of the house. Believe this system was used for laundry only. The sewer line is cast iron and when camera snaked the line is separated and settled before the tank. The septic tank was lid was dug up it was 14" under the surface. the tank was pumped out and inspected for any cracks and none were seen. The conveyance line is cast iron and had a lot of sludge in it. The 8 port concrete d-box was at ground level and badly broken. Was not able to camera snake the headers they had dirt packed in them. Also was not able to camera snake the drain field lines. At time of inspection the septic system was not in working condition. This inspection does not guarantee the life of any component. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
05/31/2023 | Alternative | RoutineScheduled | 182-05-0423 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled | 115-13-0194 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank |  | Pump | Pressure | Trenches | Not Applicable |  | ["Distribution Pump Operation","None"] | ["None"] | NA | Musty | [15 empty] | Inspected | Sludge level-1" Scum trace & 12" Sludge in Septic tank. Pump tank 5-8" fine Sludge trace. Alarm functional and pump is operational, Drainfield appears dry at this time. Owner is looking into LPD header line repair for PVC drainfield manifold,We noted a muddy spot on the main header lines but no obvious leak has been found or surface water showing. Owner will locate any leaks and repair it. Possible a crack in a line from settling?. needs looking into. Owner maintains the drainfield cutting 3x a year. No roots observed in tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
09/20/2023 | Alternative | Reportable Incident Component Maintenance | SD-07-167 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | Septic | [14 empty] | Will be sent separately | Inspected | High level alarm in both tanks. Discharge pump had been pulling high amps, tripped breaker inside the house. Replaced the discharge pump. Attempted to connect to the Vericomm panel, got error message that the panel had no ID and no program. Discussed with Orenco tech support. Program reappeared a short time later, but panel was still not running any automatic cycles for either panel. Noticed that the condensation heater for the panel was very hot to the touch (not normal). Program and ID disappeared again. Had second conversation with Orenco. Came back the next morning and installed a new motherboard and panel heater. Programmed and tested the new board. Put panel in and out of test mode and backed up the settings. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 12/20/2023 | Dec 30 1899 2:30PM
09/13/2023 | Alternative | Routine/Scheduled | 175-07-0232 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | [15 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | Dec 30 1899 8:00AM
10/09/2023 | Alternative | RoutineScheduled | 061-STS-21804 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank-8"sludge 1"scum/ EZ-Treat Recirculation Tank-14"sludge 0"scum/ Drip Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Recirc. pump intake cleaned/ Controls, pumps, floats and alarms are functioning properly/ Counts: Drip Pump-4354 ETM-542h 12m/ Peak-8/ High-18/ Watermeter-0,131,064.2/ No breakout or spongy areas on the drip field and is dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/24/2023 | Alternative | Routine/Scheduled | 157-18-0057 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 07:15 AM
03/01/2023 |  | RoutineScheduled | 181-05-0408 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Best1 |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did not need to be pumped but will be pumped next year. The effluent filter was pulled land cleaned. The spin filter and blower filter were both cleaned. The controls were operating as designed. There were no visible leaks in the drip field. The drip field was operating as designed. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 09:40 AM
04/18/2023 |  | Routine/Scheduled | 041-STS-260406 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/18/2023 | Jan 1 1900 5:10PM
10/12/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
04/05/2023 |  | RoutineScheduled | 132-07-0199 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Wet Land | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
02/10/2023 |  | RoutineScheduled | 10-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 4 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/10/2023 | Jan 1 1900 5:15PM
08/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | Dec 30 1899 9:10AM
09/04/2023 | Alternative | Follow-Up Component Maintenance | 179-17-0025-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to inspect d-box and camera header lines due a tech leaving d-box lid off during a rountine inspection. Speed levelers got knocked off due to a rabbit falling into the d-box. Header lines were all clear after inspecting with camera and d-box was retimed. Homeowner stated he was going to make arrangments to have two compartment fast tank pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89394 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend mowing the drain field area and maintaining it in a mowed condition to prevent roots from growing into the drain field lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
05/15/2023 | Alternative | RoutineScheduled | 115-01-0049 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank |  | Pump | Pressure | Trenches | Not Applicable |  | ["Distribution Pump Operation","None"] | ["None"] | NA | Musty | [15 empty] | Inspected | Sludge level-1" Scum trace & 12" Sludge in Septic tank. Pump tank 5-8" fine Sludge trace. Alarm functional and pump is operational, Drainfield appears dry at this time. Owner is looking into LPD header line repair for PVC drainfield manifold,We noted a muddy spot on the main header lines but no obvious leak has been found or surface water showing. Owner will locate any leaks and repair it. Possible a crack in a line from settling?. needs looking into. Owner maintains the drainfield cutting 3x a year. No roots observed in tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
05/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
10/06/2023 | Alternative | RoutineScheduled | 107-18-0302 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
08/23/2023 | Alternative | RoutineScheduled | SWP-05-228 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-1 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | 02:00 PM
06/08/2023 | Alternative | Reportable Incident | 159-19-0068 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Advanced Septic |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | [18 empty] | Aquasafe ATU Alarming - failed diaphragms on compressor - replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:45 PM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0407 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
03/10/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Ecoflow | Gravity | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","SludgeScum Accumulation"] | YES | [17 empty] | 0 Scum, 12" Of sludge, Cleaned the effluent filter. Cleaned bucket. Bucket working well. Peat not looking good. Holding a little water. Needs replaced in the next year of it will fail. Opened d-box. Effluent looked good. Reset speed levelers. Field looks good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 08:00 AM
08/01/2023 | Alternative |  | 10-113-039 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/01/2023 |  | 4.930000 |  |  | 1.500000 |  |  | Will be sent separately |  | BOD: 4.93 TSS: 1.50 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/01/2023 | 12:00 AM
05/04/2023 |  | Routine/Scheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/19/2023 | 12:30 PM
04/26/2023 |  | Routine/Scheduled | {FIPSCode}-STS-4546 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 11:25AM
06/22/2023 | Alternative | Reportable Incident Component Maintenance | 179-STS-89371 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in a low level alarm due to a enable float being stuck on. Replaced enable float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
12/15/2023 | Alternative | RoutineScheduled | 08-113-080 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/15/2023 | 12:00 AM
09/18/2023 | Alternative | Routine/Scheduled | 085-STS-32091 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. -Media Sheets: Cleaned media sheets. Checked and confirmed spray pattern is good. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 4:08PM
06/03/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 13" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Removed floating solids from recirculation area of treatment unit. 10" of solids in discharge portion of treatment unit. 6" of solids in recirculation portion of treatment unit. Excellent treatment quality. Septic tank and treatment unit may need to be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | 07:03 PM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 196-07-180 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
11/16/2023 | Alternative | Initial Visit | 113-STS-25895 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 3.000000 | 6050 | Septic Tank Only | EZ-Treat 1,200 | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | [7 empty] | 11/16/2023 | Pump Chamber | 9.000000 |  |  | 9.310000 |  |  | Attached to this report | Pumped Out | The 1000 Gallon pump tank was pumped and cleaned. The effluent filters were pulled and cleaned. The recirculating pumps were both pulled and cleaned. The EZ- Treat sprayers were pulled and cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The BOD and TSS effluent samples were well within permitted limits. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 11:45 AM
11/30/2023 | Alternative | Routine/Scheduled | 05-160-0195 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 217.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 09:30 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/27/2023 |  | Routine/Scheduled | 234-03-11158 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | Jan 1 1900 1:10PM
06/20/2023 | Alternative | Follow-Up Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Observed 2 additional lines were installed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
10/26/2023 | Alternative | Routine/Scheduled | 093-12-0001 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 9:30AM
10/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 10/30/2023 | Sample Chamber | 8.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance | 154-04-0829 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
02/15/2023 | Alternative | RoutineScheduled | 154-07-0636 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | UV control box needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
07/11/2023 | Alternative | Routine/Scheduled | 093-09-0137 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Drip Field - headworks serviced - Drip field flushed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | Dec 30 1899 10:45AM
10/24/2023 | Alternative | RoutineScheduled Component Maintenance | 182-07-0176 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
09/23/2023 | Alternative | RoutineScheduled | 109-01-0574 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | PuraFlo |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual; inspection. 15" of accumulated solids in septic tank. Cleaned septic tank solids filter. 4" of accumulated solids in pump tank. Raked peat in treatment pods. Peat is in good condition. Tested pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 07:03 PM
02/09/2023 |  | Reportable Incident | 228-14-0022 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [16 empty] | Pumped Out | Replaced pump & timer override float, pump relay, alarm bulb, and re-wired junction box. Cleaned pump screen and screen filter. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/09/2023 | Jan 1 1900 4:30PM
07/10/2023 | Alternative | Routine/Scheduled | 800-06-0194 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - recommend pumpout - refill will be required - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes serviced, spray grid serviced. Pump Tank - float sensors, pump and controls operating. - damage noted to access riser - appears to still be structurally sound. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | Dec 30 1899 7:30AM
12/27/2023 | Alternative | RoutineScheduled | 18-125-131 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/27/2023 | 12:00 AM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance | 182-15-0170 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Rejected | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Pad | UV |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 08/08/2023 |  | 10.000000 |  |  | 4.600000 |  |  | Will be sent separately | Inspected | Repaired riser extension Repaired Uv light Recommend adding more mulch to et bed | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
06/13/2023 | Alternative | RoutineScheduled | 001-STS-92422 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJI CLEAN CEN-5 |  | Pump | Pressure | Mound | UV | 150.000000 | [] | [] | [18 empty] | EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 11:05 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/18/2023 | Alternative | Routine/Scheduled | 07-120-0531A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/18/2023 | Dec 30 1899 4:40PM
08/28/2023 | Alternative | Follow-Up Component Maintenance | SWP-03-58 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank pumped out by others prior to peat replacement. Degrade peat was removed by hand and new peat was installed. Peat was purchased from DSI and degraded peat was disposed at Spotsylvania Refuse. Replaced 6 spreader bars. Distribution box has a large crack at the bottom, effluent was below dial-a-flows. Must be replaced, proposal to be sent to homeowner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
04/11/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | filter clog cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/07/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/04/2023 |  | Pump-Out Only | {FIPSCode}-STS-1317 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | [6 empty] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | Jan 1 1900 10:30AM
07/31/2023 | Alternative | Follow-Up | 128-05-191 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - Repair Pumped primary septic tank empty - serviced - effluent screen serviced. Removed damaged access riser and replaced with new. Aeration Tank - compressor re-built and placed back into operation. Pump Tank - pumped empty - new pump, float sensors and controls installed. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/01/2023 | 06:30 AM
12/03/2023 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Loudoun | SLUSSER, JAMES B | 1934000064 | JAMES | SLUSSER | 1.000000 | 1250 | Microfast | Septic Tank Only | Pump | Drip | Elevated Sand Mound | None |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [18 empty] | [Comments]: Trash tank pumped. Cleaned repaired. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2012 | 08:48 PM
04/12/2023 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. tratment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 8:00AM
06/13/2023 |  |  | 179-STS-91826 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/16/2023 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  | 450.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | 09:36 AM
03/23/2023 |  |  | 00-142-0693 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [18 empty] | Replaced bad contactor | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/14/2023 | 12:00 AM
04/03/2023 | Alternative | RoutineScheduled | 115-10-0091 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 4.000000 | 8000 | Septic Tank | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable | 3600.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","Control Operation","SludgeScum Accumulation"] | YES | Musty | Cloudy | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | 10:30 AM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
03/10/2023 |  | Follow-Up | 179-12-0160-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disassemble components in recirc tank and assist pumper with proper pump out. Reaasembled components and refilled tank back to proper levels. Replaced discharge alarm float. Homeowner questioned why the tank needed to be pumped out again in after 2 years. He texted pictures of the laundry products the household is using. Fabric softner and laundry detergent has fabric softner in it as well. I advised these products can not be used on a septic system as it causes a bad growth in the septic system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
07/09/2023 | Alternative | RoutineScheduled | 137-34-067 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic | Microfast | Gravity | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 07:25 AM
08/24/2023 | Alternative | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | Biomicrobics MicroFAST |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine service Primary septic tank - workshop - normal level Pump tank - workshop - float sensors, pump and controls operating. Septic tank residence - normal level Aeration unit - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls operating. Dbox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | Dec 30 1899 2:30PM
06/14/2023 | Alternative | RoutineScheduled | 182-00-0502 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | 12:00 AM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | Dec 30 1899 2:50PM
05/26/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-83422 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | NO | [17 empty] | AOSS - Initial Visit - Real Estate Inspection by "others" Owner only wanted alarm event taken care of - found aspirator heavily off balance with debris on shaft - serviced - reinstalled and alarm event abated. System has a need for full service. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/05/2023 | 12:00 PM
02/02/2023 |  | RoutineScheduled | 10-125-046 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | 12:00 AM
12/20/2023 | Alternative | Routine/Scheduled | 157-11-0155 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream, cleaned the filter in the aerator, and cleaned the filter. Changed the diffuser in the Clearstream and changed the mesh screen in the spinfilter. Replaced the UV light bulb, replaced the UV ballast, and replaced a fuse. The timer is set to 7.5 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/20/2023 | 04:00 PM
07/14/2023 | Alternative | RoutineScheduled | 19-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | YY Services LLC | 1965006418 | Brian | Stewart | 2.000000 | 1000 |  |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 | ["Auxiliary Filter","None"] | ["Auxiliary Filter","None"] | YES | Musty | Cloudy |  | 1.000000 |  | 1.700000 | Effluent Ph 7.3 Effluent DO 6.8 | 07/14/2023 | Sample Tap | 7.980000 |  |  | 5.900000 |  |  | Will be sent separately | Pumped Out | Effluent Ph 7.3 Effluent DO 6.8 EMI Results on hand if needed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/14/2023 | Dec 30 1899 11:45AM
10/05/2023 | Alternative | Routine/Scheduled | 19-142-0040 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Orenco Advantex |  | Pump | Gravity | Trenches | UV |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Uv bulb changed, filter cleaned, manifold flushed. No overrides. Changed recirc off time from 17.8 to 20. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 8:54AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/14/2023 | Alternative | Routine/Scheduled | S 800-13-0149 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Cloudy | [15 empty] | Replaced aerator, diffuser and screen filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 3:05PM
03/28/2023 | Alternative |  | 154-17-0344 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Donya | Bauer | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/16/2023 | Alternative | RoutineScheduled | 103-STS-93165 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001302 | Charles | Langford | 2.000000 | 1000 |  |  | Pump | Pressure |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 12:00 AM
08/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001763 | Jessica | Young | 2.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/12/2023 | 12:12 PM
12/11/2023 | Alternative | Routine/Scheduled | 177-STS-89303 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | 09:00 AM
04/07/2023 |  | Pump-Out Only |  | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Rappahannock-Rapidan | McKim Septic & Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Other"] | NA | [16 empty] | Pumped Out | Pump is bad ordered waiting until it arrives | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/08/2023 | 02:00 PM
11/27/2023 | Alternative | Reportable Incident | 2018-143-0037 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Advantex RT. Customer said bathroom closest to the system was backing up. When I arrived he had a plumber there and said the sewer line was full. I opened the Inlet and found Grease built up in the tee. Was was able to cut the tee off and get the clog free, got the customer to flush 3 times and everything came out clear. I then glued the tee back on. Customer wanted us to check the tee everything six months so he approved the semi annual maintenance and since old Dominion did there inspection last spring he would like to start thr membership in March of 2024 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:33 PM
03/15/2023 | Alternative | RoutineScheduled | 159-18-0053 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [null] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
12/14/2023 | Alternative | RoutineScheduled Component Maintenance | SD-06-91 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. System may need pumpout next year due to solids. Will check next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
01/30/2023 |  |  | 02-113-378 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/30/2023 |  | 2.150000 |  |  | 1.200000 |  |  | Will be sent separately |  | BOD: 2.15 TSS: 1.20 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 12:00 AM
07/06/2023 | Alternative | Pump-Out Only |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 428 | Clearstream |  | Pump | Pressure | Drip | [21 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 10:54 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/19/2023 |  | RoutineScheduled | SWP-01-682 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Annual inspection. Evidence of infiltration in the pump tank at the midseam (wet rust stains), at the buried wedge lid (long roots hanging down), and perhaps to a smaller extent at the buried wedge lid, inlet end of septic tank (short grass roots). Recommend digging, exposing and inspecting the pump tank, then resealing the midseam and wedge lid if no structural problems. Recommend pumping out the septic tank for sludge accumulation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 11:17 AM
11/02/2023 | Alternative | Routine/Scheduled | E-11-111-0068 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | EcoPure |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | Dec 30 1899 1:00PM
07/15/2023 | Alternative | RoutineScheduled | 09-100-0180 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1250 | BIOCOIR |  | Pump | Gravity | Mound | Not Applicable | 600.000000 | [] | [] | YES | [17 empty] | EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 12:55 PM
01/05/2023 |  | Routine/Scheduled | 03-142-0122 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. PUmp Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 7:30AM
07/25/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 12:00 AM
09/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/24/2023 | Alternative | RoutineScheduled | 127-STS-33416 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Recirculation Pump","Control Operation","Distribution Pump Operation"] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/18/2023 | Alternative | Routine/Scheduled | 04-142-0087 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump and effluent screen serviced. - recommend pump out and refill. Treatment Module - media drapes & spray grid serviced. PUmp Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 11:30AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Hydro-Action ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/21/2023 | Alternative |  | 101-19-0098 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Beth & Jim | Riddle | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/08/2023 | Alternative | Routine/Scheduled | 16-160-0144 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/08/2023 | 01:00 PM
09/29/2023 | Alternative | RoutineScheduled | 05-142-0102 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/08/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 000 |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/22/2023 | 12:00 AM
04/06/2023 | Alternative |  | 101-18-0088 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Laura | McGurn | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was not functioning upon arrival. Blower was replaced and the system should return to proper function | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend replacing discharge pump chamber lid. Peat is showing signs of its age. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/30/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
09/12/2023 | Alternative | RoutineScheduled | 027-STS-16062 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed 9 - Bio Max tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/12/2023 | 12:00 AM
05/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
04/20/2023 |  | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 0.000000 | 00 | Multiflo FTB |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Routine Service. Trash Tank - NOT PRESENT !!! MultiFlow - recieved direct effluent! - mixing present - compressor serviced - Pump Tank - float sensors, pump and controls operating. No indications of surfacing at pad/bed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 08:00 AM
10/27/2023 | Alternative | RoutineScheduled Component Maintenance | 182-03-0264 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
09/13/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 10:29 AM
11/15/2023 | Alternative | Routine/Scheduled | 157-06-0336 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal Level with 2" of solids and less than 1" of sludge No signs of infiltration Inlet and outlet tees intact -Aeration: Normal Level 1" of suspended solids Pulled and cleaned weir and diffuser Alarm float is functioning properly -Distribution Box: Customer would like to wait until next year -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 11:18 AM
05/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","Level Sensor Operation","BlowerCompressorAerator Operation"] | ["Level Sensor Operation","BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-12"sludge 12"scum ( Requires Pump Out) / Microfast-4"sludge/ Pump Tank-0"sludge 0"scum/ Blower air filter cleaned and blower working correctly/ Replaced faulty off float ( Stuck in closed position) Controls, pumps, floats and alarms now functioning properly/ Counts: Pump1-579 ETM-33h 20m/ Pump2-562 ETM-32h 33m Pump On-3m 30s Off-6h Peak Off-4h 48m/ Peak cnts-36/ High cnts-13/ No breakout or spongy areas of the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/22/2023 |  | RoutineScheduled | {FIPSCode}-STS-21571 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 1.000000 | 1500 | Advantex AX/RT |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge Scum Accumulation - 6" Filter Cleaned Media Lid Hinges Broken | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 1:30PM
02/03/2023 |  | Routine/Scheduled | 550-STS-6682 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | Jan 1 1900 9:15AM
04/03/2023 |  | Reportable Incident |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced decribit dbox with new. Spliced to existing conveyance line Spliced to existing header lines | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 06:30 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping treatment unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/15/2023 |  | Follow-Up | 175-14-0118 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Service Call Only: Microfast to Geoflow Drip System/ Replaced faulty blower VCF/ Tested and functioning properly/ Counts: Pump Run Time-2346/ Counts-29394/ Override-68/ High-0/ Hand-100 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/30/2023 |  | Routine/Scheduled | 800-STS-14913 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 10000 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [16 empty] | No grease in tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | Jan 1 1900 9:30AM
06/29/2023 | Alternative | Routine/Scheduled | 07-120-0684A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Effluent Screens | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen (original to install) is in extreme disrepair and requires replacement - serviced best able. Biofilter - peatmoss in poor condition - ponding present - raked / turned. PUmp Basing - float sensors pump and controls operating. DBox is in poor condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | Dec 30 1899 7:15AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 175-07-0161 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | 177-10-0135-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We removed roots from the Distibution Box and header lines to the extent possible. There are roots remaining in the top header line. We recommend excavating by hand and repairing or replacing pipe to remove the remaining roots. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
01/13/2023 |  | Reportable Incident | 234-14-278 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator & diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/13/2023 | Jan 1 1900 10:00AM
02/08/2023 |  | Routine/Scheduled | 800-STS-14318 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1.5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | Jan 1 1900 3:00PM
12/13/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Discharge | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | NA | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  | 1250 |  | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Peat fiber needs to be replaced badly broken down and also bad sample | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/23/2023 | Dec 30 1899 3:10PM
12/07/2023 | Alternative | Reportable Incident Component Maintenance | 154-16-0028 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | Septic Works LLC | 1942001080 | michael | smith |  |  | Orenco Advantex | none | Gravity | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | replaced contactor in drip panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/17/2023 | 09:07 AM
02/10/2023 |  | RoutineScheduled | 91-197-5001 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Auxiliary Filter","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/10/2023 | 12:00 AM
03/28/2023 |  | RoutineScheduled | 177-14-0148 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. I could not do the inspection due to a failed discharge pump. Pump tank was close to high level. Replaced failed pump. Distribution box had roots growing into it. Removed what I could by hand and added root-x. Homeowner will call back to schedule the full inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
08/11/2023 | Alternative | RoutineScheduled | 154-08-0385 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Effluent Screens","Auxiliary Filter","Dispersal System Operation"] | YES | Musty | Clear | [14 empty] | Inspected | Sludge/Scum Accumulation - Septic 2", ATU 12", Pump Station 2" Aerator 2.5A Drip System Flushed - Air relief in headwork removed and clean (trash buildup not allowing to close) | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/11/2023 | 03:00 PM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/01/2023 | Alternative | RoutineScheduled | 171-15-0211 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Determined the pump timer was not operating properly, ordered a replacement since all the float were working properly and seems to work in avoride but not on timing feature. Tested float switches and alarm and pump are all operational. Pump counter 27175 vs 26795 = 380 cycles. Pump run time 327.53 vs 315.57 hr equals 11.96 hours - 115v 1HP zoller pump. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/30/2023 | 09:30 AM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Filter element for canister filter replaced and air pre-filter cleaned as preventative maintenance. Local isolation switch box cover for blower is damaged, not affecting operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
03/16/2023 | Alternative | Reportable Incident | 103-STS-94609 | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Advanced Septic |  | Pump | Gravity | Pad | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Install - Repair - VDH Permit 151-22-0148 - Pumped existing septic tank and pump tank empty - found to exceed 60" in burial depth - unable to replumb tanks! New AquaSafe AS600 ATU, has a maximum burial depth of 36". Installed new GeoMat sand pad with laterals in area indicated on permit. Pending design amendments from AOSE & PE. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/20/2023 | 07:00 AM
08/05/2023 | Alternative | RoutineScheduled | 2073-05-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Disinfection","Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | Musty | Clear | 6.800000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Loudoun Environmental Treatment | 1942001460 | Raymond | Kirkpatrick | 2.000000 |  |  |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | Dec 30 1899 7:45PM
11/20/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.410000 |  |  | 0.510000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 02:30 PM
09/08/2023 | Alternative | RoutineScheduled | 150-07-030 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 2.000000 | 2500 | septic tank | Advantex AX 20 | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | Advantex annual maintenance performed, cleaned recirc pump, effluent filter, sheets, flushed manifold, cleaned RSV, ST- 1" soft FOG, 3" sludge, dischardge pump, alarms all operating properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 09:00 AM
01/09/2023 |  | RoutineScheduled | SWP-02-725 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
12/01/2023 | Alternative | RoutineScheduled |  | Page | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.600000 |  |  | 0.720000 |  | 12/01/2023 |  | 13.000000 |  |  | 18.600000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/28/2023 | 01:00 PM
01/30/2023 |  | RoutineScheduled |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
03/10/2023 |  |  | 087-STS-6264 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EZ Treat | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 12:00 AM
08/22/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | LP |  |  | Pressure |  | Not Applicable |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 12:00 AM
12/22/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-70836 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Alarm call by Owner ? We removed sludge that was stuck in the zone return, allowing water to return to the pump tank. Inspection - The pump is leaking, and ground water is infiltrating the tank. In June of 2017 the Alternative Onsite Soil Evaluator who designed the system recommended tank replacement if the tanks ever need to be resealed due to unusual PH levels in the soil which degrade concrete. We recommend contacting M&M Soil Consultants for assistance with a repair permit to replace the existing concrete tanks with Orenco fiberglass tanks. This work should be completed by a licensed installer. 2/21/24: Per Email from Ed Scott to MWebb: "We referred them to M & Soil Consultants for a repair permit to install new tanks. M & M looked at this system in 2017 and stated at that time that tanks should be replaced if they ever stated leaking. Effluent had an unusual pH that was likely degrading the concrete according to notes at that time." | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/01/2024 | 07:56 AM
07/18/2023 | Alternative | RoutineScheduled | 150-07-0216 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2500 gallons | septic tank | Advantex AX20 | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Dispersal System Operation","Recirculation Pump","Control Operation","Attached Growth Medium","Auxiliary Filter"] | YES | Musty | Cloudy | [14 empty] | Pumped Out | Advantex maintenance performed. Cleaned RSV, cleaned sheets, flushed manifolds, cleaned effluent basket, cleaned pump screen, pumped Advantex septic tank due to solids accumulation. Pumps, floats, alarm, controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 10:35 PM
12/15/2023 | Alternative | Pump-Out Only | 15-142-0139 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Supervised pump and refill Replaced all 6 floats in system Wanted media sheets | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 10:28AM
08/15/2023 | Alternative | Routine/Scheduled | 2015-143-0105 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Multiflo FTB |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | 02:30 PM
04/25/2023 |  | RoutineScheduled |  | Augusta | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | 3 caps in field needs replaced and reinspected once completed. If you would like us to come and repair let us know Thanks | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/22/2023 | 11:15 AM
03/27/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | On site to correct single point aeration. Tank pumped by Powell's Plumbing. Tank washed down and all sludge and debris removed. Found one diffuser separated and one diffuser split. Old manifold and ballast blocks removed. New manifold installed on pvc stands, leveled and secured. Check valve installed at manifold airline connection to prevent backflow into the blower and blower housing during a high level event. Flush valve added to manifold for future maintenance. Tank refilled with enough fresh water to put system into operation and verify excellent aeration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
03/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] |  | NO | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | Dec 30 1899 11:23AM
08/22/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
09/01/2023 | Alternative | RoutineScheduled | 171-09-0307 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | [16 empty] | Inspected | Sludge level- minimal scum- 4-5" sludge in Septic tank - Pump is fully operational- Peat had ponding in all 4 quadrants, the peat drians slowly when turned. Owner is planning to replace. Pump run time 28:13:09 vs 15:37:47 last yearr or 12hr 30min Pump ran last year. Doses 1101 vs 603 cycles last year - 498 cycles this past year. Pump, float swithes and alarm all respond correctly. cleaned effluent filter and tipping tray. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/30/2023 | 09:30 AM
02/27/2023 | Alternative | RoutineScheduled | 154-03-0287 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | YES | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Septic Tank, the Aerobic Treatment Unit & the Pump Tank due to sludge accumulation in the tanks. As noted previously, the risers on the Pump Tank appear to be leaking at their base. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
06/23/2023 | Alternative | RoutineScheduled Component Maintenance | 033-06-0597-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:26 AM
11/02/2023 | Alternative | RoutineScheduled | 115-04-0118 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | [15 empty] | Inspected | Sludge level- minimal Scum layer & 8" Sludge in Septic tank. Effluent screen was cleaned. Peat Moss shows its age, is worn and hard packed, No ponding observed, no roots observed, turned and broke it up in all 4 quadrants. An old crack was photographed in the tank it is above the peat moss and showed no sign of leaking in or out. The new Tipping tray is working and was cleaned and removed and replaced. The D box was not located & Drainfield appeared unremarkable. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
03/07/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
09/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 8"scum/ Microfast-13"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower is working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-632 ETM-31h 10m/ Pump2-673 ETM-33h 15m/ Peak-10/ High-10/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend replacing one of the lids as it was slightly damaged by mower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/07/2023 | Alternative | Routine/Scheduled | 2008-143-0112 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Water level normal. Inlet tee appears to be. Outlet tee appears to be. Not due for pump out. Riser lid is damaged Recirculation Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Not due for pump out RSV (Recirculating Splitter Valve) Condition of above Component Notes for above Component Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly Media Sheets Condition of above Component Notes for above Component Cleaned media sheets. Flushed and cleaned laterals. Flushed media modules. Checked and confirmed spray height Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:01 PM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/04/2023 |  | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | Biomicrobics MicroFAST |  | Pump | Gravity | Pad | Not Applicable | 750.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level Secondary septic tank - normal level - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump tAnk - float sensors, pump and controls operating. Dbox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | 09:30 AM
03/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Great Falls Septic | 2705051738 | Joshua | Hott | 1.000000 | 1875 | Septic | Micro Fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [18 empty] | Pods are holding water and the drain field is saturated. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Pad | UV |  | ["Effluent Screens" ,"Disinfection"] | ["Effluent Screens"] | YES | Musty | Clear | 7.100000 | 19.100000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/16/2023 | Dec 30 1899 12:58PM
06/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-8"sludge 6"scum/ Microfast-6"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-415 ETM-23h 18m/ Pump2-399 ETM-22h 21m/ Peak-2/ High-4/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/03/2023 |  | RoutineScheduled | 179-12-0334-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend pumping the pump tank & cleaning it after removing the contents of the tank. We also recommend replacing one air release valve housing & lid at the same time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
06/16/2023 | Alternative | Reportable Incident | 159-11-011 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Follow-up to pumpout - Trash Tank - normal level - partially pumped - requires full pumpout and removal of sludge. Aeration Tank - NO MIXING PRESENT - Compressor Failed - requires full replacement, cannot be rebuilt. UltraViolet Disinfection - NOT OPERATING ... appears that entire unit requires replacing. Pump Tank - float sensors, pump functioning - control panel has faulty relay. Drip Field - headworks serviced - found several emitters failed and a broken drip run - repaired onsite. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/22/2023 | 09:00 AM
02/08/2023 |  | RoutineScheduled | SWP-02-51 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 1-5 | 0-1 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 11.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | 04:00 PM
03/20/2023 |  | RoutineScheduled | 10-125-001 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/20/2023 | 12:00 AM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Peat fiber needs to be replaced badly broken down and pod 4 full of effluent | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
01/19/2023 | Alternative | Routine/Scheduled | 166-10-091 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | 07:19 PM
04/17/2023 |  | RoutineScheduled | 179-STS-88697 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Disinfection"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Disinfection"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Uv bulb replaced. Sheetz very dirty probably due to grease building up in septict tank. Cleaned sheets, recirc pump intake and spinners to help treatment. System has a lot of regrowth and slime everywhere as if they were using liquid softeners. Spoke to customer about system conditions if they don't stop using those products system will have to be pumped next year. Uv sleeve will have to be replaced next year at time on inspection due to steins not coming off when cleaning it. RECIRC: HL 5,LL 9, OVERRIDE 178 DISCHARGE: HL 4, LL 14, OVERRIDE 25. "R" counts back to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
08/28/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - recommend replacing riser access. Processing tank - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes and spray grid serviced. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | Dec 30 1899 8:15AM
07/19/2023 | Alternative | Routine/Scheduled | C-175-17-0083 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 1:25PM
07/21/2023 | Alternative | RoutineScheduled | 18-120-0113A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2250 | 1250 | 1000 | Pump | Gravity | Discharge | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | 12:00 AM
08/11/2023 | Alternative | RoutineScheduled | 109-16-0206 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out | The MicroFast tank was pumped and cleaned. The blower and spin filters were both cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 02:15 PM
02/14/2023 |  |  | 06-142-0500 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/24/2023 | 12:00 AM
11/10/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [16 empty] | Pumped Out | Replaced pump and float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/10/2023 | Dec 30 1899 9:30AM
07/20/2023 | Alternative | Routine/Scheduled | 093-13-0156 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | Dec 30 1899 9:00AM
06/27/2023 | Alternative | Routine/Scheduled | 149-STS-10668 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | Dec 30 1899 9:00AM
07/26/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-30510 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin |  |  |  |  | Pump | Gravity | Discharge | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | Pungent | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
03/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity |  | Not Applicable | 750.000000 | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NO | [16 empty] | Pumped Out | replace 2 pumps/ 3 check valves @ 2 floats | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | Dec 30 1899 10:35AM
05/15/2023 |  | Routine/Scheduled | 550-STS-6424 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Gravity |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | Jan 1 1900 9:20AM
10/31/2023 | Alternative | Reportable Incident | 151-08-0107 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | -Installation of a high-head Turbine Pump includes: - Removal & disposal of spent Pump - Manufacturer Warranty -Installation of a high-head Turbine Pump includes: - Removal & disposal of spent Pump - Manufacturer Warranty -Installation of a new specialty Control Panel attached to a PVC Board on a Post includes a 3 year Warranty | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 09:21 AM
08/01/2023 | Alternative | RoutineScheduled | VAG408469 | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 8.110000 |  |  |  |  | 08/01/2023 |  | 2.000000 |  |  | 12.400000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 02:30 PM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | Dec 30 1899 6:25AM
01/04/2023 |  | Routine/Scheduled | 228-16-0058 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | Jan 1 1900 2:04PM
08/21/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. Spot checked drip rate on zone 3 using drip pump #2. Rate was very high and pressure low, which suggested that there was a leak somewhere. Tall grass in dripfield made seeing any effluent to surface (usually a spot the size of a baseball) impossible. Called the airport and asked them to do away with baling the grass and keep it cut on a regular basis. ETM in recirc panel is locked up, needs replaced. Cleaned air filter and spin filter. High level count at 52 in drip control panel, low level count at 487. In the past 20 days, system has pumped an average of 2,365 gals/day at 442 gals/dose (avg.) for a total of 47,300 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 177-19-0103-SWP | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Pipe between septic and pump tank settled bad. 3 broken air release valves, temporarily repair zone #1 and 2, left number 3 turned off. 6 broken valve covers. Customer ask for a proposal ASAP. Will send proposal | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/04/2023 | 06:14 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 06:25 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
03/21/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping and fungus killer. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | Jan 1 1900 7:20PM
08/29/2023 | Alternative | RoutineScheduled Component Maintenance | 175-13-0246R | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Gravity | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Auxiliary Filter"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Sand raked while on site. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 09/15/2023 | 02:41 PM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as a matter of preventative maintenance. Observed whine and slight bearing noise from blower. "Power On" light (green) was burnt out, assembly replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
05/18/2023 |  | Routine/Scheduled | 02-120-0226A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 2.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/18/2023 | Jan 1 1900 4:42PM
08/28/2023 | Alternative | Routine/Scheduled |  | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - Media drapes and spray grid serviced - media drapes are extremely dated, stretched and should be replaced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/31/2023 | Dec 30 1899 7:45AM
07/03/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-243 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Disinfection"] | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Disinfection"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection and maintenance completed including replacement of uv lamp. Red led and silence function are slow to function on Biomicrobics panel for blower and uv lamp. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 04:50 AM
04/25/2023 |  | Routine/Scheduled | 234-17-361 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 11:00AM
06/22/2023 | Alternative |  | 085-STS-34114 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
09/25/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 2:30PM
08/20/2023 | Alternative | Routine/Scheduled | 041-STS-261418 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/20/2023 | Dec 30 1899 11:30AM
01/26/2023 | Alternative |  | 101-16-0307 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Zachary | Rubenoff | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/16/2023 | Alternative | RoutineScheduled | 085-STS-32447 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
08/22/2023 | Alternative | RoutineScheduled | 06-100-0776 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 4-5" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD PEAT REPLACED RECENTLY AND IN GOOD CONDITION | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/01/2023 | 11:55 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001763 | Jessica | Young |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/18/2023 | 01:19 PM
06/05/2023 | Alternative | Reportable Incident | 147-17-0044 | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Norweco Singulair ATU |  | Pump | Pressure | Mound | Not Applicable | 600.000000 | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Alarm Event - System alarming high level. Found cleanout to kennel broken - allowing sewage to ground surface. Found one aspirator failed found septic tank effluent screen clogged - serviced. System due for full service - Aspirator ordered. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/08/2023 | Dec 30 1899 7:30AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/14/2023 | Alternative |  | 159-03-138 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | [] | ["Auxiliary Filter","Other"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled | 02-163-0320 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex AX20 |  | Pump | Gravity | Trenches |  |  | [] | ["Control Operation","Attached Growth Medium","Distribution Pump Operation","Auxiliary Filter","Level Sensor Operation","Recirculation Pump"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
10/19/2023 | Alternative | Routine/Scheduled | 13-120-0493A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Norweco Singulair ATU |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/19/2023 | Dec 30 1899 5:22PM
02/28/2023 | Alternative | Reportable Incident | 157-18-0129 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a red light - installed an aerator rebuild kit. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1.75 minutes every 1.75 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/28/2023 | 05:30 PM
08/07/2023 | Alternative | RoutineScheduled | 182-08-0327 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | laterals cleaned. Septic pumped 8/16/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 12:00 AM
10/07/2023 | Alternative | RoutineScheduled | 019-STS-26251 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in first section of septic tank. 6" of accumulated solids in second section of septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. 0" of solids in recirculation portion of treatment unit. 0" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 07:03 PM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance | 177-17-0229-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The right side of the mound should be mowed & maintained in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
06/01/2023 |  | RoutineScheduled | 145-STS-259576 | Powhatan | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Chesterfield | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1060 | Purasys PS1-6 |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | None | Clear | [15 empty] | The drain field is surfacing on the downslope side. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/01/2023 | 12:00 AM
07/27/2023 | Alternative | Follow-Up Component Maintenance | 175-18-0222 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
04/03/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recirc was clogged | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
02/28/2023 | Alternative |  | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
01/31/2023 |  | Routine/Scheduled | 175-STS-14861 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/31/2023 |  | 2.000000 |  | 44.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 8:33AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/28/2023 | Alternative | RoutineScheduled | 108-17-0013 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | SEPTIC TANK ONLY | ADVANTEXAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | THE SYSTEM DID NEED A ROUTINE PUMPING BUT THE LAND OWNER REQUESTED IT TO BE PUMPED AT A LATER DATE. THE EFFLUENT FILTER WAS PULLED AND CLEANED. THE TEXTILE SHEETS WERE SPRAYED OFF. THE TWO PUMPS WERE PULLED AND SPRAYED OFF. THE CONTROLS WERE OPERATING AS DESIGNED. THERE WERE NO VISIBLE LEAKS IN THE LEECH FIELD. THE BOD AND TSS WERE WELL WITHIN PERMITTED LIMITS. THE LIDS WERE SECURED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 12:20 PM
08/19/2023 | Alternative | RoutineScheduled | 2069-02-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | Musty | Clear | 7.400000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/14/2023 | Alternative | Routine/Scheduled | 10-120-0039R | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/14/2023 | Dec 30 1899 9:08AM
06/26/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Annual, replaced one float and repaired drainfield leak top front corner from tractor damage | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 12:00 AM
05/10/2023 |  | RoutineScheduled | 2005-143-0226 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
02/28/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Distribution Pump Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
02/07/2023 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Best 1 | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 02/07/2023 |  | 53.000000 | [5 empty] | Will be sent separately | Inspected | Replaced compressor Repaired air vac and valve box | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
03/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/20/2023 | Alternative | RoutineScheduled | 115-05-0406 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic Tank | Microfast | Pump | Pressure | Drip | Not Applicable | 350.000000 | ["Effluent Screens"] | ["Effluent Screens","SludgeScum Accumulation","Dispersal System Operation","BlowerCompressorAerator Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | 11:00 AM
12/11/2023 | Alternative | Reportable Incident | 181-05-0374 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 4.000000 | 6000 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip |  |  | ["SludgeScum Accumulation","Auxiliary Filter","Effluent Screens","Control Operation"] | ["Control Operation","Auxiliary Filter","Effluent Screens","SludgeScum Accumulation"] | YES | [16 empty] | Inspected | When we got to job site, power was off and system backed up. Pump tank and treatment unit was pumped. Filters checked and cleaned. No apparent leaks in system or drain field area. Pumps were functioning properly after maintenance performed. Lids were properly secured | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 05:05 PM
05/25/2023 | Alternative |  |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  | Gravity | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Pumpout needed for Septic/FAST | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 12:00 AM
04/25/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge levels--1-2"scum and 8-10" sludge in Septic tank. 5" Sludge in Recirczone of tank, Clear Effluent on top. Discharge tank 6" sludge. Alarm is good, Both pumps opperational, all 6 float switches test good. cleaned biofilter, brushed manifold, Ran system in test mode, Cleaned RSV, and Flushed system. Cleaned drip filter 15 psi gping to drainfield, Reci pump run time 492.3 hours 95,529 cycles and discharge pump 159.6hours and 5181 cycles -Last Alarm 8-2021. Alerts- Jan 16-18th 2023 high recirc cycles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 05:30 PM
12/20/2023 | Alternative | RoutineScheduled | 02-197-188 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/20/2023 | 12:00 AM
08/31/2023 | Alternative | Reportable Incident Component Maintenance | SD-03-308 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Control panel making loud noise when pump runs. Replaced locked up cycle counter and the corroded contactor. Recommended again that owners get a new control panel and have it mounted on the backside of the house. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
08/24/2023 | Alternative | Routine/Scheduled | 127-STS-34908 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/24/2023 | Dec 30 1899 9:30AM
01/17/2023 |  | RoutineScheduled | 00-192-350 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/17/2023 | 12:00 AM
07/24/2023 | Alternative | Initial Visit Component Maintenance | 179-STS-92244 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Start up Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
08/16/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing tnak - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. PUmp Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | Dec 30 1899 8:00AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend flushing and balancing the lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance | SD-07-039 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/14/2023 |  | RoutineScheduled | 101-13-0171 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Gravity | Gravity | Trenches | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 01:00 PM
11/29/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.620000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 01:40 PM
04/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/17/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3092 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | Jan 1 1900 11:00AM
10/31/2023 | Alternative | Reportable Incident | 147-08-0051 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | -2 Bottles RootX -Install 18x36 Dbox lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 9:31AM
07/12/2023 | Alternative | RoutineScheduled Component Maintenance | 177-08-0023-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is crystal clear. High level cnts-30, ETM-0m. Peak cnts- 915, ETM-81h34m. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
11/07/2023 | Alternative | Routine/Scheduled | 041-STS-257801 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/07/2023 | Dec 30 1899 1:23PM
12/08/2023 | Alternative | Routine/Scheduled | 02-172-0622A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal level 6 in of sludge 1 in of solids Tee is not level No riser or filter on outlet Trash Tank Condition of above Component Notes for above Component High level upon arrival due to roots blocking rsv preventing water flow 3 in of sludge less than 1 In of solids Inlet tee is flush against the bottom of the riser Roots intruding through seal of riser Recirculation Tank Condition of above Component Notes for above Component High level upon arrival due to roots blocking rsv preventing water from flowing 4 in of suspended solids Tested floats and pump all working as should All plumbing intact and pump moving water properly however pump has met its life expectancy Brushed and flushed bio tube filter Roots intruding through seal of riser RSV (Recirculating Splitter Valve) Condition of above Component Notes for above Component Taken apart cleaned check ball and flushed out Media Sheets Condition of above Component Notes for above Component Brushed and flushed laterals Sprayed media sheets Completely flushed module Media sheets are bridging and holding water Heavy staining Control Panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Recirc pump pulled 11.6 amps All components working as should However panel is aged Distribution Box Condition of above Component Notes for above Component Unable to locate Drain Field Condition of above Component Notes for above Component No signs of surfacing Repairs on 12/13/2023: -Installation of 6"-12" Riser on the Septic Tank -Installation of 6" Effluent Filter in Septic Tank -Resealing of an existing Orenco Riser reqires excavation around the outside of each Riser includes use of specialized caulking inside and outside the Riser -Installation of a high-head Turbine Pump includes: - Removal & disposal of spent Pump - Manufacturer Warranty -Resealing of an existing Orenco Riser reqires excavation around the outside of each Riser includes use of specialized caulking inside and outside the Riser -Installation of new Advantex Treatment Unit Lid Support Struts -Advantex Engineered Textile Media Filter Replacement in Treatment unit: Removal & disposal of existing Engineered Textile Media Filters Installation of new Engineered Textile Media Filters Includes installation of new Bars & Hangers -Installation of a new specialty Control Panel attached to a PVC Board on a Post includes a 3 year Warranty | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/13/2023 | Dec 30 1899 12:33PM
10/05/2023 | Alternative | Routine/Scheduled | 041-STS-257684 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/05/2023 | Dec 30 1899 4:02PM
03/29/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced riser & lid on septic tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/15/2023 | Jan 1 1900 7:20PM
05/18/2023 | Alternative | Follow-Up | 550-STS-6650 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Hooked up the pressure switch on the aerator, the UV alarm, and the UV power. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/18/2023 | Dec 30 1899 12:00PM
07/25/2023 | Alternative |  | SP-03-231 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-1 | 0-0 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 2.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 10:00 AM
04/14/2023 |  | Routine/Scheduled | 133 10 0136 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 10:00 AM
08/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/09/2023 |  | Reportable Incident | 182-04-0396 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | repaired Pump wire | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/08/2023 | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance | 182-06-0331 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | NA | [7 empty] | 06/06/2023 |  | 286.000000 | [5 empty] | Will be sent separately | Inspected | Repalaced effluent pump,blower,blower panel and override float | This AOSS should now return to normal function after having provided the above state routine maintenance | 07/11/2023 | 11:17 AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
10/31/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 12:00 AM
04/07/2023 | Alternative | RoutineScheduled | 88-160-0363 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2500 | LPD |  | Pump | Pressure | Trenches | Not Applicable |  | ["Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [] | NA | Septic | Dark Brown | [14 empty] | Inspected | - recommend septic tank and pump chamber be pumped/cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/13/2023 | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/09/2023 | Alternative | Follow-Up | 061-16-398 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired fittings in hydraulic unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
07/31/2023 | Alternative | Reportable Incident | 157-14-0133 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The aerator needs to be raised - the hose was pulled off of the pressure switch assembly. The timer is set to 2 minutes every 2 hours. Did not take 5 year sample due to the aerator not working properly on arrival. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 01:00 PM
09/06/2023 | Alternative | Routine/Scheduled | 147-18-0012 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Processing Tank - recirc - media drapes, recirc pump & spray grid serviced. Processing Tank - discharge - float sensors, pump and controls operating. Dbox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 12:45PM
11/03/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 12:00 AM
07/28/2023 | Alternative | RoutineScheduled | 10-173-103 | Prince Edward | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Eco Flo |  | Pump | Pressure | Mound | Not Applicable | 350.000000 | ["Effluent Screens","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Cloudy | [15 empty] | The pump is not working and needs to be replaced, homeowner does not have money to do the job at this time. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/21/2023 | Dec 30 1899 1:00PM
01/17/2023 | Alternative | RoutineScheduled | 166-15-100 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1500 | Aquasafe | Aquasafe | Pump | Gravity | Pad | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | 12:00 AM
01/30/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Control panel inside client was not home. Components and system levels are operational and normal. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
08/07/2023 | Alternative | RoutineScheduled | 18-192-140 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ATL |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 12:00 AM
12/13/2023 | Alternative | Routine/Scheduled | 127-STS-34824 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 10:30AM
08/29/2023 | Alternative |  | 065-STS-30755 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Chris | Fairchild | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping ATU | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The header line appears to be nitrified and probed out slightly wet. Recommend uncovering distribution box and checking header line connections. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/13/2023 |  |  |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/05/2023 |  |  | 179-17-0372-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
03/16/2023 |  | RoutineScheduled | 07-192-233 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/16/2023 | 12:00 AM
03/31/2023 |  | RoutineScheduled | VAG401044 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers |  |  | Multi-Flo |  | Gravity | Gravity | Discharge | Chlorination |  | [] | ["Disinfection"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | 08:30 AM
06/01/2023 |  |  |  | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
03/14/2023 |  | RoutineScheduled | 199-06-0011 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1000.000000 |  | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 12:00 AM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-400 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | System alarmed last week several times. Recirc tank down to near low level, discharge tank barely out of high level. Connected to Vericomm panel and checked alarm log. Discharge tank had high level alarm first, then the recirc tank a day later. System was also alarming for a clogged filter. Cleaned biotube filter, RSV and recirc pump. Evidence of infiltration at pump tank inlet and outlet pipe penetrations, and at the pump tank inspection port (4" clean-out adapter and cap missing). One strut is broken and one hinge has broken loose for the Advantex pod lid. Owner to make arrangements to get pump tank cleaned out and replace the missing inspection port cap. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
03/21/2023 | Alternative | Reportable Incident | 159-18-0028 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed pump, failed timer relay and failed compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | K-Rain is cracked and spraying effluent when running needs to be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
08/17/2023 | Alternative | RoutineScheduled | 107-04-0052 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Gravity |  | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Septic pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/17/2023 | 12:00 AM
02/15/2023 |  | RoutineScheduled | SP-04-202 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Inlet pipe in sample box barely in box, will check next year. Pump only doing 20 gallons per minute will be upgraded when it goes bad. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
12/20/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 09:30 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/06/2023 | Alternative | Follow-Up | 121-STS-11979 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [18 empty] | - Pumping & Cleaning Alternative Septic Tank (1000 gallons) so that work could be completed -Root Removal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/14/2023 | 12:00 AM
05/12/2023 | Alternative | Initial Visit | 124-STS-2379 | Charles City | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 0.000000 | 0 | Multiflo FTB |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Real Estate Inspection. AOSS Discharge - Initial Visit. No Septic tank preceeding MultiFlo treatment unit! Multi flow pumped empty - socks serviced - aerator serviced - multiflo refilled for re-start. Chlorinator serviced - property owner has tablets! De-Chlorinator serviced - property owner has tablets! No laboratory samples taken - unknown service provider - unknown when last service / laboratory sampling has occurred. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/25/2023 | Dec 30 1899 1:15PM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | Best 1 | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was turned off and the blower connection to the air line had separated. It was connected and should return to proper function | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/23/2023 | Alternative | Routine/Scheduled | 151-18-029 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Aqua Klear |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | 05:18 PM
05/12/2023 |  | Routine/Scheduled | 234-18-191 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | Jan 1 1900 7:00AM
03/14/2023 | Alternative | Reportable Incident | 073-STS-101889 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Repair - VDH Permit 136-22-0349 - GMP2018-02 Pumped existing septic tank empty, crushed and abandoned. Installed new 1000g concrete mid-seam septic tank with effluent screen and access riser to grade. Installed new 4" PVC conveyance line. Installed new 8 port concrete distribution box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 09:30 AM
10/11/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped out the Clearstream tank and septic tank. Need to go back to hook pressure switch back up once there is enough water. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/11/2023 | Dec 30 1899 2:00PM
06/27/2023 | Alternative | Routine/Scheduled | 145-STS-259769 | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Needs to be pumped | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/27/2023 | Dec 30 1899 2:34PM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Replaced UV bulb & chord while on site for inspection. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | Dec 30 1899 12:46PM
03/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/21/2023 | 11:27 AM
03/14/2023 |  | RoutineScheduled | 179-STS-89706 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
06/29/2023 | Alternative | Pump-Out Only | 166-16-0078 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumpout of trash tank and aeration tank as recommended during last service visit. Processing tank refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 06:45 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0129-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend scraping the Advantex sheets and then pumping the Advantex RT tank afterwards. We also recommend installing a vent on the septic tank to help with slime build-up in the system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
03/15/2023 | Alternative | RoutineScheduled | 159-11-157 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
11/03/2023 | Alternative | Routine/Scheduled | 087-STS-6566 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | 10:30 AM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 107-05-0423 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Blower was off when arrived turned back on | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
01/11/2023 |  | RoutineScheduled | 033-STS-87958 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 01/11/2023 | [10 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/22/2023 | Alternative | Routine/Scheduled | 228-06-0107 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/22/2023 | Dec 30 1899 8:15AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed. Tanks appeared the same as in past years. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/07/2023 |  |  | 033-06-0191-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
09/01/2023 | Alternative | Routine/Scheduled | 13-120-0041A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/01/2023 | Dec 30 1899 2:29PM
12/28/2023 | Alternative |  | 185-STS-17513 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/28/2023 |  | 5.900000 |  |  | 1.500000 |  |  | Will be sent separately |  | BOD: 5.90 TSS: 1.50 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/28/2023 | 12:00 AM
02/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/13/2023 |  | RoutineScheduled | 101-06-0296 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Ecoflow |  | Gravity | Pressure | Drip | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | 12:00 AM
07/17/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-2722 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/17/2023 | Dec 30 1899 1:35PM
04/07/2023 |  | Pump-Out Only | 124-STS-2379 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Virginia Beach | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | [7 empty] | [] | [] |  | Septic | [15 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/04/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | Dec 30 1899 1:40PM
10/02/2023 | Alternative | Reportable Incident Component Maintenance | 175-17-0429 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | UV |  | ["Control Operation" ,"Disinfection" ,"Level Sensor Operation"] | ["Control Operation" ,"Disinfection" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | 9/29 Intermittent high level alarm on inside alarm panel only, would not silence when alarming. This panel set up to alarm for failed uv lamp and discharge tank high level. Outside alarm float set to activate before inside alarm, never did and float tested good. UV indicator light on bright and green, not flickering. Replaced float for inside alarm. All working correctly. 10/2 Inside alarm on again. This time green light was off and uv lamp was completely burnt out, replaced it. Inside alarm panel now working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
07/21/2023 | Alternative | Routine/Scheduled | 093-08-0035 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump and effluent screen serviced. TReatment Module - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | Dec 30 1899 9:45AM
02/20/2023 | Alternative |  | SD-07-289 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.700000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/22/2023 | 12:00 AM
07/21/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable | 750.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 9:25AM
06/01/2023 | Alternative | Routine/Scheduled | 151-09-0230 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | Biomicrobics MicroFAST |  | Pump | Pressure | Trenches | Not Applicable | 750.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/07/2023 | 11:15 AM
05/01/2023 | Alternative |  | 154-16-0064 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Jason & Stacey | Haddock | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/06/2023 | Alternative | Routine/Scheduled | 2004-143-0160 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Recirculation: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV: Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge pump has exceeded life expectancy. Discharge pump plumbing has exceeded life expectancy. Discharge floats have exceeded life expectancy. Noted root infiltration around base of discharge riser -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Media has exceeded life expectancy. Media lid safety support struts have failed. Media lid hinges are failing -Control Panel: Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:33 PM
12/20/2023 | Alternative | RoutineScheduled | 143-STS-16513 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Gravity | Gravity | Trenches |  |  | ["Control Operation"] | ["Control Operation"] | NA | [17 empty] | Annual inspection. New homeowner. Home is still under construction. The treatment unit is within the serial number range for the service memorandum by the manufacturer. The position of the recirculation pump floats switches have been adjusted. The recirculation pump timers were also adjusted per the memorandum. The septic tank is not quite full yet. The treatment unit has adequate water to continue to run. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2024 | 07:03 PM
05/05/2023 | Alternative | Routine/Scheduled | 157-10-0131 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effleunt screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact - re-balanced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 08:30 AM
02/10/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 7.390000 | 7.910000 |  |  |  | 02/10/2023 |  | 5.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 03:00 PM
02/09/2023 |  | RoutineScheduled | 179-06-0351 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend replacing the pressure switch and alarm light bulb in the blower control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
01/27/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches |  | 300.000000 | ["Dispersal System Operation","Effluent Screens"] | Dispersal System Operation | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/11/2023 | 12:17 PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/22/2023 | Alternative | Routine/Scheduled | 800-09-0208 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - last documented service January 2020! Primary septic tank -= normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 4 modules - peatmoss in fair condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | Dec 30 1899 12:00PM
03/27/2023 |  | Routine/Scheduled | 234-14-52 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | Jan 1 1900 3:00PM
07/10/2023 | Alternative | Routine/Scheduled | 800-03-0097 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 12:18PM
04/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | Dec 30 1899 5:20PM
04/20/2023 |  | Reportable Incident |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Biofilter change out. Pumped septic tank empty for storage and drying. Removed spent biofilter and replaced with new. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 08:30 AM
12/26/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | LP |  |  | Pressure | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | 179-19-0034-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
01/26/2023 |  | Routine/Scheduled | 043-08-0083 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | EZ Treat Sandfilter |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | 10:26 AM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-345 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Dark Brown | [13 empty] | Will be sent separately | Inspected | Routine inspection. Media was ponding, augered and started to drain not much fiver left it will need replacement next year. Customer took all the small trees down that were in the middle of the drain field area but stumps still there starting to grow again. Marked 4 big trees that are less than 10' from top trench, recommend to take them down before they cause root problems to drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/25/2023 | Alternative | RoutineScheduled | 06-137-0237 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/12/2023 |  | RoutineScheduled | 195-Discharge-19263 North Fork River | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/12/2023 | 12:00 AM
03/28/2023 |  | RoutineScheduled | 108-17-0018 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2500 | Septic Tank Only | MicroFast | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [7 empty] | 03/28/2023 | Sample Chamber | 17.600000 |  |  | 4.000000 |  |  | Attached to this report |  | The system did not need pumping. The blower filter was cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The BOD and TSS were well within permitted limits. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 08:20 PM
08/17/2023 | Alternative | RoutineScheduled |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Pump | Pressure | Pad | Not Applicable | 1200.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled | 181-16-0108 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The recirculating pump was pulled and sprayed off. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 09:50 PM
04/18/2023 |  | Reportable Incident | 550-STS-6846 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream (it was stopped up - causing alarm) and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1 minute every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | Jan 1 1900 9:00AM
05/10/2023 |  | Routine/Scheduled | 2004-143-0226 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Biofilter - peat moss in poor condition - recommend replacing - roots present. Pump Tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 08:00 AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | XWP-98-643 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Level Sensor Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. outstanding proposal for adding access point on septic tank inlet. 1 pod has a ant's nest inside, recommend to get rid of them (pod farther away from house). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
08/31/2023 | Alternative | RoutineScheduled | 181-02-0495 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20 | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter and spin filter were both pulled and cleaned. The recirculating and discharge pumps were both pulled and sprayed off. The textile sheets were sprayed off and cleaned. The controls were operating as designed. There was effluent returning to the pump tank so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 03:30 PM
03/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/20/2023 | Alternative |  | 027-STS-17468 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/20/2023 |  | 2.980000 |  |  | 1.300000 |  |  | Will be sent separately |  | BOD: 2.98 TSS: 1.30 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled | RS-102-17-0026 | Alleghany | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2500 | Septic Tank Only | MicroFast | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Septic Tank Baffles"] | ["SludgeScum Accumulation","Septic Tank Baffles"] | NA | [7 empty] | 07/11/2023 | Pump Chamber | 7.700000 |  |  | 11.800000 |  |  | Attached to this report | Pumped Out | The scum layer was pumped off the top of the septic tank. The 1500 gal MircroFast tank was pumped and cleaned. The blower filter was cleaned. The controls were operating as designed. There were no visible leaks in the leech field. The six inch pipe in the treatment unit had come out of the unit so it was dug up and repaired. The BOD and TSS samples were within the permitted limits. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/31/2023 | Jan 1 1900 10:00PM
05/24/2023 |  | Reportable Incident | 234-16-126 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/24/2023 | Jan 1 1900 11:00AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/14/2023 |  | RoutineScheduled | 099-06-0361-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
08/10/2023 | Alternative | Routine/Scheduled | 159-07-340 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Serviced the Eco-Flo system. Peat moss is good. Pump, floats, and alarms all working. The drainfield looks good. It was raining at the time of service. The timer is 1.1 minute on and .9 hours off. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 12:00 PM
02/15/2023 |  |  | SWP-05-259 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
02/14/2023 |  | Pump-Out Only |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/17/2023 | 11:32 AM
06/02/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | Distribution Pump Operation | Distribution Pump Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 01:01 PM
11/20/2023 | Alternative | RoutineScheduled | 195-STS-26918 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/08/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
04/27/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
10/12/2023 | Alternative | RoutineScheduled | 151-09-0169 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | checked sludge, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 06/14/2023 |  | 59.000000 |  | 1600.000000 |  |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | Dec 30 1899 6:25AM
07/17/2023 | Alternative | RoutineScheduled | 107-99-0028 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Auxiliary Filter"] | ["SludgeScum Accumulation","Auxiliary Filter"] | NA | Musty | Clear | [14 empty] | Pumped Out | replaced tee with filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
01/09/2023 |  | RoutineScheduled | 153-STS-19248 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/02/2023 |  | RoutineScheduled | SWP-01-576 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Hoot | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Cloudy | [13 empty] | Will be sent separately | Inspected | Annual inspection. Backwash valves not closing correctly. Had to clean strange colored (pinkish) slime from under the diaphragms (cleaned all 5). Ran a couple of short test cycles and discovered both zone check valve flappers were stuck open. Replaced the brass check valves with plastic check valves in hopes of the plastic being more resistant to the mineral build-up. Cleaned the zone return valve twice more to remove flaky tan debris and possibly filamentous growth. The system suffered for years with improper flushing velocity. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/05/2023 | 07:56 AM
08/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance | 107-19-0090 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend replacing UV bulb. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/15/2023 |  | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 2220.000000 | [] | [] |  |  |  | 6.780000 | 5.440000 | 28.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 02:30 PM
11/02/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | Dec 30 1899 2:02PM
08/22/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0075-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We continue to recommend replacing the check valves and psi gauges on the drip dispersal system. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/01/2023 | 07:38 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 047-16-019 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Disinfection" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"Recirculation Pump" ,"BlowerCompressorAerator Operation" ,"Disinfection" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
04/18/2023 |  | Follow-Up |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | We were able to open up conveyance line so effluent could get to d-box. At this time No effluent is on the ground. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/31/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/25/2023 | 10:47 AM
01/24/2023 |  | Routine/Scheduled | C-175-17-0083 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 1:42PM
04/27/2023 | Alternative | RoutineScheduled | C04-180-0035 | Salem | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | BioMicrobics Microfast |  | Gravity | Pressure | Drip | Not Applicable | 300.000000 | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Cleaned spin filter and effluent screens, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/28/2023 | 12:00 AM
08/23/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Followed up due to compressor panel not having power and atu needing pumped. Atu has been pumped out and power was restored to blower but not to the panel which still needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 09/15/2023 | 02:41 PM
04/10/2023 |  | RoutineScheduled | 17-100-0029 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AquaSafe |  | Pump | Pressure | Mound | UV | 300.000000 | [] | [] | [18 empty] | Everything is working properly | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/11/2023 | 11:30 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/23/2023 |  | RoutineScheduled | 124-STS-2379 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Rejected | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Electric to panel was shut off at arrival. Hydraulic unit has broken piping & fittings. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/15/2023 | 07:20 PM
03/20/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
06/02/2023 |  |  | 033-16-0093-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
06/13/2023 | Alternative | RoutineScheduled | 08-100-0751 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 750 | BIOCOIR |  | Pump | Gravity | Mound | Not Applicable | 450.000000 | [] | [] | YES | [17 empty] | FIBER REPLACED. EVERYTHING WORKING AS IT SHOULD. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/05/2023 | 10:50 AM
04/12/2023 |  | RoutineScheduled | 19-142-0100 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 2.000000 | 2500 | EZ Treat |  | Gravity | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:00 AM
05/16/2023 |  | RoutineScheduled | 101-17-0119 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
02/07/2023 | Alternative | RoutineScheduled | 119-STS-93117 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | 12:00 AM
12/06/2023 | Alternative | RoutineScheduled | 16-120-0306A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Carrington Pump & Irrigation | 1942001121 | John | Carrington | 2.000000 |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
10/26/2023 | Alternative |  | 154-18-0193 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/25/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Attached Growth Medium","Other"] | YES | [17 empty] | Dug up and fixed the fall on the drain line outside of the pods Dug peat back and blew out pod drain lines. Pods are draining as they should. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/31/2023 | Dec 30 1899 4:00PM
11/16/2023 | Alternative | RoutineScheduled | 175-18-0066 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation","Level Sensor Operation"] | ["Level Sensor Operation","Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-2"sludge 0"scum/ Microfast ATU Tank-0"sludge 0"scum (Media is clogged) Pump Tank-0"sludge 0"scum/ Chemical cleaning of the Microfast media is required and pump out of the Septic-Microfast Tank/ Replaced a faulty off float/ Controls, pump, floats and alarms are now functioning properly/ Blower air filter cleaned and blower working correctly/ Counts: Pump cycles-3819/ Pump Run Time-463h 27m/ High counts-3/ No breakout or spongy areas on the drip mini mounds and dosing properly. Chemical cleaning done on 11/21/2023 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/31/2023 | Alternative |  | 08-100-0861 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
04/04/2023 |  | RoutineScheduled |  | Greene | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced peat in all modules | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
12/19/2023 | Alternative | Routine/Scheduled | 151-00-0438 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Found at normal, 12in of sludge and less than 1in of solids. Pulled and cleaned filter. Riser has signs of leaking and cant secure lid due to screw holes beginning broken Discharge/Pump Tank Condition of above Component Notes for above Component Found at normal level, tested floats and pump - all working as they should. Riser has signs of leaks where forcemain leaves the tank is not sealed. Aeration Multiflo Condition of above Component Notes for above Component Found at normal level 12 of sludge and less than 1in of solids. Sock are clogged Control Panel 1 Discharge Condition of above Component Notes for above Component 120v All audible and visual alarms are functioning properly Pump pulled 10.87amps Control Panel 2 Multiflo Condition of above Component Notes for above Component 120v All audible and visual alarms are functioning properly Aerator pulling 1.91amps Distribution Box Condition of above Component Notes for above Component Concrete distribution box at grade in good condition with 8 lines balanced and taking water Drain Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/22/2023 | 08:13 AM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | 107-08-0225 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Added riser and pumped primary tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
03/03/2023 |  |  | 18-142-0132 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 12:00 AM
01/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pods 2,3 and 5 are full of effluent . Need to investage further to see if the if the drain line from the pods has a belly or settled. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
04/13/2023 |  | RoutineScheduled | 099-06-0048-ST | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We replaced the defective timer float that was always on. We recommend treating the area around the Puraflo modules for ants. We also recommend repairing the damaged Puraflo module with a fiberglass patch repair kit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
01/24/2023 |  |  | 11-163-0086 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton |  |  | Clearstream |  | Gravity | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 12:00 AM
08/22/2023 | Alternative | Follow-Up | 085-STS-34711 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 750 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | Dec 30 1899 10:30AM
01/09/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Aqua Klear | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 01/09/2023 |  | 28.000000 | [5 empty] | Will be sent separately | Inspected | Aquasafe A5600ez Lab sample Normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/05/2023 | Alternative | RoutineScheduled | 06-184-5005 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 2 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/05/2023 | 12:00 AM
05/23/2023 |  | Initial Visit | 015-STS-334097 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST 0.5 |  | Gravity | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/02/2023 | 12:00 PM
09/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0078-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NO | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We cleaned the closed RSV valve that caused an alarm on the system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
04/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/07/2023 |  | RoutineScheduled | 02-197-188 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 4 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
03/21/2023 |  |  | 18-142-0368 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation","BlowerCompressorAerator Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
10/13/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine annual, nothing to report | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
01/06/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 2000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/04/2023 | Alternative | RoutineScheduled | 182-05-0189 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Bush should be removed around pump tank....mild root intrusion at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/04/2023 | 12:00 AM
08/29/2023 | Alternative | Reportable Incident Component Maintenance | SD-12-31 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | None | [14 empty] | Will be sent separately | Inspected | Replaced half of camlock (side with levers) that was cracked and leaking during recirc pump cycles. Drip tank high level count at 239,136 and peak level count at 54,971. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
03/21/2023 |  | RoutineScheduled | 179-17-0478-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The end of the lowest mound (closest to Hillsboro Rd) is soft and spongey. Homeowner is contacting someone to look at. Recommend addressing issue before if becomes a bigger problem. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
08/11/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 12:00 AM
12/01/2023 | Alternative | RoutineScheduled | 10-120-0036AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/12/2023 | Alternative | Routine/Scheduled | 151-08-0173 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 4.000000 | 10000 | Advanced Septic |  | Pump | Pressure | Pad |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | 05:24 PM
04/12/2023 |  | Pump-Out Only | 550-STS-6558 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  | Drip | UV |  |  |  | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/12/2023 | Jan 1 1900 8:00AM
12/12/2023 | Alternative | Follow-Up | 94-160-0551 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | [9 empty] | [] | [] | [17 empty] | Inspected | Septic System Repair - repaired force main - installed riser - pumped/cleaned 1000gal septic tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
06/21/2023 | Alternative |  | 2017-143-0065 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1000 | 750 | 250 | Pump |  | Trenches | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens","Recirculation Pump","Disinfection","BlowerCompressorAerator Operation","Attached Growth Medium","Auxiliary Filter","SludgeScum Accumulation"] | YES | Pungent | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 01:15 PM
04/16/2023 | Alternative | Routine/Scheduled | 149-STS-11281 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | Dec 30 1899 12:00PM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | SP-00-364 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation"] | ["Dispersal System Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
05/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
08/07/2023 | Alternative | Routine/Scheduled | 14-120-0394A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/07/2023 | Dec 30 1899 2:08PM
07/14/2023 | Alternative | Routine/Scheduled | 234-12-85 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | a | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | Dec 30 1899 9:45AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
02/20/2023 |  | RoutineScheduled | 177-18-0079-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Control Operation" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted previously, the timer unit that has been installed in the control panel should be removed. We also recommend that the control breaker have its own dedicated source of power. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
12/05/2023 | Alternative | Routine/Scheduled | 041-STS-257672 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Purasys |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/05/2023 | Dec 30 1899 9:42AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance | XS-98-511 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
08/18/2023 | Alternative | RoutineScheduled | 03-197-179 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 AM
07/26/2023 | Alternative |  | 06-195-272-Dis | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 |  | 3.170000 | [5 empty] | Will be sent separately |  | BOD: 3.17 TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/26/2023 | 12:00 AM
03/31/2023 |  | Routine/Scheduled | 228-15-0116 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [14 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/31/2023 | Jan 1 1900 10:10AM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0193-SWT | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Vacuumed broken pit out of d-box. Pods 4 and 5 not ponding. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/11/2023 | Alternative | Reportable Incident Component Maintenance | SD-05-457 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | On site to investigate 2 reported spongy spots on drip mound. Dug up spongy spots and ran pump in order to observe the emitters close to the wet spots. Two emitters were streaming instead of dripping. Cut out about 2.5' of tubing and spliced in a new piece of tubing with the proper tan tubing couplers (for Netafim tubing). Ran pump to verify repair. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
12/22/2023 | Alternative |  |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont |  |  | Eric | Wilkening | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0602 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Puraflo peat needs replacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
04/20/2023 | Alternative | Routine/Scheduled | 151-13-0055 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls operating. DBox - plastic - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 07:45 AM
10/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Septic Tank | Microfast Tank | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | [7 empty] | Nitrite-Nitrate 3.05 mg/L | 10/03/2023 | Sample Chamber | 98.000000 |  | 1600.000000 |  | 132.000000 |  | Attached to this report |  | Septic Tank-6"sludge 0"scum/ Microfast-20"sludge (REQUIRES PUMP OUT) EZ-Treat Tank-6" sludge 0"scum On-8m Off-26m/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ No breakout or spongy areas on the drainfield/ Counts: Pump1-38451 ETM-219h 1m/ Pump2-38391 ETM-218h 24m | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/26/2023 | Alternative | Initial Visit | 159-09-0072 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Clearstream |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - Former Churchview Client - In Alarm on Arrival. Primary septic tank - normal level - effluent screen serviced. Aeration Tank - in alarm - Compressor failed - replaced and operation restored. Pump Tank - float sensors, pump and controls operating. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/27/2023 | 06:30 AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/28/2023 | Alternative | Routine/Scheduled | 07-160-0173 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 105.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 12:00 PM
08/08/2023 | Alternative | RoutineScheduled | 169-STS-26843 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Fast |  | Pump | Pressure | Trenches | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping and drip tube break in d/f area. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
05/11/2023 |  |  | SWP-96-93 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Sand Filter | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
01/10/2023 |  | RoutineScheduled | SWP-04-273 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Dispersal System Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
07/13/2023 | Alternative | Routine/Scheduled | 119-STS-105992 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 1000.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - 8 modules - peatmoss in good condition - raked / turned - wasp / hornet nest located in three modules! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 07:00 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/31/2023 |  | RoutineScheduled | 193-STS-94956 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1000 | Bio Coir NS500 |  | Pump | Pressure | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/31/2023 | 12:00 AM
11/07/2023 | Alternative | Routine/Scheduled | 136-04-0132 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal Level Less 1" of solids 6" of sludge No signs of infiltration -Recirculation Tank: Normal Level 4" of suspended solids All floats and pump are functioning properly Pulled and cleaned biotube filter, pump, and floats No signs of infiltration -RSV (Recirculating Splitter Valve): Flushed and pulled apart housing cleaned ball and made sure it was free of debris -Discharge/Pump Tank: Normal Level Less than 1" of suspended solids -Media Sheets: Flushed and brushed laterals Cleaned media sheets Flushed media module until water ran clear -Control Panel: 120v to panel All audible and visual alarms are functioning properly however the audible alarm was unplugged Recirc pump pulled 10.82amps Discharge pump pulled 6.99amps -Distribution Box: Distribution box is plastic and is crushed with roots intrusion 2 lines taking water -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 11:32 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Media Replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
11/16/2023 | Alternative | RoutineScheduled | 136-02-0618 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex AX20 |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Recirculation Pump","Control Operation","Distribution Pump Operation","Auxiliary Filter","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 12:00 AM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | 2102-05-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Disinfection" ,"Effluent Screens"] | ["Effluent Screens" ,"Disinfection"] | YES | Musty | Clear | 7.100000 | 1.900000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 07/07/2023 | 06:25 AM
04/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/20/2023 |  | Routine/Scheduled | 02-172-0430A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/20/2023 | Jan 1 1900 3:10PM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/12/2023 | Alternative | Routine/Scheduled | 157-06-0072 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has no solids with 3" of sludge Pulled and cleaned rsv -Recirculation Tank: At normal level Has 3" of sludge Pulled and cleaned pump, floats and filter Pump and floats replaced last year -Discharge/Pump Tank: At normal level Has 2" of sludge Pump and floats functioning properly -Media Sheets: Sheets in great shape Brushed and flushed laterals Sprayed off sheets and flushed chamber -Control Panel: Panel replaced last year Panel working properly Visual and audible alarms working Recirc pulling 11.04amps Discharge pulling 9.79amps -Drain Field: Unable to locate drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 04:04 PM
06/13/2023 |  |  |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
01/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | Dec 30 1899 11:08AM
12/27/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/06/2024 | 11:10 PM
09/27/2023 | Alternative | Routine/Scheduled | 02-120-0843A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | YES | [17 empty] | The system seems to operating correctly, but the control panel display was not working correctly. As noted in last year's report the control panel needs to be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | Dec 30 1899 8:32AM
07/17/2023 | Alternative | Routine/Scheduled | 151-19-0034 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3500 | Microfast |  | Gravity | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 06:07 PM
03/29/2023 | Alternative | Initial Visit | 800-STS-13234 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 2.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 5.25 minutes every 3.25 hours. Took BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Dec 30 1899 2:30PM
04/06/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
08/17/2023 | Alternative | Routine/Scheduled | 166-13-133 | Northumberland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the septic tank. Changed the filter in the aerator and changed the mesh screen in the spinfilter. The UV is not working - needs a tube, bulb, cord, and a ballast or circuit board. The Clearstream tank needs to be pumped out as well as the septic tank. The timer is set to 8 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/17/2023 | 02:00 PM
10/02/2023 | Alternative | RoutineScheduled | 11-100-0121 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | Bio-Coir |  | Pump | Gravity | Trenches | UV | 300.000000 | [] | [] | YES | [17 empty] | Sludge judge test revealed 3-4 in of accumulation from bottom of the septic tank. System is working as designed. Media is good condition and at proper level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 12:00 PM
08/20/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/20/2023 | Dec 30 1899 9:30AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-91980 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
04/06/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Jet UV cord & bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/15/2023 | Jan 1 1900 7:20PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/25/2023 | Alternative | Routine/Scheduled | 115-STS-94301 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Septic tank at normal level, pulled and cleaned filter. Pump tank in good condition, normal operating level. Peat moss in good condition, some minor root intrusion. Raked out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | 08:42 AM
05/22/2023 | Alternative | Reportable Incident | 157-02-150 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | None | None | [18 empty] | Owner had Blakes Septic Service do a "point of sale" inspection - system now in alarm - not functioning. Technician found circuit breakers OFF to control panel, compressor and discharge pump! System due for service, NO SERVICE conducted at this time due to "other service provider" involved and "operating" treatment system! | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/01/2023 | 07:15 AM
08/17/2023 | Alternative | RoutineScheduled |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 12:00 AM
10/04/2023 | Alternative | Routine/Scheduled | 053-STS-10019 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | Dec 30 1899 12:27PM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Ecoflo is in poor condition. There is severe root infiltration and a large amount of ponding. The homeowners are going to take the path of replacing the Ecoflo with a modern treatment unit. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
10/11/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1250 | anua (puraflo) |  | Pump | Gravity | Trenches | Not Applicable | 100.000000 | ["Effluent Screens"] | ["Effluent Screens","Control Operation","Level Sensor Operation"] | YES | Musty | Clear | [15 empty] | New lid installed. system is operational and in working order. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 10:00 AM
01/23/2023 | Alternative |  | 132-16-0030 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Robert | Albrecht | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/19/2023 | Alternative | RoutineScheduled | SD-11-42 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 1.000000 | 1500 | Mircofast 0.75 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Attached Growth Medium","BlowerCompressorAerator Operation"] | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 10:00 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/05/2023 |  | RoutineScheduled | 177-STS-90519 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [5 empty] | 01/05/2023 |  | 13.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Hl 8, ll 7, override 5 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
02/09/2023 |  | RoutineScheduled | 099-STS-91600 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"Level Sensor Operation"] | NA | Musty | Clear | [5 empty] | 02/09/2023 |  | 9.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Found system turned off. Breakers for panel, pump and blower were off, turned everything on and system started to work. HL 1, LL 10, OVERRIDE 0. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
09/18/2023 | Alternative | RoutineScheduled | 128-04-203 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/17/2023 | Alternative | RoutineScheduled | 175-93-0384 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["Effluent Screens"] | [] | NO | [17 empty] | Septic Tank-2"sludge 0"scum/ Pump Tank-2"sludge/ Inside Controls, pump, floats and alarm functioning properly/ No Counts or ETM on the control box/ Pump Rate: 2.5" drawdown in 1 min. The A-300 Septic tank filter is broken and requires replacement/ No breakout or spongy areas on the LPD Drainfield Site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/24/2023 | Alternative |  | 150-16-0188 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/30/2023 |  | RoutineScheduled | 175-04-0477 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | [8 empty] | 01/30/2023 | Sample Chamber | 58.000000 |  |  | 164.000000 |  |  | Will be sent separately |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/05/2023 | 12:00 PM
10/13/2023 | Alternative | RoutineScheduled | 150-19-0050 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
02/08/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | MicroFast tank needs pumping & treated with fungus killer. MicroFast lid needs 6" vent. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/15/2023 | Jan 1 1900 10:55AM
06/22/2023 | Alternative |  | 132-18-0035 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Jessica | Haynes | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/20/2023 |  | Routine/Scheduled | 08-163-0063 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/21/2023 | Jan 1 1900 8:00AM
08/17/2023 | Alternative | Routine/Scheduled | 19-174-0026 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/17/2023 | Dec 30 1899 1:15PM
05/12/2023 | Alternative | RoutineScheduled | 17-137-0241 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2250 | 1250 | 1000 | Pump | Gravity | Pad | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | Pungent | Dark Brown | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | 12:00 AM
12/26/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Septic 7" scum. 0" sludge. Treatment side 10" sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2024 | 12:00 AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 182-06-0494 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Ecoflo | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | owner has agreed to do necessary repairs | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/06/2023 | 03:05 PM
08/14/2023 | Alternative | Routine/Scheduled | 157-08-0035 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 05:00 PM
04/04/2023 |  | Routine/Scheduled |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, Recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. LPP Pad - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | Jan 1 1900 9:15AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/02/2023 | Alternative | RoutineScheduled | 103-STS-101193 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 02/02/2023 | [10 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/23/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/06/2023 | Alternative | Routine/Scheduled | 133 04 1139 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 10:00 AM
03/17/2023 |  | RoutineScheduled |  | Charles City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2000 | 1000 | 1000 | Pump | Pressure | Drip | UV |  | [] | ["Auxiliary Filter","Control Operation","Disinfection","Distribution Pump Operation","SludgeScum Accumulation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | None | Clear | 7.000000 |  | 7.000000 | [13 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/17/2023 | Jan 1 1900 12:00PM
09/20/2023 | Alternative | Routine/Scheduled | 151-05-361 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: At normal level Reseal job seems to be holding up Has less than 1" of solids with 8" of sludge Pulled and cleaned rsv -Recirculation Tank: At normal level Has less than 1" of solids with about 9" of sludge Pulled and cleaned pump, floats and filter Reseal job seems to be holding up Pump and floats working properly -Discharge/Pump Tank: At normal level Pump and floats working properly -Media Sheets: Sheets were replaced last year and are in great shape Brushed and flushed laterals Sprayed off sheets -Control Panel: Panel is new Visual and audible alarms working Recirc pump pulling 11.76amps Discharge pump pulling 6.79amps -Drain Field: Showing no signs of surfacing or blowouts Has valve box inside of an ezset riser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 01:55 PM
05/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/09/2023 | Alternative | RoutineScheduled | VAG401364 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Nayadic |  |  | Gravity | Discharge | Chlorination |  | ["Disinfection"] | ["Disinfection"] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/09/2023 | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/30/2023 | 10:30 AM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | 175-06-0480 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
01/24/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 750 | Delta Environmental Products DFSeries |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank - 3" crust, 12" of accumulated solids on the bottom. Treatment unit - 2" crust and 2" of accumulated solids on the bottom. Cleaned blower air filter. Septic tank and treatment unit do not need to be pumped out at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 07:03 PM
05/02/2023 |  |  | {FIPSCode}-STS-24675 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/02/2023 |  | 4.460000 |  |  | 1.900000 |  |  | Will be sent separately |  | BOD: 4.46 TSS: 1.90 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 12:00 AM
07/28/2023 | Alternative | RoutineScheduled | 10-173-010 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Norweco |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | Dec 30 1899 10:15AM
09/15/2023 | Alternative |  | 04-125-164 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:00 AM
06/15/2023 | Alternative | Follow-Up Component Maintenance | SD-06-111 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to auger all 5 pods. Removed roots in pods 1 and 5 and added root destroyer to those pods. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
12/05/2023 | Alternative | Routine/Scheduled | 166-14-020 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 07:24 PM
10/02/2023 | Alternative | RoutineScheduled | 08-184-5006 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/02/2023 | 12:00 AM
05/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/27/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Ecopod | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation","Attached Growth Medium"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [17 empty] | On 12/13/2022 had a service call and determined the system had a faulty peak float and the blower was not working (The blower is faulty) Replaced the E-75 Blower and the float. Counts: Peak-10537 High-565/ Pump1-4666 ETM-225h 26m/ Pump2-2709 ETM-215h 7m On 12/16/2022 Replaced a faulty peak float. On 1/27/2023 performed a inspection of the alternative system. Septic-14"sludge6"scum/ Ecopod ATU >75-18"sludge 0"scum/ Pump out is necessary due to sludge levels/ Pump Tank-3"sludge/ Controls, pump, floats and alarms now functioning properly/ Blower functioning properly/ Counts: Pump1-4692 ETM-227h 40m/ Pump2-2734 ETM-217h 15m/ Peak-10527/ High-994/ On-4m 45s Off-9h 55m | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
01/16/2023 |  | RoutineScheduled | 015-STS-335106 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
01/06/2023 |  | Routine/Scheduled | TELS-ATRSLQ | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 2:45PM
05/11/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [8 empty] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 02:14 PM
02/24/2023 |  | RoutineScheduled | SWP-03-67 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | 1" of water in sample box. Owner stated no alarms after rain. Recommend adding inlet riser on septic tank and seal pump tank wedge lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
02/27/2023 |  | Routine/Scheduled | 07-120-0427AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Best 1 |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/27/2023 | Jan 1 1900 1:03PM
05/19/2023 |  | RoutineScheduled | 2017-143-0101 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Ecopod |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Dispersal System Operation","Level Sensor Operation","Control Operation","Auxiliary Filter"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/03/2023 | Alternative | RoutineScheduled | 019-STS-27296 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Drip |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Newly installed system start up and adding of internet moniroring- Septic system, minimal Scum and minimal slduge in Septic tank, Pump tank miniml sludge, no scum. Alarm Test Good 4 Floats Good Pump count Tredning start today. 10.5 amp on recirc pump and 11.8 amp on discharge pump. Confirmed factory reccomended setting. Returned 4-30-22 to add internet monitoring, set times to 8.4 min off and 4.2 min off for override. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
04/06/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Solution added to media Tank appears unlevel Rec french drain and wash media | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
03/28/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
04/10/2023 | Alternative | RoutineScheduled | 10-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 6 Dechlorine Installed discharge sign. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/10/2023 | 12:00 AM
03/23/2023 | Alternative | Reportable Incident | S 800-16-0188 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [17 empty] | Responded to alarm event. Found compressor had failed - replaced while on property. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/28/2023 | Dec 30 1899 7:00AM
08/31/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 11:00 AM
02/06/2023 |  | RoutineScheduled | 128-15-0037 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/30/2023 | Alternative |  | 101-19-0102 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | John | Ledeter | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/17/2023 |  | Routine/Scheduled | 234-13-8 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | Jan 1 1900 9:35AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/12/2023 | Alternative | RoutineScheduled | 107-09-0072 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","SludgeScum Accumulation"] | ["Auxiliary Filter"] | [18 empty] | FAST/septic to be pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
12/13/2023 | Alternative | RoutineScheduled | 093-09-0066 | Isle of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | JEFulbright Septic, LLC | 1942001131 | Jason | Fulbright | 1.000000 | 3000 | Biomicrobics |  | Pump | Gravity | Trenches | Not Applicable | 480.000000 | [] | [] | NA | Musty | Clear | 7.180000 | 3.150000 |  |  |  | 12/13/2023 | Pump Chamber | 7.000000 |  |  | 12.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | Dec 30 1899 3:35PM
07/18/2023 | Alternative | Pump-Out Only | {FIPSCode}-STS-2787 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 2:30PM
05/23/2023 | Alternative | RoutineScheduled | 105-84-0133 | Appomattox | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 2.000000 | 2500 | Septic | Sand filter | Gravity | Gravity | Discharge | Chlorination | 450.000000 | [] | ["Disinfection","SludgeScum Accumulation"] | NA | None | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/23/2023 | 04:30 PM
07/10/2023 | Alternative | Routine/Scheduled | MS 109, Lot 14A | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 7:35AM
03/14/2023 |  | RoutineScheduled | 101-12-0164 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Recirc Sand Filter |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation","Auxiliary Filter","Effluent Screens"] | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation","Auxiliary Filter","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 01:10 PM
09/29/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 1.000000 | 1250 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable | 300.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Measured 12" solids in septic tank-pumpout not required; contents of septic tank very watery-suspect leaking toilet; cleaned septic tank Zabel filter; cycled Puraflo pump: 12.33 amps, 1924.77 hours, 20,219 cycles. Modules 2 & 3 showing signs of ponding; however, effluent drained through shortly after end of pump cycle and no overflow outside of the modules. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/26/2023 | 12:00 AM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/05/2023 |  |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 3.000000 | 1530 |  |  | Pump | Gravity | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/11/2023 |  | Initial Visit | 073-STS-93875 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Replaced the filter in the aerator. Repaired the broken air line. Pumped out the septic tank. The timer is set to 1.75 minutes every 1.5 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | 10:00 AM
01/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | MicroFast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | Dec 30 1899 11:31AM
01/31/2023 | Alternative | Reportable Incident | 151-10-0066 | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | None | NO | [17 empty] | system has slow drains and blockage in sewer line - Millers Services jetted sewer line to clear blockage - noted system appears to require service and reported that system is/was maintained by Beasley Septic Service. Residence recently sold - not interested in service and/or repairs at this time. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/01/2023 | 11:15 AM
09/12/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Repair air vent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 12:00 AM
08/08/2023 | Alternative | RoutineScheduled | 017-STS-335171 | Bath | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | No discharge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/08/2023 | 12:00 AM
05/04/2023 | Alternative | Routine/Scheduled | 13-174-0171 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | EcoPod |  | Pump | Pressure | Pad |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/04/2023 | Dec 30 1899 2:59PM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-01-682 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Septic tank needs pumping due to sludge level. Outstanding proposal for sealing leaks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance | 177-16-0157-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend the discharge point and access to the discharge point be mowed and maintained in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/15/2023 |  | RoutineScheduled | 12-197-076 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Level Sensor Operation","Effluent Screens","Dispersal System Operation","Control Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | 12:00 AM
07/22/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
01/02/2023 | Alternative |  | 101-16-0409 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Alan and Meg | Beckenstein/ Hargrave | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/14/2023 | Alternative | RoutineScheduled | 107-10-0358 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Gravity | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/01/2023 | Dec 30 1899 8:30AM
07/31/2023 | Alternative | Routine/Scheduled | 166-07-226 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation"] | ["Attached Growth Medium","Control Operation"] | YES | [17 empty] | Peatmoss Biofilter repalcement. Removed spent biofilter media with vac truck. Installed new. Replaced control panel for pump station with new Orenco MVP panel. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/01/2023 | 07:15 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-92232 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | none | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
03/07/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 03/07/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected | Inlet was clogged but able to clear and clean | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
10/11/2023 | Alternative |  | 127-STS-34693 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 2750 | 1000 | 1000 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | None | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | Dec 30 1899 3:00PM
07/10/2023 | Alternative | RoutineScheduled | 181-11-0020 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 2000 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation","Effluent Screens"] | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation","Effluent Screens"] | YES | [7 empty] | 07/10/2023 | Pump Chamber | 5.800000 |  |  | 27.000000 |  |  | Attached to this report |  | The system did not need to be pumped. The blower and spin filters were both cleaned. The controls were operating as designed. The top tank riser was dug up and replaced due to screws not holding the lid secure. The pressure gauge was replaced on the supply line to the drip field. The BOD and TSS were within permitted limits. There was return effluent returning to the pump tank so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/31/2023 | 10:30 PM
04/21/2023 |  | RoutineScheduled | 17-118-0008 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Aqua klear |  | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Auxiliary Filter","Effluent Screens","Control Operation","Level Sensor Operation","Distribution Pump Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/21/2023 | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/21/2023 | Alternative | Routine/Scheduled | 550-STS-6547 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | Dec 30 1899 11:28AM
03/20/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
01/06/2023 |  | Pump-Out Only | C 800-15-0034 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Supervised pumpout of treatment system by Goodman's Septic Service. Aeration tank refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 9:00AM
03/28/2023 |  |  | 041-STS-259259 | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 3500 | 1500 | 1000 | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles"] | YES | Pungent | Clear | 7.000000 |  | 7.000000 | [13 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/28/2023 | Jan 1 1900 2:00PM
09/20/2023 | Alternative | RoutineScheduled | 15-120-0459A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/05/2023 | Alternative | Reportable Incident | 093-18-0024 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/05/2023 | Dec 30 1899 8:00AM
06/30/2023 | Alternative | Routine/Scheduled | 234-17-371 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced aerator and diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 8:20AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
11/27/2023 | Alternative | Routine/Scheduled | 228-15-0296 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | Dec 30 1899 12:20PM
11/16/2023 | Alternative | Routine/Scheduled | 810-STS-3888 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | Dec 30 1899 4:00PM
07/12/2023 | Alternative | RoutineScheduled Component Maintenance | 099-18-0120 C-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["SludgeScum Accumulation" ,"Septic Tank Baffles" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection and replaced uv bulb. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
04/27/2023 | Alternative | RoutineScheduled | S16-111-0086 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | BioMicrobics MicroFast |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank - First compartment - 2" solids crust, 8" accumulated solids, Second compartment - 12" accumulated solids, no crust. Cleaned blower air filter. Excellent treatment quality. Adequate aeration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | Jan 1 1900 7:03PM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | 033-17-0086-SP | Caroline | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The Norweco aerator is not working and should be replaced. The Presby mound was very spongy at the bottom of the mound. There was not any water in the pump tank to test for surfacing effluent. We understand that the system designed has recommended a repair that is to be completed by another firm. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/02/2023 | 06:05 AM
12/16/2023 | Alternative | RoutineScheduled | 133 13 0151 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 RT |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 8" of accumulated solids in septic tank. Cleaned septic tank solids filter. 0" of solids in recirculation portion of treatment unit. 1" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Tested floats, pump, and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/22/2024 | 07:03 PM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping the tank prior to next years inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1000 | Septic | Pure flow | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | Dec 30 1899 1:44PM
12/19/2023 | Alternative |  | 13-197-A3 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/19/2023 |  | 9.930000 |  |  | 13.000000 |  |  | Will be sent separately |  | BOD: 9.93 TSS: 13.0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
10/18/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 | [8 empty] | [] | [] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/01/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 9:45AM
08/09/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Real Estate Inspection Primary septic tank - no sludge - clear water !!! indications has been pumped by unknown "others". Also, system has been "idle" for an extended period of time. Pump Tank - float sensors, pump and controls - recommend replacing all due to age. LPP Absorption Field - require permit to locate all components. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 09:30 AM
01/11/2023 |  | Initial Visit | 093-STS-14960 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 11.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the aerator. The timer is set to 1.5 minutes every 2 hours 53 minutes. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2023 | Jan 1 1900 8:15AM
12/01/2023 | Alternative | Routine/Scheduled | 093-06-0150 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV (Recirculating Splitter Valve): Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge pump plumbing has exceeded life expectancy. Discharge splice box conduit is damaged. Discharge riser is damaged. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Alarm logs state that recirculation has been having excessive overrides and high levels. I checked daily discharge logs and found no evidence of excessive flow or water usage. Adjusted recirculation timers to accommodate 6 person occupancy -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 9:06AM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-273 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
07/24/2023 | Alternative | RoutineScheduled | 07-118-0092 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex |  | Pump |  |  |  |  | [] | ["Recirculation Pump","Level Sensor Operation","Control Operation","Attached Growth Medium"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 12:00 AM
10/25/2023 | Alternative | Routine/Scheduled | 99-142-0430 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1250 |  |  | Pump | Pressure | Pad | Not Applicable | 250.000000 | ["Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Inspected Peat Septic Tank pumped-out 11/07/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | Dec 30 1899 11:07AM
04/18/2023 |  | Reportable Incident | 175-16-0355 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced EZ Treat pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/11/2023 | Alternative | RoutineScheduled | 159-10-177 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump |  |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled | 165-STS-336290 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled | 175-12-0317 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
02/09/2023 |  |  | 033-12-0101-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | We will be pumping the tanks in May 2023 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced blower control panel | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
12/07/2023 | Alternative | RoutineScheduled | 06-100-1254 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | JEFulbright Septic, LLC | 1942001131 | Jason | Fulbright | 8.000000 | 10000 | Nitrex Denitrification Unit | EcoFlo Biofilter | Pump | Gravity | Mound | UV | 3900.000000 | [] | [] | NA | Musty | Clear | 7.400000 | 3.250000 |  |  |  | 12/07/2023 | Sample Chamber | 7.000000 |  | 6000.000000 | 4.000000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:15 PM
01/23/2023 |  | RoutineScheduled | 177-14-0213 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/11/2023 |  | Routine/Scheduled | 157-16-0047 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | On arrival the pump breaker was tripped, the alarm light was un-plugged, and it was muted. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Pumped out the Clearstream tank and pump tank. The timer is set to 4 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/11/2023 | 01:00 PM
06/13/2023 | Alternative | Reportable Incident | 159-11-011 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Owner contacted believing this to be a conventional system - AOSS System overfull - Discharge pump not functioning, Aeration not functioning. Pumped Discharge tank empty and pumped trash tank partially. No known service agreement in place. States property is to become an Air BnB Rental! | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/21/2023 | 07:45 AM
12/12/2023 | Alternative | RoutineScheduled Component Maintenance | SD-10-335 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. Drip tank low level alarm count the same at 509. In the past 8 days, the system pumped an average of 1,306.8 gals/ day at 268 gals/ cycle (avg.) for a total of 10,455 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 09:40 AM
06/02/2023 | Alternative | RoutineScheduled | 061-STS-24565 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | MicroFast 0.50 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 08:00 AM
03/16/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
05/17/2023 |  | Routine/Scheduled | NYII-ATHMUZ | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Jan 1 1900 1:35PM
11/01/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 12:30PM
04/13/2023 |  | RoutineScheduled | 101-15-0322 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | AquaKlear |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | 12:00 AM
12/18/2023 | Alternative |  |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  | Pressure | Trenches | Not Applicable |  | ["Other"] | [] | [18 empty] | Concrete riser and lids deteriorating | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced 2 gauges | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
11/27/2023 | Alternative | RoutineScheduled | 182-16-0319 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  |  |  | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Recirculation Pump","Dispersal System Operation"] | ["Auxiliary Filter","Septic Tank Baffles","Recirculation Pump","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | 12:00 AM
11/01/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20297 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
01/22/2023 | Alternative | Reportable Incident | 157-12-0074 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Trenches | UV | 450.000000 | Distribution Pump Operation | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Alarm Event Discharge pump failure - had trash tank and pump tank pumped empty for storage ... Was able to replace pump - same day. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/23/2023 | 09:15 AM
02/06/2023 |  | Routine/Scheduled | 08-163-0074 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - mixing present - compressor serviced - recommend pumpout and refill of processing tank. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | Jan 1 1900 8:00AM
02/06/2023 |  |  | 01-137-0430 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Pumped Out | Will be doing maintenance here every 6 months due to the size of the system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | 12:00 AM
11/01/2023 | Alternative | Routine/Scheduled | 800-11-0275 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 1:25PM
03/10/2023 |  | RoutineScheduled | 03-197-151 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/10/2023 | 12:00 AM
12/05/2023 | Alternative | Routine/Scheduled | 093-11-0053 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Customer Noah Baines Property Address 3398 Fort Huger Drive, Smithfield, VA 23430 USA Technician Brandon Boughton Date Serviced 2023-12-05 Was customer present for service? Yes Type of System Alternative Type of AOSS System Clearstream Components Septic Tank Condition of above Component Notes for above Component Was pumped before time of service At normal level Discharge/Pump Tank Condition of above Component Notes for above Component Was pumped before time of service Transducer not working (The Man who installed system is replacing it) Pulled and cleaned pump and spin filter Aeration Condition of above Component Notes for above Component Found at normal level Less than 1in of sludge Air Pump/Blower Condition of above Component Notes for above Component Pulled and cleaned filter Working properly Control Panel Condition of above Component Notes for above Component Clearstream panel working properly Aquaworx panel motherboard not working properly (The man who installed is replacing ) Drip Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 9:46AM
04/13/2023 |  | RoutineScheduled | 147-15-0071 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1500 | MicroFast 0.625 |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1500 | 2-2 1-0 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 4.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 11:00 AM
05/18/2023 | Alternative | Reportable Incident | 157-07-0256 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | NO | [16 empty] | Pumped Out | AOSS - Homeowner reportedly doing own maintenance! Non-Licensed! 05/15/2023 - pumped septic tank for owner to allow peat to dry. 05/18/2023 - Vacuumed peatmoss - homeowner replacing peatmoss and conducting maintenance himself. NOTE - Did Not visually see appropriate bags of peatmoss on property for re-installation. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/30/2023 | 12:15 PM
06/21/2023 | Alternative | RoutineScheduled Component Maintenance | swp-02-920 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
05/03/2023 |  | RoutineScheduled | 181-18-0052 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Pressure | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was cleaned. The recirculating and discharge pumps were both pulled and sprayed off. The textile sheets were sprayed off. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 10:05 PM
01/05/2023 |  | Routine/Scheduled | 228-13-0515 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 2:55PM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend evaluating distribution box later this year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance | 2090-04-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 01/16/2024 | 01:58 PM
08/08/2023 | Alternative | RoutineScheduled | 13-163-0024 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump |  |  |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance | SD-02-717 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Chlorination |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Owner is going to replace concrete lids and aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
10/23/2023 | Alternative | Follow-Up Component Maintenance | 047-STS-24438 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite per builder to inspect repairs made on the septic system by the installer. When I got to the job the system was in high level with waste water overflowing out of the aqua safe riser with no alarm on the septic panel. Homeowner stated toliet in basement was not flushing properly. This was caused by the high level and homeowner almost had a back up in the house. Control breaker was tripped in septic panel due to a wiring splice made under ground that does not meet code. Ran conduit to junction box in pump tank riser and replaced all 9 wires from panel to junction box. Used camera to inspect sewer line and gravity fall between all tanks. All was corrected with pipeing issues. Aqua safe riser still has small leak at casting. Recomend repairing when we do the yearly inspection on the septic system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
06/30/2023 | Alternative | Routine/Scheduled | 157-10-0022 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 4 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 02:00 PM
04/27/2023 |  | RoutineScheduled | 15-100-0058 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AquaSafe |  | Pump | Gravity | Mound | UV | 450.000000 | [] | [] | [18 empty] | Everything working as it should. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/01/2023 | 12:30 PM
04/05/2023 |  | RoutineScheduled | 06-184-5005 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation","BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 2 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/05/2023 | 12:00 AM
12/06/2023 | Alternative | Routine/Scheduled | 228-11-0522 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | [15 empty] | Replaced motor contactor | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | Dec 30 1899 7:30AM
03/09/2023 |  | RoutineScheduled | 08-118-0052 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Premier Tech Ecoflo |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor Operation"] |  | Musty | Cloudy | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/09/2023 | 12:00 AM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Septic tank needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | Dec 30 1899 10:33AM
02/02/2023 |  | Routine/Scheduled | 093-16-0201 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 1:05PM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 107-05-0316 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity |  | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced 2 pressure gauges | This AOSS should now return to normal function after having provided the above state routine maintenance | 11/22/2023 | 09:18 AM
02/10/2023 | Alternative | RoutineScheduled | SD-05-112 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Small leak (identified earlier) in pump tank has evidently not gotten any worse and was not leaking today. Owner said last alarm was in December when they got 4" of rain. Recommend pump out of septic tank by year end. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
09/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 09/19/2023 | Sample Chamber | 6.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 033-STS-89302 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Installed new vent cap, floats and Orenco panel button. Low level and timer enable floats were not working properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
04/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/03/2023 | Alternative | Reportable Incident | 073-STS-102336 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Effluent Screens"] | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Maintenance - VDH Permit 136-23-0083 - GMP2018-02 Installed access riser on outlet of septic tank. Installed cannister style effluent screen on outlet of septic tank. Installed new 4" PVC conveyance line. Installed new 8 port concrete distribution box. Installed new 4" PVC Header lines. Installed new absorption laterals 50' x 3' @ 42". | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 06:30 AM
11/02/2023 | Alternative | Routine/Scheduled | 166-15-126 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/02/2023 | 05:44 PM
01/12/2023 |  | RoutineScheduled | 175-14-0030 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
01/19/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs UV Unit | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | Dec 30 1899 11:08AM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance | SWT-01-352 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Zone 1 gal/min is 14. Zone 2 gal/min is 6.7. This is an indication of check valve failure. We recommend excavating by machine and installing two new check valves. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
02/15/2023 |  | Reportable Incident |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | BlowerCompressorAerator Operation | [20 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/29/2023 | 02:29 PM
02/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A septic system inspection was done on a conventional gravity. The septic tank lid was dug up it was 16" under the ground. The tank was pumped out and inspected for cracks or leaks and none were seen. We would recommend a riser and a filter be added. The sewer line was camera snaked and was clear. The 10-port concrete d-box was dug up it was 10" under the ground. We attempted to camera snake all 7 header lines but found lines 1 and 6 blocked with what appeared to be sludge. Line 2 was clear. Lines 3,4,5 and 7 were full of dirt you could see that the corrugated lines were split. There are 2 small trees between the drain field lines 6 and 7 that should be removed. At this time the septic system is not in working condition. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/29/2023 |  | RoutineScheduled | {FIPSCode}-STS-67375 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
04/03/2023 | Alternative | Routine/Scheduled | 093-09-0045 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Dec 30 1899 2:10PM
01/31/2023 | Alternative | RoutineScheduled | 151-11-0091 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service | 1942001034 | Kent | Cuthbertson | 2.000000 | 30,000 | 15000 | 15000 | Pump | Gravity | Trenches | UV | 19653.000000 | ["None"] | ["None"] | YES | [15 empty] | Attached to this report |  | Lab results were suspect due to admitted problems at the lab according to the lab director | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 07:03 PM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/18/2023 |  | RoutineScheduled | {FIPSCode}-STS-70836 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
11/08/2023 | Alternative | Routine/Scheduled | 136-00-0439 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level, 11in of sludge and less than 1in of solids. -Discharge/Pump Tank: Found at normal level, less than 1in of sludge. Tested floats and pump. All working as they should. Plumbing has brass gate and check valve. -Aeration: 24in of sludge and 4in of solids. Diffuser looks good. Pulled and cleaned diffuser and weir. High level alarm float working. -Air Pump/Blower: Pulled and cleaned air filter. Air pressure sensor working as it should. Audio alarm is not working. -Control Panel: 120 volts audio and visual alarms working as they should. Pump pulled 11.5 amps. -Distribution Box: Found 6lines, removed roots and found a crack in the plastic box. -Drain Field: No signs of surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 01:00 PM
02/06/2023 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1060 | Multiflo FTB |  | Gravity | Gravity | Trenches |  | 450.000000 | None | None | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 03:29 PM
01/18/2023 | Alternative | Routine/Scheduled | 166-06-059 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. BioFilter - peatmoss in fair condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - plastic - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | 07:30 AM
11/06/2023 | Alternative | RoutineScheduled | 061-17-02 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","BlowerCompressorAerator Operation"] | ["Control Operation","BlowerCompressorAerator Operation"] | NA | [7 empty] | 11/07/2023 | Sample Chamber | 12.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 1"scum/ Microfast ATU Tank-2"sludge/ Pump Tank-1"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Found broken contactor in the control box/ Replaced the contactor/ Controls, pump, floats and alarms are now functioning properly/ Counts: Pump-1366 ETM-14169/No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/07/2023 | Alternative | RoutineScheduled | 061-18-206 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 11/07/2023 | Sample Chamber | 12.000000 | [5 empty] | Attached to this report |  | Septic Tank-8"sludge 0"scum/ Microfast Septic Tank-2"sludge/ Microfast ATU Tank-12"sludge 0"scum/ Recommend pump out of all tanks due to 5 years since last pump out/ Blower air filter cleaned and blower working correcty/ Controls for Microfast working properly/ No breakout or spongy areas on the drainfield and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/27/2023 | Alternative | Routine/Scheduled | 18-120-0452A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/27/2023 | Dec 30 1899 11:40AM
10/24/2023 | Alternative |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine Annual, nothing to report | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 12:00 AM
06/24/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | EcoPod |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 10" of accumulated solids in septic tank. 18" of solids in treatment unit. Cleaned blower air filter. Tested alarm. Excellent treatment. Blower sounds slightly louder than normal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 07:03 PM
03/13/2023 | Alternative | RoutineScheduled | 05-198-262 | Wythe | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 |  | EcoFlow |  | Pump | Pressure | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Other","Effluent Screens"] | ["Effluent Screens","SludgeScum Accumulation","Other"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | Dec 30 1899 12:00PM
06/21/2023 | Alternative | Routine/Scheduled | 175-02-0291 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Gravity |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | Dec 30 1899 10:35AM
03/08/2023 |  | Follow-Up | 175-06-0440 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed new control panel & sample box lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
09/20/2023 | Alternative | RoutineScheduled | 182-11-0030 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | 12:00 AM
12/06/2023 | Alternative | RoutineScheduled | VAG401991 | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.620000 |  |  | 1.900000 |  | 12/06/2023 |  | 4.000000 |  |  | 7.300000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/28/2023 | 02:00 PM
04/25/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | Auxiliary Filter | Auxiliary Filter | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/12/2023 | 01:43 PM
02/22/2023 |  | Routine/Scheduled | 087-STS-6575 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/22/2023 | 12:34 PM
10/23/2023 | Alternative | RoutineScheduled Component Maintenance | 177-17-0127-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
01/18/2023 | Alternative | Routine/Scheduled | 151-15-0143 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 50.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 06:49 PM
05/10/2023 | Alternative | RoutineScheduled | 09-100-0583 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | BIOCOIR |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | [] | [] | YES | [16 empty] | Pumped Out | REPLACED FIBER IN SYSTEM. PUMPED SEPTIC TANK. EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/09/2023 | 01:00 PM
09/05/2023 | Alternative | Routine/Scheduled | 234-17-302 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | Dec 30 1899 10:55AM
06/26/2023 | Alternative |  | 179-17-0427-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
01/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 01/24/2023 |  | 8.000000 |  | 49.000000 |  |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | Dec 30 1899 8:47AM
01/31/2023 |  | Reportable Incident | {FIPSCode}-STS-3118 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced pump with a Zoehler 152, pump on/off float and alarm float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/31/2023 | Jan 1 1900 10:00AM
07/14/2023 | Alternative | RoutineScheduled | 019-STS-24961 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [16 empty] | Inspected | Investigate and alarm which occur the day prior. System was at rest and alarmed overnight. Adjusated pump off time to accomidate number of people per company reccomendations. 10 min off and 5 min off override time. Was set to 15.7 min off and7.7. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/30/2023 | 09:30 AM
07/28/2023 | Alternative | RoutineScheduled | 2006-143-0161 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/23/2023 | Alternative | Routine/Scheduled | 073-STS-101716 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Delta Environmental Products, UC Series |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped all tanks empty, cleaned / pressure washed. Filled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 08:30 AM
07/10/2023 | Alternative | RoutineScheduled | 181-10-0056 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 4.000000 | 4000 | Ecopod | Biomicrobics MicroFAST | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. Pumps functioning properly. No apparent leaks in system or drain field area. Panel boxes all functioning properly. System did not need to be pumped. Lids were properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/15/2023 | 10:35 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/26/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed at this time. There are three emitter spots near the far side of the drainfield that appear highly nitrified but it might just be less cover as the line ends. Recommend homeowner monitor and notify if there are any changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/29/2023 | Alternative | Routine/Scheduled | 550-STS-7010 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 5.000000 |  | 1.000000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). leaned the filter in the Clearstream, cleaned the disc filter, cleaned the disc filter, and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 6 minutes every 2 hours. Took 5 year BOD and Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Dec 30 1899 10:30AM
05/10/2023 |  | Routine/Scheduled | 2006-143-0066 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | N/A | [17 empty] | Air filter cleaned. System checked. System appears to be operating normally. Drain field needs some grading to promote runoff. The broken 6" Inspection port needs to be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 01:42 PM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-93031 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
07/13/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 2.000000 | 1000 | anua (puraflo) |  | Pump | Gravity | Trenches | Not Applicable | 100.000000 | ["Dispersal System Operation","Effluent Screens"] | ["Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [6 empty] | Sample Chamber | 21.500000 | [7 empty] | The system is operational. The peat moss is coming to its end of life expectancy but still operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 04:30 PM
08/21/2023 | Alternative | Routine/Scheduled |  | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating. Biofilter - peatmoss in good condition - raked / turned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 06:30 AM
03/06/2023 |  | Routine/Scheduled | 19-142-0063 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | UV | 600.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service PRocessing Tank - RSV, recirc pump and Effluent screen serviced. Treatment Module - media drapes & spray grid serviced. UV Disinfection - bulb and housing serviced. Pump tank - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | Jan 1 1900 9:15AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend servicing advantex in the near future | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping micro fast. Strongly recommend clearing/mowing drainfield area before any brush gets too large. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/14/2023 | Alternative | Routine/Scheduled | 800-05-0179 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | Dec 30 1899 11:35AM
08/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Micro fast | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2024 | Dec 30 1899 11:49AM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/11/2024 | 01:04 PM
05/18/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Low Pressure | [6 empty] | ["None"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/24/2023 |  | RoutineScheduled | 06-183-346 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/24/2023 | 12:00 AM
09/30/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20 |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 15" of accumulated solids in septic tank. Flushed treatment unit spray manifold. Suggest that passive air vent be replaced due to moss growing inside restricting air flow. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/15/2023 | 07:03 PM
01/05/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
09/28/2023 | Alternative | Routine/Scheduled | 06-160-0367 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable | 180.000000 | SludgeScum Accumulation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 01:00 PM
03/29/2023 |  | Routine/Scheduled | 550-STS-6350 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Jan 1 1900 11:05AM
04/27/2023 | Alternative | RoutineScheduled | C07-180-0041 | Roanoke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Delta Whitewater |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. 12" of solids in treatment unit. Air line leak due to excavation around new septic tank riser. Repaired second leak in air line on 5-11-2023. Blower alarm went away with repair. Adequate aeration after repair. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/16/2023 | Jan 1 1900 7:03PM
07/06/2023 | Alternative | RoutineScheduled | 2018-143-0241 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Auxiliary Filter","Attached Growth Medium","Control Operation","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
09/14/2023 | Alternative | Routine/Scheduled | 093-15-0035 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Annual Maintenance: -Septic Tank: Barn: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out. House: Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. -Discharge/Pump Tank: Barn: Water level normal. Inlet tee appears to be intact. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. House: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. -Media Sheets: Cleaned media sheets. Checked and confirmed spray pattern is good. -Control Panel: Barn: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. House: Checked and confirmed components within control panel are functioning. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 1:00PM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast ATU needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
03/23/2023 |  | RoutineScheduled | 06-113-019 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/23/2023 | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0852 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"SludgeScum Accumulation"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Advantex RX20 is ready for pumping First Side Sludge 8 Scum 8 Plus 2nd Side Sludge 12 Scum 0 Pump Tank Sludge 13 Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/29/2023 | 03:58 AM
10/13/2023 | Alternative | Reportable Incident Component Maintenance | 196-17-0078 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Three Rivers | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 2.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed blower. Replaced failed blower. Leaks on septic tank inlet wedge lid and outlet riser. Shed and Chicken pen is not recomended. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
10/01/2023 | Alternative | Routine/Scheduled | 041-STS-261186 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/01/2023 | Dec 30 1899 11:30AM
03/24/2023 |  | RoutineScheduled | 04-183-280 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/24/2023 | 12:00 AM
06/07/2023 |  |  | SP-04-76 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
01/04/2023 |  | Reportable Incident | 179-10-0140-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Septic backup in the house January 1st. Owner noticed the disconnect switch (next to control panel) was off and reset it. Alarm sounded. Red light still on today. No power to pump due to tripped breaker in the house. Replaced failed pump with same model (Zoeller N140). Junction box at tank was half buried and full of mud. Needs to be raised up on a short 4x4 post. Used handheld controller to check the panel. Event log showed that the panel was powered down May 25th and not powered up until January 1st. If the event log was working correctly, this would suggest that no pump cycles were taking place in the past 7 months. However, there were no signs of tank overflow and no other backups prior to January 1st. Plastic septic tank has 42" of cover and has not been pumped out in 6 years. Although the sludge level is still not at 25%, it may be a good idea to pump the tank to facilitate checking the tank for leaks (in or out) and structural problems. Peat was in good shape in all pods and dusty dry. The first pod's peat was noticeably lower and more compacted (possible drainage issue). D-box visibly out of level. Lines 2 and 3 were getting most of the effluent. After adjusting the dial-a-flows, lines 8, 9 and 10 are 1/2" too high to get any effluent. D-box needs reset. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
03/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping Pump chamber. There is a fair amount of scum visible. Small roots were seen around the riser but does not appear to be an issue. Recommend monitoring and resealing if necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/04/2023 |  | Initial Visit | 121-STS-12471 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1000 | AS 600 |  | Gravity | Gravity | Trenches | UV | 600.000000 | ["None"] | ["Other"] | NO | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/04/2023 | 03:00 PM
02/20/2023 |  | RoutineScheduled | 2130-09-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | UV | 250.000000 | ["Distribution Pump Operation","Disinfection","Control Operation"] | ["Distribution Pump Operation","Disinfection","Control Operation"] | NO | Musty | Clear | 7.600000 |  |  |  |  | 02/21/2023 |  | 8.000000 |  |  | 7.000000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/06/2023 | 12:00 AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/31/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Damaged riser was replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/16/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
08/22/2023 | Alternative | RoutineScheduled | 179-STS-92554 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0=0 0-0 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear | [14 empty] | Inspected | new home | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 10:00 AM
11/28/2023 | Alternative | RoutineScheduled | 175-14-0330 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 11/28/2023 | Sample Chamber | 4.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 0"scum/ Microfast-6"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-881 ETM-5164/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/22/2023 | Alternative | RoutineScheduled | 165-STS-337359 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
06/30/2023 | Alternative | Routine/Scheduled | 166-98-524 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 02:32 PM
04/24/2023 |  | RoutineScheduled | 027-STS-17695 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/24/2023 | 12:00 AM
04/04/2023 |  | RoutineScheduled | 17-113-126 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens","Control Operation","Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/04/2023 | 12:00 AM
06/10/2023 |  |  |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel |  |  |  |  | Gravity |  |  |  |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
03/28/2023 |  | Reportable Incident | {FIPSCode}-STS-1719 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - Initial Visit by Millers Services 03/24/2023 - after hours - found system full - found that someone re-wired the discharge side of the control panel for "Demand" dosing operation - all float sensors disconnected and pump wired to single float sensor and straight to circuit breaker. - Float sensor had failed - re-wired pump and pumped out of alarm condition. 03/28/2023 - System pumped by MDM septic service for full service and repair - no known service since CPEG notes of April 2017! Processing Tank - pumped empty - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes heavily impacted coated with biomat - ponding and bridging - access lid hinges fractured - recommend replacing media drapes. Pump Tank - requires re-wiring of control panel to proper timed dosing - sometime in the past someone has disabled all float sensors, alarms, etc. for the discharge side of the control panel and wired the pump as "demand" dosed. Pump is currently functioning. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/29/2023 | Jan 1 1900 10:45AM
05/10/2023 |  | RoutineScheduled | 153-STS-20283 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
10/26/2023 | Alternative | Routine/Scheduled | 175-06-0268 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Cajun Aire ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 10:25AM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-09-0188-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Small roots on both D-boxes, removed and added root-x. Vacuumed sludge out of both D-boxes and adjusted speed levelers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 107-15-0215 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 10/03/2023 |  | 16.000000 | [5 empty] | Will be sent separately | Inspected | Lab Normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
11/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/21/2023 | Alternative | Routine/Scheduled | 810-STS-4041 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/21/2023 | Dec 30 1899 12:30PM
05/17/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-9219 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | LPD |  | Pump | Pressure | Trenches | Not Applicable |  | [] | [] | NA | Septic | Cloudy | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | 12:00 AM
03/07/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0229 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/11/2023 | 11:24 AM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0069 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
09/05/2023 | Alternative | Routine/Scheduled |  | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - noramal level Aeration tank - normal level - mixing present - compressor serviced. NOTE - owner reports periodic aeration alarm - found loose wires at terminal bar - Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 10:30AM
04/14/2023 |  | RoutineScheduled | 175-03-0495 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
03/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/14/2023 |  | RoutineScheduled | 175-12-0084 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Recirculation Pump" ,"SludgeScum Accumulation" ,"Auxiliary Filter"] | ["Disinfection" ,"Recirculation Pump" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | On site for annual inspection, 5-year sampling, and routine maintenance. Treatment looks good, but fecal sample may not pass because there was no way to collect a free-falling effluent grab sample after the uv assembly. Sample was collected by plunging the collection bottle into the discharge pump tank effluent. BOD sample was collected in the same manner but is considered acceptable. Groundwater infiltration observed at the buried inlet wedge lid for the discharge pump tank (small roots visible and dripping observed). Recommend adding a riser and lid to grade and then moving the uv assembly into the pump tank. This would eliminate the leak, provide a way to properly collect samples, and facilitate pump-outs. Advantex septic tank needs pumped out due to sludge accumulation. AX20 squirt height was only 16". This was after cleaning the recirc pump intake and flushing the laterals. Pump may be wearing out or being affected by sludge level. Will re-evaluate at next service or tank pumping. Replaced uv lamp and cleaned sleeve, but could not remove and flush out the uv housing because it is hard-piped in place - which gives another reason to move it. The drip flush rate has steadily decreased over the past 3 years: 05/20 13.8 gpm, 06/21 12.3 gpm, 05/22 11.6 gpm, and 02/23 10.2 gpm. Recommend a bleach flush of the tubing as the first step in trying to return the flush rate to at or near the design rate of 15.4 gpm. Roots or crimped tubing could also be the cause of the decreased flush rate. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
11/30/2023 | Alternative | RoutineScheduled | 08-100-0912 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | 1250 | Gravity | Pressure | Pad | Not Applicable | 300.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | 12:25 PM
02/08/2023 |  | RoutineScheduled | 179-13-0077-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend scraping the Advantex sheets followed by pumping the Septic Tank & the Advantex RT tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance | 179-19-0047-SR | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | The Puraflo modules are not draining properly. This will accelerate the deterioration of the peat. We recommend pumping the tanks to allow for the peat to dry out and then excavating by machine to replace the plumbing that allows the modules to drain. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
02/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | Dec 30 1899 8:47AM
08/15/2023 | Alternative | RoutineScheduled | 107-10-0246 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
02/21/2023 |  | Routine/Scheduled | 234-16-135 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 1:20PM
07/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-07-010-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
07/05/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.230000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 02:30 PM
12/05/2023 | Alternative | RoutineScheduled Component Maintenance | SD-13-440 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. No breakers off this year, treatment looked good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
03/31/2023 | Alternative | RoutineScheduled | SD-10-208 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001682 | Frank | Hogan |  | 45000 | Whitewater ATU | Whitewater ATU | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | 7.200000 | 4.000000 |  |  |  | 03/31/2023 | Pump Chamber | 14.000000 |  |  | 3.000000 | 47.000000 |  | Will be sent separately | Inspected | Nitrogen high again, needs correction rrothgeb - Robert Rothgeb - Jan 04, 2023 3:15 PM Pre tank: Tank Okay No pumping. Flow EQ Tank: Tank needs pumping weir washed down. Blowers: Needs service. Change oil and change filters. ECOPOD Tanks: Service needed. Pump solids out of bottom of tanks. lower level of tank by 1/2 to 1 foot. Recirc / Discharge tank: Needs service. Remove any solids from tank. Only lower level by 1 to 2 feet. Drip Filter System: Filter System operating Normally - 0 rrothgeb - Robert Rothgeb - Jan 04, 2023 3:27 PM WWTP Secure and gates locked on arrival: Yes Unusual odors around plant: No Blowers working if present: Yes, No. Blower #3 and Blower #2 not operational Any component in Alarm?: No - 0 Pump Station Locked if present: Yes Drive through community look for alarms and overflows: No alarms identified Community alarms or overflow detail: NA - 0 Completed Data Sheet: No Peak Flow Last 7 Days: 15661 gal. 1/3/23 Low Flow Last 7 Days: 30 gal. 12/29/22 AVG Flow Last 7 Days: 11705.3 gal. From 12/28/22 To 1/3/23 1. install new alarm float in dosing tank. 2.test operations ok mthomassr - Michael Thomas - Jan 25, 2023 10:24 AM Today we repaired the: - New float We tested the new components: Yes We need to return to test the components: We do not need to return to test We left the sytsem in: Automatic System is functional The next step is: No further work required mrlynn - Makenzie Lynn - 1/24/2023 12:01:22 PM - install new omni float on recirc tank rrothgeb - Robert Rothgeb - Feb 22, 2023 9:58 AM Arrived rrothgeb - Robert Rothgeb - Feb 22, 2023 10:45 AM Pre tank: Tank Needs pumping Flow EQ Tank: Tank needs pumping weir washed down Flow EQ Alarms: Checked audio visual needs repair. ?HIGH LEVEL? alarm not working. One leg not connected to OMNISite. Blowers: All good check oil levels and belts no service needed ECOPOD Tanks: Service needed. One foot of solids needs to be removed. Recirc / Discharge tank: Tested audio visual alarms all work Drip Filter System: Filter System operating Normally - 0. ?HIGH LEVEL? alarm not connected to Drip Filter Control Panel. Omni Site Panel Test: Needs service. EQ Tank ?HIGH LEVEL? alarm has one leg not connected rrothgeb - Robert Rothgeb - Feb 22, 2023 10:58 AM WWTP Secure and gates locked on arrival: Yes Unusual odors around plant: Yes. Earth, diesel fumes, and smoke. Blowers working if present: Yes, No. Blower #2 not connected to air line. Blower #3 VFD down (not on wall). Any component in Alarm?: Yes - 1. Blower #1 running. Showing fault on Control Panel. Pump Station Locked if present: Yes Test telemetry system raise all floats for notice for office: Telemtry working Drive through community look for alarms and overflows: No alarms identified Community alarms or overflow detail: NA - 0 Completed Data Sheet: No Peak Flow Last 7 Days: 10292 gal. 2/15/23 Low Flow Last 7 Days: 5296 gal. 2/17/23 AVG Flow Last 7 Days: 7781 gal. From 2/15/23 To 2/21/23 rrothgeb - Robert Rothgeb - Mar 15, 202rrothgeb - Robert Rothgeb - Mar 10, 2023 5:04 PM Working with Steven on Master Zone Valve and Flow Meter. rrothgeb - Robert Rothgeb - Mar 9, 2023 5:25 PM Leaving rrothgeb - Robert Rothgeb - Mar 9, 2023 2:05 PM Back at Warrenton Chase to clean small filter. rrothgeb - Robert Rothgeb - Mar 9, 2023 11:00 AM Riggo and crew here to work on Master Zone Valve. rrothgeb - Robert Rothgeb - Mar 9, 2023 10:48 AM Opened gate at Raymond Farms for team to sample Monitoring Wells. rrothgeb - Robert Rothgeb - Mar 9, 2023 10:30 AM. Hosed down Pre-Tank. Checked anti-odorants, working well. rrothgeb - Robert Rothgeb - Mar 9, 2023 9:02 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/18/2023 | Alternative | Routine/Scheduled | 151-08-0291 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Biofilter - lid fractured from fallen tree - peat in good condition - raked/turned. Pump Basin - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 12:30 PM
01/23/2023 |  | RoutineScheduled | 179-18-0306-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation"] | [] | NA | [17 empty] | Septic-8"sludge 10"scum/ Microfast ATU-12"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Septic Microfast Tank requires pump out and the media requires spraying / No pump out of the pump tank needed at this time/ Controls, pump, floats and alarms functioning properly/ Blower air filter cleaned and blower working properly/ Counts: Pump cycles-43363 ETM-277h 23m/ High level-15/ Power failure-76/ Watermeter-0180482.5 On-7m 30s Off-3h 52m @ 8gpm FF-11.1/ No breakout or spongy areas on the drip field and dosing properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/31/2023 |  | Pump-Out Only | 147-15-00130 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | System pumped as recommended during routine service. Aspirator serviced, effluent screen serviced. System refilled with fresh water for re-start. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Jan 1 1900 8:00AM
12/29/2023 | Alternative | RoutineScheduled | 11-163-0058 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Best |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Auxiliary Filter","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/29/2023 | 12:00 AM
09/18/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches |  | 600.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | 12:44 PM
11/11/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Living Water Environmental | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | puraflo (anua) |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Effluent Screens","Dispersal System Operation"] | YES | Musty | Clear | [15 empty] | fluffled and even peat moss. installed a new junction box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/22/2023 | 11:45 AM
04/06/2023 |  | Reportable Incident |  | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Advanced Septic |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | AOSS - Voluntary Upgrade - VDH Permit 119-STS-101181 Primary septic tank pumped empty and abandoned. Installed new 1000 gallon concrete septic tank. Installed new Aquasafe AS600 ATU Installed new 1000 gallon concrete pump tank. Installed new absorption bed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 07:00 AM
02/21/2023 |  | Routine/Scheduled | 175-STS-14483 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 11:40AM
09/28/2023 | Alternative | Routine/Scheduled | 073-STS-92572 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Found at normal level, 3in of sludge and 2in of solids -Discharge/Pump Tank: Found at normal level, less than 1in of sludge and solids. Tested floats and pump all working as they should. -Aeration: Could hear and see treatment tank working as it should. -Air Pump/Blower: Pulled and cleaned air filter. Air pressure sensor working as it should. Air pump pulled 2.99 amps Control Panel for Microfast. 120 volts audio and visual alarms working as they should. -Control Panel: 120 volts. Audio and visual alarms working as they should. Pump pulled 5 amps moving water -Distribution Box: 3 lines balanced and taking water -Drain Field: No signs of surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 09:17 AM
03/23/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 03/22/2023 | Sample Chamber | 10.000000 | [5 empty] | Attached to this report |  | Septic Tank-10"sludge 3"scum/ Microfast-6"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-259 ETM-8h 2m/ Pump2-251 ETM-8h 5m/ Peak-8/ High-6/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/17/2023 | Alternative | Pump-Out Only | 09-120-0347R | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | 11/17/23 pemped 1000 gallons from aeration tank supervised refill of aeration tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | Dec 30 1899 10:01AM
11/20/2023 | Alternative | Routine/Scheduled | 136-05-310 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found above normal level due to clogged filter. Cleaned filter water level returned to normal. Found 5in of sludge and less than 1in of solids -Discharge/Pump Tank: Found at normal level, tested floats and pump all working as they should. Alarm is in the garage -Peat Moss: Tipping bucket and trays are in working order. Raked out peat peat has some ponding and compaction. Peat still has life left. 3 small cracks ecoflo -Distribution Box: 3 lines. Normal level. No roots or cracks -Drain Field: No signs of surfacing in drainfield area repairs 11/24: There is a couple spots that are cracked. There are no warranty or guarantee with these repairs. Came out and prepared spots to get fiberglass patches. Completed fiberglass patches and cleaned up area | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/05/2023 | 02:18 PM
04/04/2023 | Alternative |  | 154-18-0316 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Chris | Patterson | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/13/2023 |  | RoutineScheduled | SP-04-148 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The discharge pump is only doing approximately 10 gal/minute, and the pump tank was almost in high level. The laterals in the low-pressure dispersal system may be starting to clog. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
11/09/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-96-312 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We replaced the EZ Treat pump that has stopped working. We recommend pumping the clarifying tank due to sludge accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
07/06/2023 | Alternative | Routine/Scheduled | 17-172-0203A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | None | Clear | 6.700000 | 4.200000 |  |  |  | 07/06/2023 | Sample Chamber | [8 empty] | Routine Service Processing Tank - normal level - RSV, recirc pump, effluent screen serviced. TReatment Module - media drapes and spray grid serviced. U.V. - flushed and serviced bulb and housing. - obtained lab samples . Pump Tank - float sensors, pump and controls operating. Drip Field - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 7:30AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
03/13/2023 | Alternative | Reportable Incident | 157-18-0127 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - installed a rebuild kit on the aerator. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 4 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/13/2023 | 02:30 PM
03/13/2023 |  | RoutineScheduled | 06-125-178 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 12:00 AM
05/24/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Biomicrobics Micro Fast |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic Tank 1" scum 16" sludge - Treatment unit 12" sludge, Pump Tank -5-6" fine sludge- Pump operational - Pump alarm operational -- Cleaned , flushed and lubricated Spin Filter -Pump 79h33m vs 51hrs 22min last year equals 28 hours pumped and400 cycles- - Pump count 1398 vs 998 since last year. Flushed system, Good aeration in Fast treatment unit. Drainfield - No leaks -observed - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
03/10/2023 | Alternative | Reportable Incident | 136-14-0363 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Trenches | UV | 450.000000 | Disinfection | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Alarm Event - system in high level on arrival. After evaluation, found UV housing fractured - ballast underwater causing pump breaker to continuously trip. Waterproofed ballast - UV System housing needs to be excavated and replaced. System operating on departure. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/13/2023 | 10:15 AM
02/22/2023 | Alternative | Routine/Scheduled | 093-STS-14739 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. Installed a 3/4" check valve, installed 2 - 6" x 24" risers, and installed 2 - 6" x 20" risers. The timer is set to 1.75 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Dec 30 1899 1:00PM
11/17/2023 | Alternative |  | 033-18-0194-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/19/2023 | Alternative | RoutineScheduled | SD-01-562 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine annual, we did replace a broken check valve today. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 12:00 AM
11/20/2023 | Alternative | Routine/Scheduled | 13-137-0158 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Not due for pump out. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Checked and confirmed UV system is functioning properly. Flushed and cleaned vortex filter -Aeration: Water level normal. Not due for pump out -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. -Control Panel: Checked and confirmed components within control panels are functioning properly. Checked and confirmed audible alarms are functioning properly. Checked and confirmed visual alarms are functioning properly -Drip Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | Dec 30 1899 2:28PM
01/16/2023 |  | Reportable Incident | SP-05-307 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in high level due to hung toliet. Homeowner corrected toliet and system cleared high level alarm then went into low level. I will follow up. Testing the system while onsite everthing is working properly. Possibly a float or board working intermittently. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
05/31/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Damaged riser was replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/24/2023 | Alternative | RoutineScheduled | 154-10-0043 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Pump | Pressure | Drip |  | 150.000000 | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 10:55 AM
07/27/2023 | Alternative |  | 09-197-A3 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/27/2023 |  | 2.510000 |  |  | 3.000000 |  |  | Will be sent separately |  | BOD: 2.51 TSS: 3.00 DC | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 12:00 AM
01/09/2023 |  | RoutineScheduled |  | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Whitewater ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced discharge pump | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
05/26/2023 |  | RoutineScheduled | 132-02-0470 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/28/2023 | 12:00 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 12:02 PM
10/12/2023 | Alternative | Routine/Scheduled | 09-120-0251A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | Dec 30 1899 4:39PM
05/23/2023 |  | RoutineScheduled | 2009-143-0003 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation"] |  | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/23/2023 | 12:00 AM
10/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | NA | [7 empty] | 10/17/2023 | Sample Chamber | 95.000000 |  | 1600.000000 |  |  |  | Attached to this report |  | Septic Tank-6"sludge 2"scum/ Microfast-18"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ Microfast media is clogged/ Chemical cleaning and pump out is required of the Septic-Microfast Tank/ Blower air filter cleaned and blower is working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-8100 ETM-1234h 31m/ Peak-7 ETM-28h 0m/ High level-9/ Watermeter-0,718,255.92/ No breakout or spongy areas on the drip field and is dosing properly. Returned on 10/24/2023 for the chemical cleaning and pump out. Microfast media and system now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/28/2023 |  | Routine/Scheduled | 234-13-297 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | Jan 1 1900 10:20AM
01/15/2023 |  | RoutineScheduled | 101-12-0453 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/05/2023 | 11:55 AM
03/29/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | alarm buzzer not working when arrived. Needs replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
05/08/2023 |  | Routine/Scheduled | 13-163-0038 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. No surfacing present - owner declined having dbox excavated. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Jan 1 1900 10:45AM
07/26/2023 | Alternative | Routine/Scheduled | 04-160-0062 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 01:00 PM
11/30/2023 | Alternative | Routine/Scheduled | 115-STS-96028 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 2" of solids with 1" of sludge -Discharge/Pump Tank: At normal level Pump and floats working properly Has less than 1" of sludge -Aeration: At normal level Aeration is working properly -Air Pump/Blower: Working properly Pulled and cleaned Air filter -Control Panel: Both panels working properly Discharge pulling 7.46amps Aeration pulling 3.17amps -Distribution Box: At normal level All lines taking water properly -Drain Field: Showing no signs of surfacing or blowouts | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 04:01 PM
06/30/2023 | Alternative | RoutineScheduled | 113-19-018 | Madison | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 2.000000 | 3000 | Bio microbics |  | Gravity | Pressure | Drip | Not Applicable | 1200.000000 | ["None"] | ["None"] | NA | Musty | Cloudy | [5 empty] | 06/30/2023 | Pump Chamber | 25.000000 |  |  | 6.370000 | 44.980000 |  | Attached to this report |  |  | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/24/2023 | 12:00 AM
12/13/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | Type of System Alternative Type of AOSS System Delta Ecopod ATU to Drip Dispersal Septic Tank Condition of above Component Notes for above Component Water level above normal due to clogged effluent screen. Flushed and cleaned effluent screen and septic tank returned to normal level. Inlet tee appears to be intact. Not due for pump out Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. Checked and confirmed drawdown and float measurements are good. Made new splice connections for floats. Flushed and cleaned vortex filter. Aeration Condition of above Component Notes for above Component Water level normal. Not due for pump out. Air Pump/Blower Condition of above Component Notes for above Component Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator air intake filter. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarms are functioning properly. Checked and confirmed visual alarms are functioning properly. Drip Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 09:50 AM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance | 033-12-0067-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Control Operation"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Control Operation"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | New EZ Treat pump and float were installed along with a new alarm light & horn. Additionally, a new EZ treat riser was installed. Follow-up visit to replace the EZ set riser is planned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/18/2023 | Alternative | Reportable Incident | 115-STS-93366 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the red light being on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV light bulb and replaced the UV ballast. Pumped out the septic tank and pumped the sludge out of the Clearstream tank. The timer is set to 2 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/18/2023 | 04:30 PM
07/18/2023 | Alternative | Routine/Scheduled | 550-STS-6596 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 1:25PM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/08/2023 | Alternative | RoutineScheduled | 107-05-0647 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | [] | ["Control Operation"] | [18 empty] | Replaced control panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 12:00 AM
02/16/2023 |  | RoutineScheduled | 177-15-0220-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
12/05/2023 | Alternative | RoutineScheduled | 101-19-0116 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | AquaSafe 500EZ |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2023 | 10:55 AM
03/30/2023 | Alternative | RoutineScheduled | 133-STS-94950 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/07/2023 | Alternative | RoutineScheduled Component Maintenance | 013-STS-1033 | Arlington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Arlington | SES Mid Atlantic, LLC | 1942001203.000000 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | Dec 30 1899 1:16PM
02/01/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Needs floats replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/15/2023 | Jan 1 1900 10:55AM
07/06/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-76142 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
05/30/2023 | Alternative | RoutineScheduled | 061-STS-24967 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Advantex |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Distribution Pump Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","SludgeScum Accumulation"] | NA | [7 empty] | 05/30/2023 | Pump Chamber | 10.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/09/2023 | 03:00 PM
06/27/2023 | Alternative | Reportable Incident | 234-15-20 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the disc filter. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit (needs to be raised - makes a slight rattling noise). Could not check the UV (under water). It was raining at the time of service and could not check out the drainfield or mound. No valve boxes - could not locate the vacuum breakers. The timer is set to 9 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/27/2023 | Dec 30 1899 10:45AM
06/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
06/22/2023 | Alternative | Routine/Scheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 09:58 AM
09/07/2023 | Alternative | RoutineScheduled | 023-STS-42917 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 09/07/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | Jan 1 1900 2:25PM
11/07/2023 | Alternative | RoutineScheduled | 2018-143-0195 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 12:00 AM
07/05/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed new control panel. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | Dec 30 1899 12:46PM
02/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/14/2023 | Alternative | RoutineScheduled | 150-08-0132 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 gallons | septic tank | Delta Whitewater | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation"] | NA | Musty | Clear |  |  | 50.000000 | [12 empty] | Septic tank 3" fog 8" sludge, Delta Whitewater 50% SS, serviced aerator. Pump, alarm, floats, controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/23/2023 | 05:05 PM
02/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/16/2023 | Alternative | RoutineScheduled | 193-STS-92890 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters and uv | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/06/2023 | Alternative | RoutineScheduled | 2005-143-0140 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Other"] | [8 empty] | 09/14/2023 | Pump Chamber | 9.000000 | [5 empty] | Attached to this report |  | BOD sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 9:00AM
05/17/2023 |  | RoutineScheduled | 179-11-0183-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
03/10/2023 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced N140 effluent pump & (3) floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
07/05/2023 | Alternative | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Replaced alarm float on discharge side, other floats operational | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/30/2023 | 09:30 AM
05/09/2023 | Alternative | RoutineScheduled | 07-160-0158 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | Microfast |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [] | NA | Septic | Dark Brown | [14 empty] | Inspected | - pretreatment tank needs to be pumped/cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/19/2023 | 12:00 AM
07/11/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches |  | 600.000000 | None | None | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 09:40 AM
01/04/2023 |  | Routine/Scheduled | 810-STS-4044 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | [5 empty] | 01/24/2023 |  | 2.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 1:50PM
05/24/2023 | Alternative | RoutineScheduled | E-05-111-0058 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 4000 | Biomicrobics Fast |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | [] | NA | [16 empty] | Inspected | Sludge levels-- 24"+ sludge in upper Septic tank by Dumpster - This or next year maybe need Pumping Fast - Side fast port has 24" sludge. - Pump tank 6-8" sludge in front/side Fast tank, float swithes and pumps are opperational- Blower alarm good -Good aeration- discharge pump opperational, alarm is disconnected, Drainfield - the installer comes and repair leaks as and when needed. Septic tank by sancuatary had 14" sludge and pump tank 12" and pump is operational. Multiple tank by playground were chacked, Sludge varies about 3 to 12 inches and pump and float controls are operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
09/29/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-4052 | Dickenson | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | [18 empty] | Nobody is living at the property. System is idle. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/29/2023 | 12:00 AM
06/01/2023 |  | Routine/Scheduled | 550-STS-6441 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Jan 1 1900 1:50PM
12/18/2023 | Alternative | RoutineScheduled | 182-06-0491 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | drip tube repaired | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
08/17/2023 | Alternative | RoutineScheduled | 182-07-0080 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Dispersal System Operation","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","Dispersal System Operation","BlowerCompressorAerator Operation"] | [18 empty] | filters cleaned. jumbo lid replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 12:00 AM
06/19/2023 | Alternative | Reportable Incident | VAG408178 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Siphon | Gravity | Discharge | Chlorination |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | Musty | Clear | [15 empty] | no discharge during visit Tablets in feeders | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/06/2023 | 12:00 AM
05/15/2023 |  | Routine/Scheduled | {FIPSCode}-STS-4297 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | Jan 1 1900 10:00AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/16/2023 |  | RoutineScheduled | 101-06-0550 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | EcoFlo |  | Gravity | Pressure | Drip | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
10/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1125 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/02/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | [] | [8 empty] | 08/02/2023 | Pump Chamber |  |  |  |  | 23.700000 |  |  |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:30 PM
06/10/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
09/19/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Salcor control head & UV Bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 12:58PM
09/25/2023 | Alternative | RoutineScheduled | 11-183-190 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/25/2023 | 12:00 AM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0360-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Disinfection" ,"BlowerCompressorAerator Operation" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Disinfection" ,"BlowerCompressorAerator Operation"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
12/14/2023 | Alternative | RoutineScheduled | 181-10-0094 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | FAST/Treatment side needs pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 12:00 AM
02/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/22/2023 | Alternative | RoutineScheduled | 13-100-0443 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer |  |  | Septic Tank | Eljen Geotextile Sandfilter | Gravity | Pressure | Pad | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 02:10 PM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20466 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/17/2023 | 12:46 PM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
11/06/2023 | Alternative | RoutineScheduled | 17-197-023 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 6.000000 |  | 0.000000 |  | 11/06/2023 | [10 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/12/2023 | Alternative | RoutineScheduled | 101-04-0238 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 750.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | 12:00 AM
09/07/2023 | Alternative | Reportable Incident | 234-16-405 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/07/2023 | Dec 30 1899 9:00AM
10/10/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 12:00 AM
11/17/2023 | Alternative | Routine/Scheduled | SP-04-256 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal level 4in of sludge 4in of solids Pulled and cleaned rsv No signs of infiltration -Recirculation Tank: Normal level Tested floats and pump all working as should Pulled flushed and brushed bio tube filter All plumbing intact and pump moving water properly Floats are aged No signs of infiltration -RSV (Recirculating Splitter Valve): Taken apart cleaned check ball and flushed out Male slide intact and properly working -Discharge/Pump Tank: Arrived on site found tank was in high level due to timer enable float intermittently failing however as of now it is operational plumbing all intact and pump moving water properly Plumbing is aged, pump is free hanging Croc riser Pumped down to normal level -Media Sheets: Flushed and brushed laterals Sheets are bridging and stained locking struts are broken off. Lid is started to deteriorate Ran in test mode until water ran clear -Control Panel: 120 volts coming in All visual and audible alarms functional Discharge pump pulled 8.09 amps Recirc pump pulled 9.90 amps All components working properly Panel is aged -Distribution Box: Normal level 4 lines all intact and taking water properly Speed balancers intact and functional -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 02:27 PM
02/16/2023 |  | Routine/Scheduled | 2015-143-0027 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/16/2023 | 11:21 AM
05/15/2023 |  | RoutineScheduled | 177-06-0160-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Water quality was not as clear as it should be due to clogged biotube filter and pump intake, cleaned both. Treatment looks like medications are being used in the house. Will check next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
04/17/2023 | Alternative | Routine/Scheduled | 109-STS-33819 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Pressure | Drip | UV | 200.000000 | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | NO | [7 empty] | 04/17/2023 | Pump Chamber | 6.000000 |  | 110.000000 |  |  |  | Will be sent separately |  | Samples taken. Disc filter cleaned. Spray pattern for Advantex manifold emitters was adjusted. Timers adjusted. Had 5000 overrides in last 30 days. System should return to normal operation. The next visit is scheduled for on or around 10/18/2023. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/17/2023 | 09:51 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/26/2023 | Alternative | Routine/Scheduled | 157-07-0139 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 4 Modules - Peatmoss spent - ponding effluent - requires peatmoss biofilter replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/30/2023 | 08:00 AM
06/15/2023 |  | Follow-Up | 101-04-0599 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
05/24/2023 |  | Reportable Incident | 175-14-0220 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | EcoPod | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Salcor UV Unit with Norewco UV Unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
03/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | Dec 30 1899 7:05AM
11/21/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Not due for pump out. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly -Aeration: Water level normal. Flushed and cleaned effluent screen. Not due for pump out. -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Cleaned aerator shaft. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Drip Field: Flushed and cleaned disk filter. Found no signs of surfacing on dispersal field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | Dec 30 1899 3:52PM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/22/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/09/2023 | Alternative | Routine/Scheduled | 550-STS-6679 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 12:06PM
10/03/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
01/26/2023 | Alternative |  | 101-17-0487 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Robert/Dusty Lynn | Page | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/15/2023 | Alternative | RoutineScheduled | 109-18-0069 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 300 | BioMicrobics MicroFast |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of solids on the bottom of the septic tank. 4" solids crust in septic tank. 8" of accumulated solids in treatment unit. 3" of solids in discharge pump tank. Cleaned blower air filter. Cleaned drip manifold spin filter. Good aeration and excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 07:03 PM
06/30/2023 | Alternative | Routine/Scheduled | 234-16-360 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | Dec 30 1899 8:36AM
01/29/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 100 |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/29/2023 | 10:00 AM
01/13/2023 |  | RoutineScheduled | SWP-03-222 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
03/18/2023 |  | RoutineScheduled | 2050-03-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | YES | Musty | Clear | 7.300000 |  |  | 2.200000 |  | 03/21/2023 | Sample Chamber | 2.000000 |  |  | 6.100000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/03/2023 | 12:00 AM
06/14/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Visual alarm was replaced. Issues could not be replicated when troubleshooting and the system appears to be functioning as designed at this time. Advise homeowner to monitor alarms and notify if there are any changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/03/2023 | Alternative | RoutineScheduled | SD-04-33 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Puraflo peat needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | 12:26 PM
04/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
05/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection","SludgeScum Accumulation","Attached Growth Medium"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | Septic Tank-12"sludge 8"scum/ Microfast-18"sludge 0"scum/ Pump Tank-0"sludge 2"scum/ Pump out required of the Septic-Microfast Tank/ Blower air filter cleaned and blower working properly/ Controls, pump, floats and alarms functioning properly/ UV-Light sleeve cleaned but bulb requires replacement/ Counts: Pump-5609 ETM-1290h 13m/ Peak-26/ High level-28/ Standard Off-3h Peak Off-1h48m/ Dose 45 gal/ Watermeter-0,237,022.1/ No breakout or spongy areas on the drip field and dosing properly. Replaced UV-Light Bulb during inspection and now functioning correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
12/04/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | Dec 30 1899 2:05PM
04/26/2023 |  | RoutineScheduled | 179-07-0064-SWT | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Bad override float, replaced. Biotube filter was clogged bad, cleaned. Tank needs pump out. Will send proposal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
10/27/2023 | Alternative | RoutineScheduled Component Maintenance | 099-07-0210-ST | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Outstanding proposal for new junction box and wires for pump and floats. Pod number 4 ponding, unclogged outlet pipes and added new gravel. Augered and drained pretty well will check it next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 137-STS-25807 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
07/17/2023 | Alternative | Routine/Scheduled | 151-18-099 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 06:10 PM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/13/2023 | Alternative | Reportable Incident | 061-STS-21686 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Recirculation Pump"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm in the recirc tank due to loose/burnt connection at hot wire. Cut/stripped hot, neutral and ground wires and installed new wire nuts in the splice box. Pump running again. Reset all "R" counts to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
10/12/2023 | Alternative | Routine/Scheduled | 157-03-185 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual maintenance: -Septic Tank: At normal level Has 2" of solids(wipes) and 15" of sludge Riser is below grade -Trash Tank Rsv: At normal level No solids with7" of sludge Pulled and cleaned rsv -Recirculation Tank: At normal level Has 11" of sludge Pulled and cleaned pump, floats and filter Pump and floats are aged -Discharge/Pump Tank: At normal level Pump and floats functioning properly -Media Sheets: Lid is not attached Hinges and strut are broken Sheets are stuck together and ponding water Brushed and flushed laterals -Control Panel: Panel working properly Recirc pulling 12.43amps Discharge pulling 10.85amps -Distribution Box: Plastic dbox at grade At normal level Removed a few grass roots -Drain Field: Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 04:21 PM
07/11/2023 | Alternative | RoutineScheduled | 165-STS-336640 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
08/08/2023 | Alternative | RoutineScheduled | 133 18 0214 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 4000 | EZ Treat Filter |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Second Quarter 2023 inspection. Grease trap #1 - First section- 6" crust, 24" in bottom, Second section - 3" crust, 36" in bottom. Grease trap #2 - First section- 2" crust, 20" in bottom. Second section - 2" crust, 36" in bottom. Septic Tank- First section- 3" crust, 14" in bottom. Second section- 2" crust, 36" bottom. Anoxic tank/Septic tank #2- first section -skim crust, 12" on bottom. Second section- 1" crust, 10" on bottom. Recirculation Tank- First section-skim crust, 10" on bottom. Second section- skim crust, 24" on bottom. EZ Treat Tank #1- 0" crust, 0" on bottom. EZ Treat Tank #2- 1" crust, 24" on bottom. Discharge pump tank- 0" crust, 0" on bottom. Cleaned septic tank filters. Requested septic hauler to pump out grease trap #1 and #2, as well as, EZ treat Tank #2. Good spray patterns on EZ Treat spray nozzles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 07:03 PM
02/16/2023 |  | RoutineScheduled | 195-Discharge-14227 Peaceful Valley Rd. | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/16/2023 | 12:00 AM
05/04/2023 |  |  | 17-113-088 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/04/2023 |  | 3.110000 |  |  | 4.130000 |  |  | Will be sent separately |  | BOD: 3.11 TSS: 4.13 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 12:00 AM
09/06/2023 | Alternative | Routine/Scheduled | 136-14-0363 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Trenches | UV | 450.000000 | Disinfection | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service - U.V. system still in failure - NOT REPLACED. Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. Obsidian UV - FAILED - Disconnected from Power as it trips pump breaker - requires replacing. LPP Field - no indications of surfacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/07/2023 | 12:15 PM
01/09/2023 |  | RoutineScheduled | 179-12-0142-SR | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | There was no power to the UV panel. Owner is taking steps to address this. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/02/2023 | 07:17 AM
07/19/2023 | Alternative | Routine/Scheduled | 234-14-149 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced aerator and diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 1:10PM
09/13/2023 | Alternative | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 540 | Fuji |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/14/2023 | 10:51 AM
11/09/2023 | Alternative | Reportable Incident | 093-STS-14995 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Replaced norweco circuit board. Hooked pressure switch back up on the aerator. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/09/2023 | Dec 30 1899 12:00PM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | new alarm fix and bulb filter out of holster 3 pod peat replaced | This AOSS should now return to normal function after having provided the above state routine maintenance | 07/06/2023 | 08:40 AM
08/01/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-14975 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1000 | Aqua Klear | none | Gravity | Gravity | Discharge | Not Applicable | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Other"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Other"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/21/2023 | 03:45 PM
03/24/2023 | Alternative | Routine/Scheduled | 073-STS-95687 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash Tank - normal level Aeration tank - normal level - mixing present - compressor serviced. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 08:00 AM
02/16/2023 |  |  | 02-142-0007 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Pumped Out | We will be replacing the advantex control panel on 2/27/23 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  | 1000 | Pump | Pressure | Drip | Not Applicable |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2022 | 12:00 AM
04/03/2023 |  | RoutineScheduled | 101-13-0383 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Aquasafe |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/11/2023 | 10:25 AM
07/10/2023 | Alternative | RoutineScheduled | 181-04-0337 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches |  |  | [] | [] | NA | [17 empty] | Blower screen checked and cleaned. No apparent leaks in system or drain field area. Control panel functioning properly. Alarm functioning properly. System did not need to be pumped. Lid was properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:25 PM
03/21/2023 |  | RoutineScheduled | 08-113-035 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/21/2023 | 12:00 AM
05/12/2023 | Alternative | RoutineScheduled | 10-173-027 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 2.000000 | 2000 | Septic | Norweco | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | Dec 30 1899 10:30AM
09/26/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Virginia Beach | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip |  | 175.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/01/2023 | Dec 30 1899 12:00PM
05/23/2023 | Alternative | Routine/Scheduled | 136-96-0531 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced - recommend pumpout. Pump Basin - float sensors, pump and controls operating. Biofilter - 4 Modules - not serviced due to vegetative overgrowth! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 09:00 AM
02/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 11:51 AM
10/04/2023 | Alternative | RoutineScheduled | 127-STS-32907 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 12:00 AM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20230 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2024 | 11:49 AM
05/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
09/26/2023 | Alternative | RoutineScheduled | 109-12-0219 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20 |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned recirculation pump solids basket filter. Sprayed off treatment unit sheets. Flushed treatment unit spray manifold. There are roots around the septic tank inlet that may become an issue. Tested floats, pump, and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 07:03 PM
05/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/20/2023 |  | RoutineScheduled | 14-100-0361 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-21755 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.000000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0463 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:58 PM
05/02/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Sandfilter, Recirculating | [6 empty] | Distribution Pump Operation | Distribution Pump Operation | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 10:05 AM
10/06/2023 | Alternative | RoutineScheduled | 132-11-0035 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | MicroFast |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
08/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-11-0237 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Gravity | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance | 033-07-0183-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex Tank due to sludge accumulation in the tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
08/28/2023 | Alternative | RoutineScheduled | 10-125-046 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/28/2023 | 12:00 AM
05/03/2023 |  | RoutineScheduled |  | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/17/2023 | Alternative | RoutineScheduled | 003-STS-30832 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Mound | Not Applicable | 150.000000 | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 11:15 AM
04/04/2023 |  |  | 36609 | Clarke | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lord Fairfax | McKim Septic & Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Purflo | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/08/2023 | 02:25 PM
11/22/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Distribution Pump Operation","SludgeScum Accumulation"] | NA | [17 empty] | 42" overall liquid depth,12"-18" of sludge , 2" of scum. 12" on Fast side, 3" in the pump tank, Pumps, Alarms, Floats working, Field dry. Needs to be pumped, and vortex filter replaced. I will add to my truck for next inspetcion | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 12:00 PM
06/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced pressure gauge | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
10/11/2023 | Alternative | RoutineScheduled | SD-12-327 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable | 62.000000 | ["SludgeScum Accumulation","Attached Growth Medium"] | ["Dispersal System Operation","Effluent Screens"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 12:00 AM
08/22/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [6 empty] | Distribution Pump Operation | Distribution Pump Operation | [17 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/13/2023 | 01:25 PM
02/01/2023 |  | RoutineScheduled | 175-13-0231 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/13/2023 | 08:47 AM
12/14/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0228-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for rountine inspection. System has been alarming lately from to much water coming from the house. Home owner will check toliets. Peat moss is in good condition but roots are growing in all pods. Floats are to short in pump tank. Follow up visit will be made to remove roots from pods, auger peat moss and install longer floats in pump tank to give the system more storage. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
07/06/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89133 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Inlet pipe to pump tank is badly settled. Attached picture shows pipe in tank pointing at the ceiling. Force main for pump looks fine. Interior splice box in pump tank is leaning back tight against the riser, which is now cracked with mud stains present. This is probably due to the conduit settling just outside the riser. Both of these issues need to be repaired. Owner to contact his builder. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
09/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/30/2023 | Alternative | RoutineScheduled | 181-07-0289 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 3.000000 | 3500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens","SludgeScum Accumulation"] | ["Auxiliary Filter","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Filters checked and cleaned. System was pumped. No apparent leaks in system or drain field area. Control panels, blower, pumps and alarms all functioning properly. Lids were properly secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/15/2023 | 05:25 PM
11/07/2023 | Alternative | Routine/Scheduled | 145-STS-258062 | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/07/2023 | Dec 30 1899 3:41PM
03/21/2023 |  | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2500 | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Control Operation" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced blower and blower panel Need to clean up on drainfield and reinstall panel post Primary tank pumped | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
09/28/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 8.090000 | 7.200000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 03:45 PM
10/06/2023 | Alternative | Routine/Scheduled | 19-172-0074AR | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/19/2023 | Dec 30 1899 7:05AM
03/22/2023 |  | RoutineScheduled | SP-05-493 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Disinfection" ,"Attached Growth Medium"] | ["Control Operation" ,"Disinfection" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
06/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/05/2023 |  | RoutineScheduled | 132-03-0021 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
04/04/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [17 empty] | Replace 2 pumps/ 2 check valves | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | Dec 30 1899 11:30AM
06/21/2023 |  |  | {FIPSCode}-STS-76694 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
02/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | Dec 30 1899 2:21PM
08/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1000 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 08/29/2023 | Sample Chamber | 17.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/06/2023 |  | RoutineScheduled | 05-100-1313 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | JEF Septic LLC | 1942001131 | Jason | Fulbright | 8.000000 | 10000 | Nitrex Denitrification Unit | EcoFLo Biofilter | Pump | Gravity | Mound | UV | 3900.000000 | [] | [] | NA | Musty | Clear | 7.250000 | 3.250000 |  |  |  | 03/06/2023 | Sample Chamber | 3.000000 |  | 0.000000 | 1.400000 | 1.500000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/06/2023 | 10:00 PM
08/02/2023 | Alternative | Reportable Incident | 139-03-0186 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | 0.5 FATS |  | Gravity | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Septic | Black |  |  |  |  | Replaced FAST Blower & 2 Control Panels | [11 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/21/2023 | 04:15 PM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
12/01/2023 | Alternative | RoutineScheduled | 16-142-0094 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 12:00 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 11:17 AM
02/21/2023 |  | Routine/Scheduled | 234-08 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 1:45PM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | recommend camera the inlet line homeowner has agreed to repair fixed blower pipe at the coupling | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/06/2024 | 10:42 AM
03/28/2023 |  | RoutineScheduled | 17-100-0422 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [8 empty] | 398.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 12:00 AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
03/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/18/2023 |  | Reportable Incident | 177-07-0253-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Alarm call for high level on discharge tank. Found pilot fuse pulled out so processor was not getting any power, put back in place. Off float was not showing in processor, replaced and started to show. DLO relay was clicking on and off so replaced it (Doble pole 120v) and system started working normal. Advised owner to minimize water usage for the next 24 hours to get system back to normal level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92013 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | UV |  | ["Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Control Operation" ,"Disinfection" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump"] | YES | Musty | Clear | [5 empty] | 09/25/2023 |  | 3.000000 |  | 17.000000 |  |  |  | Will be sent separately | Inspected | Routine inspection. Sample taken. Found septic tank on high level due to clogged filter and leak on riser (bad rain past 2 days) cleaned filter and started flowing. Septic tank riser leaks badly needs to be sealed. water in d-box was very low as if seals are leaking recommend sealing it with adh200. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
04/07/2023 |  | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - effluent screen serviced. Aeration Tank - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/10/2023 | 08:45 AM
12/13/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-21755 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 4 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/13/2023 | 12:00 AM
01/18/2023 |  | RoutineScheduled | 177-STS-86713 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
08/30/2023 | Alternative | RoutineScheduled Component Maintenance | 061-19-034 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Septic tank needs pumped out ASAP. Referred owner to a local pumper. Tank will need to be refilled with fresh water after pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
09/13/2023 | Alternative |  | 17-125-039 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 09/13/2023 |  | 14.400000 |  |  | 18.800000 |  |  | Will be sent separately |  | BOD: 14.4 TSS: 18.8 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/13/2023 | 12:00 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 154-01-0052 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | PUMP STATION #2 - Will install new alarm horn and lightbulb at next quarterly inspection. PUMP STATION #3 - Installed new psi gauge on Zone 2. PUMP STATION #4 - installed new psi gauge on Zone 1 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
05/17/2023 | Alternative | Routine/Scheduled | 166-10-211 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | 04:41 PM
10/05/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced alarm float, aerator and pump relay | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/05/2023 | Dec 30 1899 10:00AM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/14/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | [] |  |  |  | 7.680000 | 5.510000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:35 PM
06/16/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Solenoid was replaced and the system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/03/2023 | Alternative | RoutineScheduled | 137-17-009 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Rappahannock | Ace Contracting Services, Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 |  | Puraflo | none | Gravity | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 03:09 AM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-25044 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Timer float was found to be stuck on, replaced it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
08/21/2023 | Alternative | Routine/Scheduled | 00-142-0592 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 250.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/23/2023 | Dec 30 1899 8:02AM
07/21/2023 | Alternative | RoutineScheduled | 175-14-0059 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 6"scum/ Microfast-4"sludge/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats, alarms and hydraulic unit functioning properly/ Counts: Pump-16158 ETM-3114/ Override-3/ Hand-68/ High-13 On-15m 36s Off-1h 49m/ Watermeter-055534.1/ No breakout or spongy areas on the drip field and dosing correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/19/2023 | Alternative | Follow-Up | C 800-16-0207 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Replaced the aerator motor (new serial # 22070570). Hooked up the pressure switch on the aerator. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/19/2023 | Dec 30 1899 12:00PM
09/16/2023 | Alternative | RoutineScheduled | SD-02-456 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | Puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/17/2023 | 02:00 PM
01/25/2023 |  | Routine/Scheduled | 228-02-1557 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | None |  | 6.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | Jan 1 1900 11:40AM
03/09/2023 |  | RoutineScheduled | 2008-143-0084 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Biomicrobics Microfast |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/09/2023 | 12:00 AM
04/28/2023 | Alternative | RoutineScheduled | 195-STS-26562 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","SludgeScum Accumulation","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/28/2023 | 12:00 AM
01/26/2023 |  | Routine/Scheduled | 234-155 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 9:30AM
06/01/2023 |  | RoutineScheduled |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-20-2 |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Distribution Pump Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 4.000000 | [11 empty] | Inspected | system is functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 11:00 AM
05/17/2023 |  | RoutineScheduled | 2107-05-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES |  |  | 7.000000 | 6.900000 |  |  |  | 05/17/2023 |  | 68.000000 |  |  | 95.000000 |  |  | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 06/15/2023 | 12:05 PM
02/14/2023 |  | Routine/Scheduled | 15-120-199AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | The treatment tank needs to be pumped | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/14/2023 | Jan 1 1900 8:41AM
07/03/2023 | Alternative | Follow-Up Component Maintenance | {FIPSCode}-STS-78640 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Repaired airline on FAST unit. Drip field is OK, no wet spots. Media starting to clog, will check in a month. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 04:50 AM
08/11/2023 | Alternative | RoutineScheduled Component Maintenance | 109-STS-31651 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/01/2023 | Alternative |  | 154-17-0220 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | EZ Treat | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/28/2023 |  | RoutineScheduled | 181-10-0083 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin filters were both cleaned. The controls were operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 09:20 PM
03/13/2023 | Alternative |  | {FIPSCode}-STS-17776 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Frank | Robinson | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/29/2023 | Alternative | Routine/Scheduled | 16-118-0054 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Multiflo FTB |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/29/2023 | Dec 30 1899 5:20PM
12/04/2023 | Alternative | RoutineScheduled | 06-184-5005 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/04/2023 | 12:00 AM
02/27/2023 |  |  | 099-18-0047 SRSA | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
10/04/2023 | Alternative | Routine/Scheduled | 053-STS-10251 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | Dec 30 1899 12:57PM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0101-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. 10 psi. HL-997, LL-14, OVERRIDE-0. Small leaks on risers but customer said he doesn't get any alarms. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
06/02/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
01/26/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 01/26/2023 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected | Do not flush wipes into system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
05/11/2023 |  | RoutineScheduled | SWP-03-610 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | NA | Pungent | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment does not look good due to dirty sheets and system needing pump out, cleaned sheets, biotube filter and pump intake so it should help but tank needs pumping. Roots growing in through top seem of tank below RSV valve. Recommend to inspect dbox at time of repair. Will send proposal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
03/28/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
04/19/2023 |  | Routine/Scheduled | 07-160-0088 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 02:30 PM
09/20/2023 | Alternative | RoutineScheduled | 115-05-0384 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Other conventional maintenance performed | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 12000 | Biomicrobics Fast 2.5 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Group meeting with engineers and contractors to discuss the new school addition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/30/2023 | 09:30 PM
11/14/2023 | Alternative | RoutineScheduled | 2015-143-0180 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/18/2023 |  | RoutineScheduled | 179-15-0093-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | There are roots growing in the distribution box & top header line. We removed what we could be hand, but there are roots remaining that could be clogging the line and preventing water from flowing evenly to the drianfield lines. We recommend excavating by hand to remove roots and repair or replace the header line as necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
03/30/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 2-3 0-4 | 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 9.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 09:00 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-19098 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
04/25/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
09/20/2023 | Alternative | Routine/Scheduled | 166-07-188 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | 04:30 PM
04/20/2023 |  | RoutineScheduled | 177-18-0351-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
12/08/2023 | Alternative | Routine/Scheduled | 199-17-0034 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal Level 12" of sludge and 1" of solids Pulled and cleaned filter Root intrusion under riser Discharge/Pump Tank Condition of above Component Notes for above Component Normal Level All floats and pump are functioning properly however they are Aged Peat Moss Condition of above Component Notes for above Component Peat moss is holding water and is broken down Raked peat moss and the consistency of the Peat moss is very muddy Distribution Box Condition of above Component Notes for above Component Normal Level All seals intact Plastic distribution box above grade in good condition with 3 lines taking water Drain Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 12:04PM
02/08/2023 |  | RoutineScheduled | 179-14-0018-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Septic tank, Advantex RT tank and distribution box were pumped in conjunction with this inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
04/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/27/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-24675 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/27/2023 | 12:00 AM
08/19/2023 | Alternative | RoutineScheduled | 101-15-0397 | Albemarle | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Blue Ridge | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | Microfast |  | Pump | Pressure | Drip | Not Applicable | 85.000000 | ["BlowerCompressorAerator Operation"] | [] | NA | None | [15 empty] | Pumped Out |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/21/2023 | 09:05 AM
10/17/2023 | Alternative | Reportable Incident | 11-142-0304 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Replacement of Puraflo Biofilter in four Modules - includes: - Purchase & delivery of new Biofilter (specialty peat moss) - Pumping of Septic Tank - Removal of existing Biofilter using a specialty Vacuum Truck - Disposal of existing Biofilter - Installation of the new Biofilter | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | Dec 30 1899 9:46AM
09/09/2023 | Alternative | RoutineScheduled | 2060-98-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.600000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/11/2023 | 12:00 AM
02/17/2023 | Alternative |  | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
08/25/2023 | Alternative | Routine/Scheduled |  | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Trash tank - normal level - Aeration tank - normal level - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - Plastic - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | Dec 30 1899 12:45PM
02/15/2023 |  |  | 179-STS-89959 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Purasys | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
01/20/2023 |  | Routine/Scheduled | {FIPSCode}-STS-26549 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluetn screen serviced. Treatment Module - media drapes and spray grid serviced. Pump Tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | Jan 1 1900 8:45AM
03/15/2023 |  | RoutineScheduled | SP-05-439 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend scraping the Advantex sheets and pumping the tanks in conjunction with your 2024 inspection. We will also plan to replace a 3/4" ball valve in the Advantex module that is bent and difficult to open. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
07/19/2023 | Alternative | Routine/Scheduled | 234-15-230 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 12:35PM
05/19/2023 | Alternative | RoutineScheduled | SD-11-262 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches |  | 50.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation","Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/20/2023 | 08:00 AM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | 154-05-0330 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend removing the trees that are growing around the Septic Tank and Puraflo modules to prevent root intrusions. The peat in the Puraflo modules has settled but is still in good condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
07/18/2023 | Alternative | Routine/Scheduled | 234-17-462 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 10:00AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-87778 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, there is effluent coming to the ground surface in the dispersal area. We recommend contacting the Alternative Onsite Soil Evaluator (AOSE) who designed the system for further evaluation and repair options. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
02/20/2023 |  | Routine/Scheduled | 093-12-0043 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | Jan 1 1900 10:49AM
05/07/2023 | Alternative | RoutineScheduled | 001-STS-92807 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJI CLEAN |  | Pump | Pressure | Mound | UV | 600.000000 | [] | [] | [18 empty] | EVERYTHING WORKING AS IT SHOULD. CLEANED HIGH PRESSURE FILTER. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | 12:50 PM
09/28/2023 | Alternative | Routine/Scheduled | 03-160-0298 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 11:15 AM
08/10/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | [9 empty] | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | Replace Peat Moss in 5 Pods | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/31/2023 | Dec 30 1899 4:20PM
04/20/2023 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
02/23/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
07/21/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-87490 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Level Sensor Operation" ,"Distribution Pump Operation" ,"Septic Tank Baffles" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Two part septic tank needs to be pumped out due to sludge levels. Homeowner called pumper to pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
06/27/2023 | Alternative | Routine/Scheduled | 03-120-0371A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump tank - float sensors, pump and controls operating. Dbox - Intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | Dec 30 1899 10:45AM
02/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | All tanks need pumped out including the advantex. The sheets need cleaned and the botton of advantex needs cleaned a lot of sludge | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/21/2023 |  | Routine/Scheduled | 13-172-0059A | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/21/2023 | Jan 1 1900 4:08PM
03/29/2023 | Alternative | RoutineScheduled | 166-18-0156 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced UV blub & ballast. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1125 | septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/24/2023 |  | Routine/Scheduled | 234-14-71 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/24/2023 | Jan 1 1900 10:45AM
10/19/2023 | Alternative | RoutineScheduled | 109-05-0323 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Delta, DF Series |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. 4" solids crust and 8" of solids in the bottom of treatment unit. 10" of solids in discharge pump tank. Flushed drip manifold spin filter. Removed drip tubing air releases and flushed. Cleaned blower air filter. Adequate aeration. Excellent treatment quality. The septic tank, treatment unit and discharge pump tank should be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 07:03 PM
02/03/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2437 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | Jan 1 1900 8:20AM
11/30/2023 | Alternative | Routine/Scheduled | 02-160-0414 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/30/2023 | 03:00 PM
11/10/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-25848 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Distribution Pump Operation" ,"Control Operation"] | ["Disinfection" ,"Distribution Pump Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | On site for annual inspection and to investigate reported alarm. UV panel was alarming. Replaced burnt out uv lamp, cleaned sleeve, and rinsed housing. High level count at 7. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
08/28/2023 | Alternative | RoutineScheduled |  | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Blue Ridge | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 2000 | Multiflo | Multiflo | Gravity | Gravity | Discharge |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [8 empty] | 08/28/2023 | Sample Chamber | 33.000000 | 6.600000 |  | 72.400000 | [5 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/07/2023 | 03:25 PM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/28/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower connection was repaired. System should return to normal operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/04/2023 | Alternative | Follow-Up | SD-02-805 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Replaced 4 remaining pressure regulators and bleach-flushed the drip tubing. Drip rates fully restored. Flush rates averaged 8 gpm (no record of flush rates at start-up). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
08/15/2023 | Alternative | RoutineScheduled | 08-160-0164 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 1.000000 | 1000 | ECOPURE |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Dispersal System Operation","SludgeScum Accumulation"] | YES | Septic | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 12:00 AM
08/29/2023 | Alternative | RoutineScheduled | 2016-143-0151 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/24/2023 | Alternative | RoutineScheduled | 033-07-0499-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 1000 | Biomicrobics MicroFast |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","BlowerCompressorAerator Operation","Control Operation"] | YES | [6 empty] | Recommend pumping in 4-5 years | [9 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 01:20 PM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance | 177-11-0076-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | 07:22 AM
11/22/2023 | Alternative | Reportable Incident Component Maintenance | 179-16-0344-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Effluent Screens" ,"Control Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium" ,"Control Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Inlet side of RT tank was on high level due to clogged up pump intake and 1 bad spinner, took pump apart to get off the sheet fiber that was clogging it and replaced bad spinner. system out of high level after all the testing done. Cleaned septic filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
06/01/2023 | Alternative | RoutineScheduled | 109-STS-31219 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/20/2023 | 12:00 AM
02/14/2023 |  | RoutineScheduled | 179-18-0231-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | As noted previously, there is a wet area in the drip dispersal field. A follow up visit is planned in the spring. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/09/2023 | Alternative | Follow-Up | -STS-13565 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 |  | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] |  | Septic | Black | [14 empty] | Inspected | - completed initial inspection on 05-09-23, found non functional due to blower not working - 05-10-23 replaced blower onsite - tank needs to be pumped/cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/11/2023 | 12:00 AM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/07/2023 | Alternative | RoutineScheduled Component Maintenance | 2035-12-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity |  | UV |  |  |  | NA | Musty | Clear | 6.900000 | 23.100000 | [11 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
12/06/2023 | Alternative | RoutineScheduled | 177-STS-93267 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-0 0-0 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [17 empty] | Inspected | new system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 10:00 AM
05/01/2023 | Alternative |  | -STS-91701 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/24/2023 |  | RoutineScheduled | 177-06-0362-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/28/2023 | 12:00 AM
02/01/2023 |  | Routine/Scheduled | 550-STS-6497 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 |  |  |  | 01/24/2023 |  | 6.000000 |  | 700.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | Jan 1 1900 1:35PM
05/15/2023 | Alternative | RoutineScheduled | 154-05-0024 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
03/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | Dec 30 1899 11:23AM
02/06/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Aquarobic Mini Plant | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 02:17 PM
10/16/2023 | Alternative |  |  | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.420000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 12:35 PM
03/09/2023 |  | RoutineScheduled | 177-11-0116-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Drip rate on zone 2 dropped from 7.8 to 3.6 after replacing a failed check valve on zone one. Flush rate is still a little low, but may improve over time now that the check valve has been replaced. Replaced burnt out bulb for the atu panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
02/28/2023 | Alternative | Reportable Incident | 157-11-0015 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Advanced Septic |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | Distribution Pump Operation | [18 empty] | Pumped Out | System alarming - Pumped & serviced septic tank - effluent screen serviced. Pumped and serviced pump tank - float sensors, pump functioning - Control panel failed and was replaced - found fracture in sidewall of pump tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/01/2023 | 10:30 AM
06/07/2023 | Alternative | Routine/Scheduled | 17-142-0385 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Treatment Module - recirc - recirc pump, media drapes & spray grid serviced. Treatment Module - discharge - float sensors, pump and controls operating. Pumps to community pump station and absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 11:00AM
02/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/17/2023 | Dec 30 1899 10:44AM
05/03/2023 | Alternative | Routine/Scheduled | 136-12-0158 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Biofilter - 4 modules - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 06:45 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping the tank prior to next years inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 182-08-0092 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired air supply | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | 01:07 PM
07/28/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | 1 | [6 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/28/2023 | 12:00 AM
02/20/2023 |  | RoutineScheduled | S-04-111-0005 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Delta white water |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [16 empty] | Inspected | Called for realestate Inspection, Found the blower was operational, cleaned airfilter, checked sludge levels and arranged for Foutz to come out and pump the septic tank and remained of the pump tank. Reset Air level sensor operation as it has zeroed out. Pumped water to corrected level. Flushed draine lines and checked zoner valve for proper operation. All appears good. Replaced pressure gauge and system reads 45 psi when pumping, New blower installed last Fall 2022. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | Jan 1 1900 9:30AM
12/18/2023 | Alternative |  | 101-17-0587 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Stephen & Anne | Altizer | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/21/2023 | Alternative | RoutineScheduled | 171-15-0163 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | BioCoir |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Grease Trap first section - 1" crust, 12" in bottom. second section - 0" crust, 20" in bottom, good separation. Septic Tank first section - 0" crust, 8" solids in bottom, second section - 0" crust, 12" in bottom. Treatment Tank - 0" crust, 5" on bottom. Aeration portion - 0" on top, 6" on bottom. Clear effluent. Both aerators operational. Cleaned grease trap filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2024 | 07:03 PM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance | 175-13-0031 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Septic/recirc tank needs pumped out. A proposal will be sent to the owner to meet a local pumper on site for removal of the pump vault, biotube filter, etc to allow for a proper pump-out. Neither splice box has water in it, all floats working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
03/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The peat fiber is badly broken down and sandy Peat needs replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
11/02/2023 | Alternative | Routine/Scheduled | 151-18-0031 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level Not able to take sludge reading due to depth of tank -Discharge/Pump Tank: Normal level Not able to take sludge reading due to depth of tank Tested floats and pump all working as should -Peat Moss: Tipping bucket and dispersal trays intact Peat moss in good condition no standing water or puddling Raked out peat moss even No cracks or breaks in peat module No standing water in inspection port -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Pump pulled 9.5 amps All components working properly -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 01:32 PM
09/01/2023 | Alternative | RoutineScheduled | 175-16-0097 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 6"scum/ Microfast-3"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-1752 ETM-180h 53m On-5m 50s Off-11h 55m/ Peak-0/ High-15/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/01/2023 | Alternative | RoutineScheduled | 019-STS-27530 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Delta, DF Series |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 16" of accumulated solids in septic tank with a 2" solids crust. 18" of solids in the treatment unit. 10" of "fluffy" solids in discharge pump tank. Adequate aeration. No noticeable smell from treatment unit. Cleaned blower air filter. Septic tank and treatment unit should be pumped out before next rental season. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 07:03 PM
03/30/2023 |  | Routine/Scheduled | 235-17-112 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | Jan 1 1900 12:05PM
04/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 6"scum/ Microfast-12"sludge 0"scum ( May require pump out next year) Pump Tank-2"sludge/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-641 ETM-53h 4m/ Pump2-629 ETM-50h 34m/ Peak-4/ High-8/ No breakout or spongy areas on the LPD Pad Site and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled | 115-11-0043 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 2.000000 | 3000 | MultiFlo ATU |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [16 empty] | Inspected | Main Home-#1- Sludge level-1/2" scum-12" sludge in Septic tank - Guest house septic tank trace scum and 10" sludge trace- Treatment tank scum layer 3-4" thick may want to pump off the deck scum soon using a shop vac. and pour into - Pump Tank - 12in sludge- has good aeration and clear effluent on top - Alarm good, Pump operational - Flushed drip system and cleaned spin filter, 24PSI observed on pressure gauge going to drainfield. 2,074 pump cycles since last year, this years pump count reading 28357 vs 26283. Pump run time, 103,508min vs 95408 min on meter. total 8100 min since last year, about 135 Hrs. drainfield cut by owner and no leaks observed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
01/05/2023 |  |  | {FIPSCode}-STS-12380 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Cloverleaf Environmental Consulting, Inc | 1942001135 | Robert | Charnley | [9 empty] | [] | ["SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | 12:05 PM
04/20/2023 |  | RoutineScheduled | VAG408203 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.340000 |  |  | 0.510000 |  | 04/20/2023 |  | 2.000000 |  |  | 1.000000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/15/2023 | 12:00 AM
05/03/2023 |  | Routine/Scheduled | 2018-143-0156 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1060 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter cleaned. Spin filter and drip field flushed. Manifold flushed. System was in high level upon arrival. Was operating normally and had caught up when we left. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/03/2023 | 11:34 AM
05/12/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Repaired electrical junction box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/30/2023 | 10:30 AM
10/04/2023 | Alternative |  | 177-STS-90572 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
01/06/2023 |  | RoutineScheduled | 132-18-0080 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled | 03-125-034 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/27/2023 | 12:00 AM
05/18/2023 |  | RoutineScheduled | 003-STS-32956 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Pressure | Discharge | UV | 450.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0581 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Replaced the element for the blower canister filter and cleaned the air pre-filter. Filterbed vent pipe was broken at the inlet side. Removed broken pipe remnants from hub connection and glued old pipe back in place. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
10/05/2023 | Alternative | Follow-Up Component Maintenance | 179-09-0114-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Step 20 EZ Treat pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
01/19/2023 | Alternative | RoutineScheduled | SD-06-281 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 175-10-0297 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | 7.500000 | 12.700000 | [11 empty] | Will be sent separately | Inspected | Needs Sign | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 10/16/2023 | 12:58 PM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Electrical junction box needs repair. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/30/2023 | 10:30 AM
02/03/2023 |  | Reportable Incident |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [6 empty] | Control Operation | [18 empty] | Pumped Out |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/29/2023 | 02:25 PM
02/27/2023 |  |  | 099-STS-92162 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
12/18/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Advantex | Pump | Pressure | Drip |  |  | [] | ["Control Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 36" overall liquid depth, 0 scum, 10"-12" of loose sludge. Effluent filter was clogged. Cleaned filter. Getting High water alarms on the recirculation. top two floats were not getting accurate reading all the time. Took cover off of junction box. It was full of water. Cleaned all water out and checked connections. Floats are working right now. Alarms, floats, pumps working, Field dry. All in working order when I left. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 11:00 AM
09/05/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-6168 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Processing tank - recirc - Media drapes, pump & spray grid serviced. U.V. Disinfection - serviced housing, replaced UV Bulb. Processing Tank - discharge - float sensors, pump and controls operating. DBox - Intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 10:45 AM
03/29/2023 |  | Follow-Up | 175-19-0029 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 03/29/2023 |  | 7.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
10/20/2023 | Alternative | RoutineScheduled | 061-18-345 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Microfast | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 08:55 AM
06/15/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
11/24/2023 | Alternative | RoutineScheduled | -STS-20150 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | ATU | Polishing Sand Filter | Pump | Pressure | Discharge | Chlorination | 500.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.200000 |  |  | 1.300000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/27/2023 | 12:00 AM
11/01/2023 | Alternative | RoutineScheduled | 151-18-077 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Laneview Environmental, LLC | 1942001775 | James | Boone | 2.000000 | 1000 gallona |  |  | Gravity | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/01/2023 | Alternative | Initial Visit | C-13-111-0059 | Botetourt | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | Delta Whitewater | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | [17 empty] | The system did not need to be pumped. The blower filter was pulled and cleaned. The control panel for the blower was also rewired to the permitted design. The blower pipe was broken at the unit due to backfill settling. The pipe was dug up and repaired. The effluent pump controls were operating as designed. There were no visible leaks in the leech field, however the field was grown up with briars and advised the homeowner that it needed to be cleared and mowed. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/08/2023 | Jan 1 1900 4:40PM
02/21/2023 | Alternative | Routine/Scheduled | 149-STS-10081 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Told homeowner in the next couple months will need to pump the treatment tank | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/21/2023 | Dec 30 1899 9:00AM
02/09/2023 | Alternative | RoutineScheduled | SD-12-381 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/23/2023 |  | Routine/Scheduled | 810-STS-4041 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 |  |  |  | 01/24/2023 |  | 6.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 4:00PM
09/08/2023 | Alternative | RoutineScheduled | 154-13-0133 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | ClearStream |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 11:45 AM
05/11/2023 |  | RoutineScheduled | 177-06-0620-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
05/09/2023 |  | Reportable Incident | 177-12-0102-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Owner called about high level alarm and tank overflowing. Disconnect switch at pump tank was turned off. Turned it back on and pump worked fine for several test cycles. Secured switch cover with a zip tie. Observed infiltration occurring at septic tank and pump tank inlet lids (buried wedge lids), and at riser joints on septic tank and pump tank. Effluent filter had been pushed out of its housing by the high water level. Extended handle a couple of feet so that the riser lid would keep it in place. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
10/23/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 12:40PM
04/28/2023 |  |  | 2013-143-0105 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
10/11/2023 | Alternative | Routine/Scheduled |  | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level, 3in of sludge and less than 1in of solids -Equalization Tank: Found at normal level, pulled and cleaned filter. Housing is stuck in place. Was unable to remove with out causing damage to housing. -Discharge/Pump Tank: Found at normal level, found less than 1in of solids and sludge. Tested floats and pump all working as they should. -Aeration: Found at normal level. 2in of sludge and less than 1in of solids and sludge. Removed aspirator and found the crows foot was missing so treatment wasn't happening. Cleaned debris off shaft and left power off to aspirator. -Control Panel: 120 volts. Audio and visual alarms working as they should. Pump pulled 5.5 amps -Distribution Box 1 (Surge Box): Found at normal level, plastic seals are deteriorated and roots are pushing in. Surge box is deformed. -Distribution Box 2: Found dbox at normal level. 3 lines balanced and taking water. Plastic seals are deteriorated and roots are pushing in. Bottom of dbox is cracked. -Drain Field: No signs of surfacing in drainfield area. Repair 10/13: -Installation of new crows foot on aspirator Everything working as it should | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 3:47PM
07/18/2023 | Alternative | Routine/Scheduled | 550-STS-6733 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/18/2023 | Dec 30 1899 8:15AM
08/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Gravity | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | Septic/atu tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/06/2023 | Dec 30 1899 4:30PM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air line from blower to the Whitewater unit appears to be obstructed. No aeration is occurring. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
02/14/2023 |  | Initial Visit |  | Lancaster | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | None | N/A | [17 empty] | AOSS - Initial Visit - system reported backing up into residence - homeowner reports they have NEVER had maintenance / service on the system to their knowledge. System requires full service - recommend pumpout - requires jetting of sewer line to clear clog in line. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/15/2023 | 12:15 PM
11/14/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 11:30 AM
08/23/2023 | Alternative | Pump-Out Only | 160-02-0499 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Pumped Out | - recommend septic be serviced more - recommend Advanced Environmental for alternative inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled Component Maintenance | 108-15-0020 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 4.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
04/03/2023 |  | RoutineScheduled | 175-06-0524 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Treatment looks great, effluent level normal, and neither tank needs pumped out yet. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
02/23/2023 |  | RoutineScheduled | 099-07-0123-SWT | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
05/05/2023 |  | Reportable Incident | 196-12-093 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed pump. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/01/2023 | Alternative |  | 033-13-0074-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/25/2023 | Alternative | RoutineScheduled | 113-STS-25897 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 01/25/2023 |  | 64.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2023 | 08:47 AM
05/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-16-0031-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
02/07/2023 |  | RoutineScheduled | 09-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Multiflo |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Auxiliary Filter","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/07/2023 | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Blower audible alarm not operating, let us know if want us to repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 08/23/2023 | 06:57 AM
01/27/2023 | Alternative | Routine/Scheduled | 136-02-117 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - effluent screen serviced. Aeration Tank - mixing present - compressor serviced. Pump tank - float sensors, pump and controls operating. DBox - intact - 2 laterals appear to NOT be accepting effluent! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 09:30 AM
06/14/2023 | Alternative | Routine/Scheduled | -STS-43171 | Roanoke City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | Attached Growth Medium | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Discolored | [16 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/14/2023 | Jan 1 1900 9:30AM
07/10/2023 | Alternative | RoutineScheduled | 147-06-0209 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 12:00 AM
02/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | NA | [17 empty] | Arrived onsite and found system in high water alarm due to trash in the return solenoid, corrected and system should get out of alarm in a couple of days. Septic-Tank-4"sludge 0"scum/ Microfast-4"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-23375 ETM-3850h 21m On-10m Standard Off-1h 42m Peak Off-1h 2m/ Peak-90 ETM-2269h 53m/ Watermeter-17,847,268/ No breakout or spongy areas on the drip/mound area. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20301 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/20/2023 | 12:57 PM
09/27/2023 | Alternative | RoutineScheduled Component Maintenance | 099-06-0337-SP | King George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | As noted previously, large trees have fallen on the drip dispersal system, damaging the manifold and drip tubing. We continue to recommend contacting a licensed installer to assist with his repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/01/2023 | 07:38 AM
01/18/2023 | Alternative | Routine/Scheduled | 151-07-0120 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Ecoflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 06:53 PM
11/21/2023 | Alternative | Reportable Incident | 157-16-0105 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Clearstream. Dog house light was on. Found air pump not working, diaphragms were busted. Customer approved to replace Air pump, confirmed Air is making it to the tank. Customer request invoice | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 03:37 PM
03/30/2023 |  | RoutineScheduled | 15-197-006 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Presby |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Dispersal System Operation","SludgeScum Accumulation"] | ["Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 12:00 AM
04/06/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | repaired alarm float | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
11/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | Dec 30 1899 3:10PM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92570 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 2.83 amps. Septic tank has no access point other than just a 4" cleanout, recommend to add a riser and lid to inlet side. Customer installed a charcoal filter on 6" vent for microfast tank, they understand the responsibility to maintain it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
12/04/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/04/2023 | Dec 30 1899 2:55PM
10/02/2023 | Alternative | Routine/Scheduled | 087-STS-6575 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/25/2023 | 01:36 PM
05/02/2023 |  | RoutineScheduled | 175-01-0722 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
01/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance | 107-19-0097 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 2000 | none | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | System Pumped Repaired audible and visual alarm | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
11/08/2023 | Alternative | RoutineScheduled | 015-STS-336262 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles"] | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles"] | [18 empty] | Baffle clogged | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/08/2023 | 12:00 AM
10/05/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok).Cleaned the disc filter and cleaned the UV light bulb. Changed the filter in the aerator. The Clearstream tank and septic tank needs to be pumped and cleaned. The timer is set to 8 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | Dec 30 1899 1:15PM
10/30/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.810000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/07/2023 | 02:30 PM
12/18/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles"] | ["Septic Tank Baffles"] | [18 empty] | Recent rain. Ground saturated more so in location of lower lines off of splitter box | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 12:00 AM
03/21/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 2 ends were fixed and all 7 buckets and lids are on. Septic system is in working condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/19/2023 |  | RoutineScheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Required pumping of primary tank. Please let us know if want us to handle | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/22/2023 | 11:15 AM
01/12/2023 | Alternative |  | 154-06-0241 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | EcoFlo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
09/11/2023 | Alternative | RoutineScheduled | 11-100-0290 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1500 | BIOCOIR |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | SLUDGE JUDGE 2-3" FROM BOTTOM 0" FROM TOP CLEANED FILTER CLEANED NOZZLES REHUNG FLOATS EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 11:30 AM
10/27/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 | Fiji, 1000 Pump Tank | Septic | Fuji Cen5 | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | 0 Scum And 6" of sludge, 4' overall in Settling tank in Fuji. Went through the flushing and cleaning steps in the Fuji Manual. Alarms, blower, floats, pump all working. field is dry. filters clean. 497 Events 71 hrs 59 Min run time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | 10:30 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/20/2023 | 01:07 PM
07/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | ["Control Operation","BlowerCompressorAerator Operation","Disinfection"] | NA | [7 empty] | 07/20/2023 | Sample Chamber | 28.000000 |  | 540.000000 |  |  |  | Attached to this report |  | Septic Tank-10"sludge 4"scum/ Microfast-12"sludge (Black color)/ Pump Tank-2"sludge/ Pump out highly recommend due to color and to prevent clogging/ Found contactor in the control box was faulty and replaced during inspection/ Blower air filter cleaned and blower working correctly/UV-Light sleeve cleaned and light functioning/ Controls, pump, floats and alarms now functioning properly/ Counts: Pump-7217 ETM-1940h 22m/ Peak-12 ETM-0h 0m/ High-12/ Watermeter-0,370,947.04/ No breakout or spongy areas on the drip field and dosing correctly/ High Fecal sample should improve after the sleeve cleaning. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/19/2023 | Alternative | Routine/Scheduled | 03-120-0104A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Water level normal. Inlet tee appears to be intact. Outlet tee appears to be intact. Riser is damaged. Due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. Due for pump out. Refill is required for proper operation and to prevent damage to components. -RSV: Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. Discharge pump has exceeded life expectancy. Discharge pump plumbing has exceeded life expectancy. Discharge floats are not properly secured and have exceeded life expectancy. Noted signs of groundwater infiltration within discharge riser -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Media lid safety support struts have failed. Media lid has been patched and is deteriorating. Media has exceeded life expectancy. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy -Distribution Box: Water level normal. Distribution box lid is damaged -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | Dec 30 1899 12:59PM
10/26/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 3:30PM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/06/2023 | Alternative | RoutineScheduled | 107-04-0696 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [18 empty] | repairs completed 7/20/23 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/20/2023 | 12:00 AM
01/23/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/27/2023 | 07:00 PM
12/09/2023 | Alternative | RoutineScheduled | 2042-97-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | SBR |  | Pump | Gravity | Discharge | UV | 250.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | NA | Musty | Clear | 6.600000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/12/2023 | 12:00 AM
11/15/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in both Clearstreams and cleaned the filter in the septic tank. Changed the diffuser in both Clearstreams and changed the filters in both aerators. The pressure switch on the aerator is not hooked up - it needs to be. The timer is set to 2 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | Dec 30 1899 11:35PM
01/04/2023 |  | RoutineScheduled | 175-17-0047 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | 179-16-0217-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-89365 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | The drip dispersal area should be mowed and maintained in a mowed condition. The plumbing & floats have mud stains. This can be a sign that tanks are leaking, and groundwater is getting into the tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
06/08/2023 | Alternative | Routine/Scheduled | 199-17-0030 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | Dec 30 1899 1:15PM
11/09/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | Dec 30 1899 1:50PM
07/26/2023 | Alternative |  | 12-125-066 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 |  | 3.460000 |  |  | 2.000000 |  |  | Will be sent separately |  | BOD: 3.46 TSS: 2.00 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/26/2023 | 12:00 AM
08/28/2023 | Alternative | Reportable Incident |  | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | NO | [17 empty] | AOSS Alarm Event - found compressor failed - no mixing present. Compressor replaced and system returned to normal operation. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/31/2023 | 07:15 AM
12/08/2023 | Alternative | Reportable Incident | C 800-16-0207 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a red light on for a month. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream. The aerator is not working - needs to be replaced. Replaced the timer (was burnt up - would not cut off) and replaced the alarm light bulb. The timer is set to 2 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/08/2023 | Dec 30 1899 2:15PM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/14/2023 |  |  | 16-172-0035A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/19/2023 | 12:00 AM
01/10/2023 |  | RoutineScheduled | 177-12-0121-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
05/31/2023 |  | RoutineScheduled | 175-85-0206 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | UV |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [7 empty] | 05/31/2023 | Sample Chamber | 6.000000 |  | 13.000000 |  |  |  | Attached to this report |  | Septic Tank-4"sludge 0"scum/ EZ-Treat Recirculation Tank-0"sludge/ Pump Tank-0"sludge/ No pump out needed at this time/ Recirc. pump intake cleaned/ Controls, pumps, floats and alarms functioning properly/ Counts: Discharge pump-969 ETM-145h 19m/ High-9/ Watermeter-55,371.79/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/23/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Level Sensor Operation"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | New Client -1st trip- Routine Inspection - Cleaned effluent filter which was very clogged. found 1-2" scum in specti tank and 16-18" sludge on bottom. Reccomend to pump, Recir zone of advantex for 12-14" sludge, Discharge zone found 14-16" fine sludge trace. Owner may pump entire system for improved operation. REfill tanks Asap with fresh water. Tested floats found dishcahrge 5th floats sending a week signal to the board casuing a delay in discharge pump operation, Found the 2nd float in the recirc zone not responding which turns on overide pumping cycles . May need new floats and wirenuts. Currently the system is working but will improve operationing with pumping and replacement of floats which we are scheduled to do soon | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/24/2023 | 09:30 AM
02/22/2023 |  | Routine/Scheduled | 085-STS-33248 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/22/2023 | Jan 1 1900 3:47PM
11/30/2023 | Alternative | RoutineScheduled | 182-01-0567 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | no return on either zones. Leak around the outside of enclosure surrounding zone valve. Scheduled for repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 11/30/2023 | 12:00 AM
01/10/2023 |  | RoutineScheduled | {FIPSCode}-STS-23367 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/10/2023 | 12:00 AM
02/28/2023 |  | RoutineScheduled | SWP-04-161 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. media level is about 5" below manifold and breaking down causing for sample box to Clogg and pond every year. Peat moss will need replacement next year. Vacuumed water out of sample box. Most pavers were removed from around risers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/25/2023 | Alternative | Routine/Scheduled | 136-18-0331 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 4.000000 | 4600 | Clearstream |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 75.000000 | [11 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 05:47 PM
12/18/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2024 | Dec 30 1899 11:49AM
03/14/2023 |  | Routine/Scheduled | 12-163-0101 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - at grade - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | Jan 1 1900 7:15AM
09/25/2023 | Alternative |  | 103-STS-101193 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned fitlers | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/06/2023 | Alternative | Initial Visit | 115-STS-101799 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok) Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the aerator. The timer is set to 2.5 minutes every 2 hours. Did not take sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 05:00 PM
03/01/2023 |  |  | 2016-143-0104 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
09/17/2023 | Alternative | RoutineScheduled | 047-18-002 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1000 | septic | Multiflo | Gravity | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/17/2023 | 01:55 PM
03/20/2023 |  | Routine/Scheduled | 19-1200148AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks |  |  | Aqua Klear | [6 empty] | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | [18 empty] | Air line broke due to settling. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | Jan 1 1900 3:00PM
12/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/24/2023 | Alternative | Routine/Scheduled | 16-174-0054 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/24/2023 | Dec 30 1899 9:39AM
08/22/2023 | Alternative | RoutineScheduled | 96-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 | [11 empty] | None | Clear | 7.200000 | 5.000000 | [14 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
08/10/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | NA | [17 empty] | 0 scum, Loose sludge 6" average. Blower working, Blower alarm working. Cleaned Blower filter. Pump tank clean, Alarm, Transducer, and pump working. Set pressure on return, cleaned spin filter, Walked field, Dry with no leaks. 420:26:09 hrs, 2353 events | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 11:50 AM
06/07/2023 | Alternative | Routine/Scheduled | 17-142-0341 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Treatment Module - recirc - recirc pump, media drapes & spray grid serviced. Treatment Module - discharge - float sensors, pump and controls operating. Pumps to community pump station and absorption field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 11:00AM
03/21/2023 |  |  | 2005-143-0319 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
09/01/2023 | Alternative | RoutineScheduled | 171-14-0270 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20-RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | [16 empty] | Inspected | Sludge levels-Septic Tank minimal scum- and 12" sludge - Recirculation zone of tank 6" sludge, Discharge zone of tank 12" sludge, Clear Effluent on top, Cleaned Effluent filter, tested float switches, ran in test mode. hosed off media and sprayer. good spray, RTU131464 EDW-WD-AX21 Rev 8.0 - Alarm disconnected by owner - 2534 hours on recirc pump 75,166 cycles 826.9 hours run time on discharge pump and 3584 cycles | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/30/2023 | 09:30 AM
03/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Great Falls Septic | 2705051738 | Joshua | Hott | 1.000000 | 2000 | Septic | Fuji System | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Pods are holding water. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
04/20/2023 |  | RoutineScheduled | 02-163-0248 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 6.000000 |  | Puraflo |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Auxiliary Filter"] | NA | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | 12:00 AM
11/21/2023 | Alternative |  | 033-19-0017-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Looking away from building - Aerator on left kept blowing fuses and would not run. Was not running upon arrival Aerator on right was running but it does not seem like the air was making it into the treatment unit. It was left off to not burn the motor with back pressure. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
04/14/2023 | Alternative | RoutineScheduled | 165-STS-333615 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 4.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired Discharge alarm float Multiple wet spots in drainfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/21/2023 | 03:35 PM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Fittings that connect blower to downshaft are damaged | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
06/08/2023 | Alternative | Routine/Scheduled |  | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 0.000000 | 0 | None | None | Pump | Pressure | Trenches | Not Applicable | 10000.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [17 empty] | Community Pump station to Community absorption Field. Tank appears to be intact. Both pumps serviced - control panel functioning. Teste stand-by generator - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | Dec 30 1899 1:00PM
08/21/2023 | Alternative | Initial Visit | 107-05-0500 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20 | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was pulled and cleaned. The textile sheets were sprayed off. The recirculating pump was pulled and sprayed off. The control panel was replaced due to a board malfunction. There were no visible leaks in the leech field. After the panel was replaced, the control and float switches were tested and are operating as designed. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/28/2023 | 02:55 PM
07/17/2023 | Alternative | Reportable Incident | 136-18-0059 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. The timer is set to 3 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | 11:00 AM
03/01/2023 |  | RoutineScheduled | 177-STS-87438 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [7 empty] | 03/01/2023 |  | 25.000000 | [5 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Two compartment microfast tank needs to be pumped out due to sludge levels. Homeowner to make arrangments. Ceder trees were planted to close to the first drainfield trench homeowner will move them. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
03/28/2023 |  | RoutineScheduled | 95-192-211 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/28/2023 | 12:00 AM
08/10/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-89709 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
05/08/2023 | Alternative | Reportable Incident | S 800-19-0041 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/08/2023 | Dec 30 1899 10:30AM
02/08/2023 |  | RoutineScheduled | 033-19-0062-SP | Caroline | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | YES | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | The Orenco UV lamp, cord, & control panel logo unit are not working. They appear to be damaged by a power surge or lightning strike. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | 12:05 PM
06/16/2023 | Alternative |  | 041-STS-260069 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","Recirculation Pump"] | YES | Pungent | Dark Brown | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 12:00 AM
03/02/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | Fast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 0 scum and 8" of sludge in septic tank none in pump tank. Pump, blower working. Drip field looks good with no leaks. 47445 Hrs and 2895 events. Filters are clean visual alarms working on blower and pump but audio alarms are not working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/02/2023 | 10:00 AM
12/18/2023 | Alternative | Follow-Up | 228-19-0052 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped and cleaned the pump tank and pumped the trash from the Clearstream tank. Replaced 1 vacuum breaker. Re-installed the weir filter. Need to go back in a to set the pressures, flush out the drainfield, and perform a draw down test. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/18/2023 | Dec 30 1899 12:00PM
10/23/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/23/2023 | Dec 30 1899 10:35AM
11/20/2023 | Alternative | RoutineScheduled | 175-14-0401 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Ecopod ATU | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-0"sludge 0"scum/ Ecopod ATU (E-75)-4"sludge 0"scum/ Pump Tank-4"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower is functioning properly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-638 ETM-95h/ High level-1/ Zone1- 8.4gpm/ Zone2- 8.1gpm/ On-10m Off-3h 54m/ Watermeter-0,365,563/ Design-750 gal. ADF-487 gal./ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/17/2023 |  | Routine/Scheduled | NYII-BCPSDM | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Jan 1 1900 1:07PM
03/17/2023 | Alternative | Reportable Incident | 157-07-0330 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Pumped septic tank and pump basin empty for repairs. Installed new control panel, and access riser on septic tank. Septic tank pumped empty - effluent screen serviced. PUmp tAnk - float sensors, pump and controls now operational. Peat chamber flooded - peatmoss failed - believe hydraulically overloaded from pump panel failure. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/20/2023 | 09:30 AM
03/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [17 empty] | Home owner has planted a large number of trees. We showed home owner the area not to plant. No trees are to be planted in reserve or on drain field are. Also told owner she should keep trees away from area at least 10 feet | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/15/2023 | Dec 30 1899 3:30PM
02/23/2023 |  | Follow-Up | 234-00-7645 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | Control Operation | Control Operation | N/A | [17 empty] | System serviced 02/10/2023 and issues identified that should be addressed. Scope of Work and estimate submitted for repair / replacement of components. Owner is complaining of audible alarm sounding regularly and requires that the Audible Alarm be disabled Permanently at this point in time. Audible alarm disconnected inside of control panel at owner's request and against Operator Advice. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/27/2023 | Jan 1 1900 7:15AM
10/05/2023 | Alternative | Routine/Scheduled | 17-163-0149 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: At normal level Has 1" of solids with 2" of sludge Pulled and cleaned filter -Recirculation Tank: At normal level Pump and floats working properly Pulled and cleaned pump and floats Pulled and cleaned UV and housing, uv working -Discharge/Pump Tank: At normal level Pulled and cleaned pump and disc filter Pump and floats working properly - Media Sheets: Sheets has some fog build up but cleaned up nice Brushed lateral -Control Panel: Working properly Visual and audible alarms working Recirc pulling 8.47amps Discharge pulling 7.59amps -Drip Field: Showing no signs of surfacing or blowouts | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 8:34AM
09/26/2023 | Alternative | Reportable Incident |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | -Installation of a slide-in Filter in Septic Tank -Pumping of 1000 gallons | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | Dec 30 1899 3:28PM
04/04/2023 |  | Routine/Scheduled | 145-STS-258463 | Powhatan | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Multiflo FTB |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/04/2023 | Jan 1 1900 11:38AM
05/17/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2863 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Gravity |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Jan 1 1900 11:00AM
04/03/2023 |  | RoutineScheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Effluent Screens" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Pressure Gauge Replaced Solution added to media | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
06/23/2023 | Alternative | RoutineScheduled | 19-142-0010 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Replaced blower 6-23-23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
07/07/2023 | Alternative |  | ST-04-246 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
04/25/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 2.000000 | 4000 | none |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Spring Inspection - Septic tank 3" scum 8" sludge - Pump tank 6" sludge pumps opperational - Septic tanks uptop hill #1 close to roar- 3+" scum and 8" sludge- Tank #2 1-2" scum and 4" sludge-Cleaned both biofilters- alarm good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
04/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1000 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Computer display on panel box is broken. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12:00 AM
07/14/2023 | Alternative | Routine/Scheduled | 234-15-113 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | Dec 30 1899 11:25AM
08/22/2023 | Alternative | RoutineScheduled | 179-18-0288-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-4 | 0-1 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 6.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 02:00 PM
09/01/2023 | Alternative | RoutineScheduled | 171-09-0026 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | [16 empty] | Inspected | Sludge level- minimalscum- 5-6" sludge in Septic tank - Pump tank sludge 4-5" trace , Peat drains well when broken up, No Ponding, roots noted in all 4 quadrants, turned peat all 4 quadrants. Pump run time 127:40:10 this year vs 122:48:19 last year Just about 5 hours running. - Doses 7529 vs 7242 last year totals 287 cycles -Alarm good, pump floats good and filter cleaned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/30/2023 | 09:30 AM
01/11/2023 |  | Reportable Incident | SP-04-100 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. Water was coming out of pump basin due to bad pump and floats. Breaker for pump was tripped. Replaced pump and both floats and system went back to normal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 03:56 PM
02/23/2023 | Alternative | Reportable Incident | SD-09-254 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Control Operation" ,"Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Panel alarmed a few days earlier and the owner shut off the control breaker because it alarmed several times and was disturbing his son's sleep. The panel's electronic alarm log confirmed that there were numerous high level alarms in the recirc tank on 2/1/23, none in the discharge tank. The field flush valve was not fully closing so effluent was circulating back to the septic tank. Drip rate was very low due to clogged spin filter, installed new filter. Rates went back to about what they were at last service October 2021. The field flush rate is substantially lower than design, needs further investigation. Inlet riser and lid on the recirc tank are damaged, need to be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
07/18/2023 | Alternative | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/27/2023 | 02:02 PM
12/07/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Septic tank was pumped last year. They didn't do a good job. Still has a thick scum layer, and is hard to get a good reading on sludge. Fast side has 12" of loose sludge, pump tank has 3" of sludge. Blower is running . Cleaned filter. Floats, Alarms, pump all working. Field is dry. 30 PSI return. Cleaned Filter. 340.32 Hr, 2002 Events. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | 11:00 AM
01/03/2023 |  | RoutineScheduled | 175-16-0098 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | J&G Septic Service |  | James | Kleindl | 2.000000 | 3000 | Mirco fast |  | Pump | Pressure | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/07/2023 | 09:00 PM
04/07/2023 | Alternative | Routine/Scheduled | C-07-111-0012 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/07/2023 | Jan 1 1900 10:15AM
01/30/2023 |  |  | 95-113-169 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/30/2023 | [7 empty] | Will be sent separately |  | BOD: BDL TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/30/2023 | 12:00 AM
06/16/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 |  | Microfast Drip |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | 12:00 AM
07/11/2023 | Alternative | Initial Visit | 093-STS-14718 | Southampton | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 39.000000 | [7 empty] | Received a call about it bubbling out of the tops. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. The filter in the septic tank was installed sideways - fixed. The timer is set to 2.5 minutes every 2.5 hours. Took initial BOD sample. NOTE : BOD sample was a tad high - system should function properly after service. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/11/2023 | Dec 30 1899 12:45PM
04/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
02/13/2023 |  | Reportable Incident | 181-08-0005 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | New Client/ New Owner -First trip- Owner said system not functioning for past 1.5 years - Was told it had a bad pump - Recirculation pump breaker was tripped on initial observation with high water in the treatment/septic tank. Upon running it in test mode the water level quickly corrected itself. Cleaned the media, the bio filter, the rsv and pulled out the recirc pump and cleaned it, PF300511 Pump - Water level was hgih enough to back feed to short out the circuit break and circuit board. Had corupt alarm logs in history. Replaced the circuit board with new. It maybe possible a water leak is casuing the system to flood during rain events and we will address this in the future if it appears to be an issue. Currently the system is working normal and in rest mode. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/01/2023 | 09:30 AM
06/28/2023 | Alternative | Routine/Scheduled | 033-STS-92026 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 12:30 PM
07/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92270 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Level Sensor Operation" ,"Control Operation" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [5 empty] | 07/17/2023 |  | 6.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. 3rd dialflow was set a little lower than others, adjusted it up for equal distribution. Blower 2.86 amps. R counts back to zero. Minor drip in septic tank riser (inlet) will let installer know. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
10/17/2023 | Alternative | Routine/Scheduled | 093-07-0086 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Annual Maintenance and Pump Out on 10/17: -Septic Tank: Above normal level due to dirty filter Tank is buried has lots of sludge and solids Customer approved pumping -Discharge/Pump Tank: Above normal level due to dirty spin filter Pump and floats working properly Mid seam is not sealed Splice box not sealed -Aeration: Has lots of suspended solids Customer approved pump and refill Pulled and cleaned aspirator -Control Panel: Both panels are working properly The discharge alarm toggle was left in off The aspriator switch was left in off Discharge pump pulling 10amps -Drip Field Headworks: No leaks in headworks box Pull and cleaned very dirty disc filter Drainfield has been blowing out in areas for about 3 months due to the pump being over ran because of the dirty disc filter. Need to re evaluate drainfield next year Goodmans pump out and refill (10/27): -Norweco. Met Goodman and Davis on site to pump and refill the septic and treatment tank. After refill I turned everything back on. Michael is approving the discharge tank re seal and splice box Repairs: -Entry of tank to reseal and parge seams and penetrations in tank to prevent further root intrusion and ground water infiltration. No guarantee on longevity. -Installation of a water-resistant SB4 Junction Box inside a Riser includes Conduit and Grommet Kit | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/30/2023 | Dec 30 1899 10:03AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/16/2023 | Alternative | RoutineScheduled | 179-STS-91626 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 14596.000000 | [] | [] |  |  |  | 6.950000 | 6.780000 |  |  |  | 10/30/2023 |  | 28.000000 |  |  | 16.500000 | 34.700000 |  |  |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 05:00 PM
06/28/2023 | Alternative | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 312.000000 | [] | [] |  |  |  | 7.790000 | 4.060000 | 10.000000 |  |  | 06/28/2023 |  | 3.000000 |  |  | 6.600000 | 45.210000 |  |  |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 02:00 PM
02/07/2023 | Alternative | Pump-Out Only | 136-17-0045 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | owner contacted office regarding have septic tank pumped out for Chesapeake Bay - no mention that system was Alternative. Pumped Septic tank ONLY - recommended service agreement and full service by technician on AOSS. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 08:33 AM
09/08/2023 | Alternative | Routine/Scheduled | SHUN-BCEN95 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | Dec 30 1899 8:46AM
12/12/2023 | Alternative | Routine/Scheduled | 095-STS-7040 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | Dec 30 1899 9:30AM
11/16/2023 | Alternative | Follow-Up | 193-STS-104958 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [29 empty] | Replacement of Puraflo Biofilter in Four Modules - includes: - Purchase & delivery of new Coconut Husk Biofilter - Pumping of Septic Tank - Removal of existing Biofilter using a specialty Vacuum Truck - Disposal of existing Biofilter - Installation of the new Biofilter - Replacement of existing spray grids - Voluntary Upgrade Permit through VDH required prior to installation This service includes distances up to 250' from where the Vacuum Truck can be staged. Additional charges may apply for distances that exceed 250' from staging area. The Septic Tank is to be pumped within 3 to 5 days of scheduled Biofilter replacement. The structural integrity of unit(s) will be evaluated upon completion of removal of existing Biofilter, and prior to installation of new Biofilter. If any unknown structural deficiencies exist that are too extensive to be repaired or pose a threat to the integrity and longevity of the remainder of the System, then the new Biofilter will not be installed, work will cease, and the Owner(s) will be notified as soon as possible. If additional services are deemed necessary for the proper operation of the System, the job will cease until the additional costs are agreed upon for the completion of the project. If the new Biofilter is not installed due to structural deficiencies, then the cost of pumping the Septic Tank, labor and equipment used to remove and dispose of the existing Biofilter totaling $5100.00 + any additional charges associated with staging distances exceeding 250' will be immediately due. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2024 | 03:51 PM
05/22/2023 | Alternative | RoutineScheduled | 171-07-0295 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Sludge level-2-3" scum layer on top-20" sludge on bottom in Septic tank - Pump tank 14" sludge, May want to arrange a pump out later this fall. Pump runs good. Cleaned RSV,Cleaned Biofilter,Brushed and flushed Manifold and sprayed off media. Float switches tested good, alarm tests good. has connected monitoring. Pump recirc run ttime 2435 hours and 96,830 Cycles. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
03/15/2023 | Alternative | RoutineScheduled | 159-10-015 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [null] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
01/03/2023 |  | RoutineScheduled | 179-09-0196-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | We recommend replacing the EZ Set spray nozzles. We also recommend remounting the control panel on the post. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 07:17 AM
06/13/2023 | Alternative | RoutineScheduled | 087-STS-6484 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
12/27/2023 | Alternative | RoutineScheduled |  | Madison | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Rappahannock-Rapidan | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 2.000000 | 4500 | Bio MIcrobics 4.5 | Bio Microbics 2.5 | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | 6.000000 | 6.600000 | [5 empty] | 9.000000 |  |  | 3.200000 | 41.600000 |  | Attached to this report |  |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/29/2024 | 12:00 AM
11/24/2023 | Alternative | Routine/Scheduled | C08-180-0021 | Roanoke City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/24/2023 | Dec 30 1899 1:45PM
12/20/2023 | Alternative | RoutineScheduled | 182-10-0274 | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | System requiring work on floats, leak in drip field, and digging off FAST tank for eval/obstruction. Pumping needed as well for septic | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/03/2024 | 12:00 AM
02/06/2023 |  | RoutineScheduled | 179-06-0255-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Broken lid on pump tank, replaced with new 24" EZ-set lid. Broken lid on 1 pureflow module, replaced. Septic tank needs pump out. Recommend to pumping pump tank as well due to sludge 4". Spoke to customer and he told us his going to call a company to get it done. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
11/13/2023 | Alternative | RoutineScheduled | 001-STS-92126 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | PURAFLO |  | Pump | Gravity | Pad | Not Applicable | 150.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE TEST REVEALED 4-5" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD MEDIA IN GOOD CONDITION | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/16/2023 | 12:45 PM
01/16/2023 |  | Routine/Scheduled | 093-02-0221 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced - recommend pumpout of processing tank - 1500 gallons + refill. Treatment Module - media drapes & spray grid serviced. Pump tank - float sensors, pump and controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | Jan 1 1900 7:30AM
03/07/2023 |  | Reportable Incident | 175-13-0085 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | [18 empty] | Service call only: Replaced faulty .75 Blower/ Replaced faulty peak float/ Tested system and now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
06/29/2023 | Alternative | Pump-Out Only | 128-04-283 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | NO | [16 empty] | Pumped Out | discharge tank pumped empty for storage - pending pump and control replacement. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/05/2023 | 07:00 AM
05/07/2023 | Alternative | RoutineScheduled | 001-STS-92104 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Pressure | Mound | UV | 450.000000 | [] | [] | [17 empty] | Pumped Out | PUMPED SEPTIC, REPLACED VENT ON AQUASAFE TANK. EVERYTHING WORKING GREAT. CLEANED HIGH PRESSURE FILTER. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 11:15 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance | 107-13-0186 | Augusta | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Ecoflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation"] | ["Dispersal System Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | pumping required-wipes peat moss bad-650 module alarm unplugged corrected | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/06/2023 | 08:40 AM
01/27/2023 |  | RoutineScheduled | 175-05-0269 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 3.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/29/2023 | 01:20 AM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance | SD-13-108 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
06/16/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Solenoid was replaced and the system appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/06/2023 | Alternative | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 2.000000 | 2500 | Microfast |  | Pump | Pressure | Drip | Not Applicable | 225.000000 | ["Attached Growth Medium","Auxiliary Filter","Distribution Pump Operation"] | ["Attached Growth Medium","Auxiliary Filter","Distribution Pump Operation"] | NA | [17 empty] | Replacement of pump and uncovered and cleaned out microfast unit | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/11/2023 | 11:00 PM
10/11/2023 | Alternative | Routine/Scheduled | 05-120-0206A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Inlet tee appears to be intact. Not due for pump out. -Recirculation Tank: Water level normal. Checked and confirmed recirculation pump is functioning properly. Flushed and cleaned recirculation pump. Checked and confirmed recirculation floats are functioning properly. Flushed and cleaned effluent screen. Recirculation pump has exceeded life expectancy. Recirculation pump plumbing has exceeded life expectancy. Recirculation floats have exceeded life expectancy. -RSV: Flushed and cleaned RSV. Checked and confirmed it's free of debris and functioning properly. -Media Sheets: Cleaned media sheets. Flushed and cleaned laterals. Flushed media module. Checked and confirmed spray height is good. Media has exceeded life expectancy. Media lid safety support struts have failed. -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Control panel has exceeded life expectancy. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 3:56PM
10/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 10/02/2023 | Sample Chamber | 4.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/29/2023 | Alternative | Reportable Incident | 124-STS-2379 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 2250 | 1250 | 1000 | Pump | Pressure | Pad | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Control Operation","Attached Growth Medium","Auxiliary Filter","Disinfection"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/29/2023 | 10:30 AM
11/13/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | [] |  |  |  | 7.850000 | 0.260000 | [14 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/15/2023 | 12:00 PM
05/15/2023 |  | RoutineScheduled | 2062-99-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 350.000000 | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 6.800000 |  |  | 2.100000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/18/2023 | 12:00 AM
12/21/2023 | Alternative | Routine/Scheduled | 157-12-0040 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Pumped and cleaned out the Clearstream tank and pump tank and pumped out the septic tank. The timer is set to 8 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | 01:00 PM
08/09/2023 | Alternative | Routine/Scheduled | 234-16-156 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 2:10PM
01/29/2023 |  | Routine/Scheduled | 053-STS-9957 | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/29/2023 | Jan 1 1900 11:30AM
02/10/2023 |  | RoutineScheduled | 181-00-0249 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The pump was operating as designed. The controls were operating as designed. There were no visible leaks in the LPD system. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/11/2023 | 01:15 PM
02/14/2023 | Alternative |  | 132-08-0097 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Jonathan | Elliott | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/14/2023 |  | RoutineScheduled | 175-07-0579 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 02:21 PM
01/18/2023 | Alternative | Routine/Scheduled | 151-19-0043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 06:57 PM
04/25/2023 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 |  |  | Pump | Pressure | Trenches |  | 600.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | 09:47 AM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/18/2023 | Alternative | RoutineScheduled | 03-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 4 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/18/2023 | 12:00 AM
05/04/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation"] | [18 empty] | 3' of liquid depth, 0 scum, and 4" of sludge in the septic tank. Pump tank clean. alarm, floats, and pump are all working. Peat moss and pods are in good shape, Draining well. Good flow through sample box to the d-box. Drainfiled is dry. 594 events, 6.57hrs on pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 11:00 AM
05/02/2023 | Alternative |  | 154-04-0144 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Marcie | Horree | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/17/2023 |  | Pump-Out Only | 234-13-32 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [8 empty] | N/A | [16 empty] | Pumped Out | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/17/2023 | Jan 1 1900 10:00AM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 107-06-0570 | Augusta | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | multiple leaks in drainfield not repaired, Let us know if you want this repaired Valve boxes, Discharge contactor, Recirc alarm float all repaired | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/06/2023 | 03:05 PM
12/28/2023 | Alternative | RoutineScheduled | 182-14-0268 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  |  |  | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles"] | ["Auxiliary Filter","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 12:00 AM
07/19/2023 | Alternative | RoutineScheduled | 047-16-116 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Advantex | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 07:30 AM
12/19/2023 | Alternative | Routine/Scheduled | 093-06-0223 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 12:30PM
04/12/2023 |  | RoutineScheduled | 179-18-0424-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 04:23 AM
08/13/2023 | Alternative | RoutineScheduled | SD-02-517 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic | Microfast | Gravity | Gravity | Discharge | Chlorination |  | [] | ["SludgeScum Accumulation","Septic Tank Baffles","Control Operation","Disinfection","BlowerCompressorAerator Operation","Attached Growth Medium","Auxiliary Filter"] | YES | Musty | Clear | 7.200000 |  |  | 1.060000 |  | 08/13/2023 | Sample Chamber | 2.000000 |  |  | 1.500000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/28/2023 | 08:30 AM
03/15/2023 | Alternative | RoutineScheduled | 159-02-404 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0275-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Grass was very high on drainfield. Needs to be mowed on a regular basis. Treatment looked very poor compared to past years. Homeowner will look into it. Possible use of scent beads or fabric softner. Pump tank needs to be pumped out due to sludge levels. Recommend recirc tank be pumped out as it is very close and will not make until next year and it had a lot more wipes in the tank compared to past years. Tanks are very far away from the house and pump out is not possible during the winter and spring months as truck will have to drive through the yard to pump out tanks. Proposal to be sent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
09/06/2023 | Alternative | RoutineScheduled | SD-07-85 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Effluent Screens","Attached Growth Medium"] | ["SludgeScum Accumulation","Effluent Screens","Attached Growth Medium"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 08:30 AM
01/17/2023 |  | Follow-Up | 179-15-0108-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite to disasemble components in recirc tank and assist pumper with proper pump out of the septic and recirc tanks. Reasembled components and refilled both tanks back to proper levels. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
11/13/2023 | Alternative | Routine/Scheduled | 800-05-0348 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | Dec 30 1899 3:25PM
06/28/2023 | Alternative | Routine/Scheduled | 234-13-368 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [13 empty] | Replaced aerator and diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | Dec 30 1899 8:20AM
06/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/28/2023 |  | RoutineScheduled | 153-STS-20260 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
05/23/2023 |  |  | 2013-143-0103 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
04/20/2023 |  | RoutineScheduled | 02-113-378 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/20/2023 | 12:00 AM
01/04/2023 |  | RoutineScheduled | 113-19-018 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 2.000000 | 1000 | Biomicrobics |  | Pump | Pressure | Drip |  |  | ["None"] | ["None"] | NA | Musty | Clear | 6.200000 | 6.400000 |  |  |  | 01/04/2023 | Pump Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/20/2023 | 12:00 AM
05/10/2023 | Alternative | RoutineScheduled | 115-07-0391 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | Septic Tank | Advantex AX20 | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | ["Effluent Screens"] | ["Control Operation","Effluent Screens","SludgeScum Accumulation","Level Sensor Operation"] | YES | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 11:30 AM
05/22/2023 | Alternative | RoutineScheduled | 182-15-0166 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Need to maintain vegetation around system components and drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | 12:00 AM
06/06/2023 | Alternative | Routine/Scheduled | 151-04-267 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. BioFilter - 4 modules - peat moss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 08:30 AM
03/21/2023 |  | RoutineScheduled | 027-STS-17468 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens","Control Operation","Auxiliary Filter","Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/21/2023 | 12:00 AM
10/03/2023 | Alternative |  | SWP-03-727 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
06/20/2023 |  | RoutineScheduled |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | FAST | Gravity | Pressure | Drip | Not Applicable |  | [] | [] | YES | [17 empty] | Repair | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/29/2023 | 08:55 AM
04/24/2023 |  | Follow-Up | 228-12-0024 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [17 empty] | Replaced UV control panel and bulb | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/24/2023 | Jan 1 1900 8:00AM
06/23/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip |  | 150.000000 | ["Auxiliary Filter","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/07/2023 | 09:16 AM
03/01/2023 |  | RoutineScheduled | 2102-05-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  |  |  | NA |  |  | 7.900000 | 1.800000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 03/31/2023 | 12:26 PM
12/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Disinfection","Level Sensor Operation","SludgeScum Accumulation"] | ["Disinfection"] | NA | [17 empty] | Septic Tank-6"sludge 3"scum/ Microfast ATU-12"sludge/ Pump Tank-1"sludge/ Found the blower outlet pipe was broken and requires repair/ Peak float is faulty and needs replacement/ Owner stated the repairs will be done by someone else/ Blower air filter cleaned/ UV-Light sleeve cleaned and functioning properly/ Counts: Pump-2562 ETM-622h 30m/ Peak-128 ETM-161h 3m/ High-19/ Watermeter-400,170.41/ No breakout or spongy areas on the drip field. We returned on 12/13/2023 to make the repairs. Fixed the broken air line for the blower/ Replaced the faulty peak float. All repairs were completed. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0270 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
04/18/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 350 | BioMicrobics -Fast |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Septic Tank 5" scum, 30" Sludge In Fast Septic zone, Fast Side port 24" Sludge, will need pumping this year. Owner called Foutz- Good aeration observed in treatment tank. Cleaned Airfilter on blower motor. System was running good and near time to pump out. New blower control box works and alarm is good. Checked the D-Box and removed minor dead roots in main pipe by hand. Blower which is operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 PM
05/08/2023 |  | Routine/Scheduled | 234-18-390 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | Jan 1 1900 12:20PM
11/15/2023 | Alternative | Routine/Scheduled | 07-160-0308 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 141.000000 | None | ["Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | 12:00 PM
09/12/2023 | Alternative | Routine/Scheduled | 14-160-0108 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 233.000000 | SludgeScum Accumulation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 01:45 PM
01/10/2023 |  | Routine/Scheduled | AFES-AC9KPC | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 11.000000 |  | 20.000000 | [5 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The timer is set to 12 minutes every 1.5 hours. Took the 5 year BOD and Fecal samples. NOTE : BOD was a tad high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | Jan 1 1900 2:00PM
12/14/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Type of System Alternative Type of AOSS System Ecoflo Septic Tank Condition of above Component Notes for above Component Found at normal level, 6in of sludge and less than 1in of solids. Pulled and cleaned filter. Filter style has been discontinued but still functional. Minor cracks in he filter itself. Riser showing signs of leaking. Discharge/Pump Tank Grinder (basement) Condition of above Component Notes for above Component Found at normal level, on off float working as it should pump pulled 9.2 amps. No alarm present. Pump has met life expectancy. Peat Moss Condition of above Component Notes for above Component Tipping bucket and trays are in working order. Raked out peat on both sides. Peat is holding water, some compaction and deterioration. Need to reevaluate neat next year. 2 spots where repairs have been done previously. No signs of leaking Distribution Box Condition of above Component Notes for above Component Found at normal level. 5 lines. 4lines full of roots. Roots coming in around inlet pipe and under lid. Drain Field Condition of above Component Notes for above Component No signs of surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 10:04 AM
01/30/2023 | Alternative | RoutineScheduled | SD-04-577 | Culpeper | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | The blower is not working and should be replaced. The EZ Set riser lid on the septic tank should be replaced. We also recommend pumping the drip pump tank due to sludge accumulation in the tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | 12:05 PM
01/16/2023 |  | RoutineScheduled | 10-172-0019AR Disc | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Bobby's septic inspections LLC | 1942001548 | Robert | Burnett | 1.000000 | 1000 | advantex |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Effluent Screens","Recirculation Pump","SludgeScum Accumulation","Level Sensor Operation","Septic Tank Baffles"] | ["Attached Growth Medium","Control Operation","Disinfection","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] |  | None | Clear | 6.700000 |  | 5.000000 | [12 empty] | Replaced UV unit and control panel. UV is now operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | Jan 1 1900 2:00PM
04/05/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | UV |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
04/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/13/2023 |  | RoutineScheduled | 15-192-042 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/13/2023 | 12:00 AM
01/16/2023 |  | Routine/Scheduled | 199-15-0017 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. dBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | Jan 1 1900 8:00AM
02/21/2023 |  | Routine/Scheduled | 093-14-0106 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | Jan 1 1900 8:25AM
12/21/2023 | Alternative | RoutineScheduled | 14-118-0045 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 3.000000 |  | Aqau Klear |  | Pump | Gravity | Trenches |  |  | [] | ["Control Operation","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | 12:00 AM
05/18/2023 |  | RoutineScheduled | 101-18-0057 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Pressure | Drip | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
06/01/2023 |  | RoutineScheduled | {FIPSCode}-STS-70012 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-20-2 |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Distribution Pump Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 4.000000 | [11 empty] | Inspected | system is functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 11:00 AM
03/07/2023 |  |  | 2015-143-0138 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EZ Treat | [6 empty] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/08/2023 | 12:00 AM
01/26/2023 |  | RoutineScheduled | 179-14-0309-STWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
07/06/2023 | Alternative | RoutineScheduled | 15-100-0288 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Gravity | Pad | UV | 450.000000 | [] | [] | [18 empty] | EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 01:55 PM
05/01/2023 |  | RoutineScheduled | SWP-03-776 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The riser on the Pump Tank is leaking. This can cause your system to have to handle excess water when rainwater leaks into the tank and result in high level alarms. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/12/2023 | Alternative | Routine/Scheduled | 228-12-0533A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 9:10AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/23/2023 |  |  | 124-STS-2379 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | Virginia Soils Inc, dba VSI Supply / AG Onsite | 1942001291 | Archie | Arnold | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
07/24/2023 | Alternative | RoutineScheduled | 033-06-0011-ST | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 0-3 | 0-0 | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 5.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 02:00 PM
02/21/2023 |  | RoutineScheduled | 04-197-A1 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | 12:00 AM
09/26/2023 | Alternative | Initial Visit | VAG408461 | Rockingham | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | ["Disinfection"] |  | None | Cloudy | 7.590000 |  |  |  |  | 09/26/2023 |  | 55.000000 |  |  | 59.200000 |  |  |  |  | BOD and TSS over the limit. We replaced the UV bulb and made some other adjustments. Will return and resample BOD and TSS and sample for Fecal Coliform. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | 10/13/2023 | 04:15 PM
04/25/2023 | Alternative | Reportable Incident | PPIE-AJFN8F | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | On arrival the alarm was muted and the light bulb was burnt out. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Replaced the alarm light bulb. Meet with the pumping company and pumped out the Clearstream tank and pumped out the septic tank. The timer is set to 3 minutes every 2 hours. Could not take the 5 year BOD lab due to the aerator not working on arrival. Disconnected the pressure switch on the aerator due to the pumping. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/25/2023 | Dec 30 1899 9:00AM
12/07/2023 | Alternative | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [16 empty] | Pumped Out | Heavy sludge in discharge and treatment tank. Pumped and cleaned both tanks. Refilled tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/12/2024 | 11:01 AM
04/13/2023 |  | RoutineScheduled | 02-192-142 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 12:00 AM
07/26/2023 | Alternative | RoutineScheduled | 05-100-0381 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | [] | [] | YES | [16 empty] | Pumped Out | REPLACED FUSE IN ALARM PUMPED SEPTIC PEAT LOOKS GOOD EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 10:30 AM
11/30/2023 | Alternative |  | SD-03-603 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/14/2023 | 12:00 AM
02/03/2023 |  | Routine/Scheduled | 09-120-00334R | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Hoot |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump tank - sensor probe, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | Jan 1 1900 11:45AM
05/01/2023 |  | Routine/Scheduled | 228-17-0384 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | Jan 1 1900 10:20AM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Hydraulic unit needs replaced due to failed components that are now discontinued. Proposal sent last year but has not been approved to allow repair to occur. System will continue to fail inspections and always has risk up backup in home until repair is completed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/20/2023 | Dec 30 1899 2:30PM
03/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/20/2023 |  | Initial Visit | 12-120-0218AR Disc | Chesterfield | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Discharge | UV | 450.000000 | SludgeScum Accumulation | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - NPDES Discharging System - Initial Visit - previous service provider noted as Gentry Septic Tank Service (out of business) Primary septic tank - normal level - effluent screen serviced - recommend pumpout. Processing Tank - Recirc - recirc pump, media drapes & spray grid serviced. Processing Tank - U.V. operational - bulb and housing serviced. - Outlet "baffle" is fractured Discharge point clear of debris, signage present. Requires lab annual lab sampling. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/23/2023 | Jan 1 1900 8:00AM
08/16/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Gravity | Gravity | Discharge | UV | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. U.V. - bulbs and housing serviced. Discharge point clear of debris, free flowing , rodent guard in place | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/21/2023 | Dec 30 1899 8:00AM
01/26/2023 |  | Reportable Incident |  | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced damaged distribution box with new 8 port concrete DBox. Spliced to existing Conveyance Line Spliced to existing header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/30/2023 | 06:30 AM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Septic tank needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/06/2023 | Dec 30 1899 9:34AM
03/02/2023 |  | RoutineScheduled | 175-03-0999 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
02/06/2023 |  | RoutineScheduled | 133 08 0035 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | [] | [] |  | None | Clear | [5 empty] | 02/06/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 07:55 AM
02/21/2023 |  | RoutineScheduled | {FIPSCode}-STS-18653 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Septic Tank to Norweco ATU | Norweco ATU to EZ-Treat Recirculation Tank | Pump | Gravity | Discharge | UV |  | ["Disinfection"] | ["Disinfection"] | NO |  |  | 7.700000 |  |  |  |  | 05/04/2023 | Sample Chamber | 25.000000 |  | 13.000000 | 124.000000 |  |  | Attached to this report |  | Septic Tank-6"sludge 0"scum/ Norweco-0"sludge 0"scum/ EZ-Treat-3"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ Salcore UV-Light & ballast is faulty and require replacement/ Controls, pumps, floats and alarms are functioning properly/ Recirc. pump intake cleaned and media in good condition. Returned on 4/13/2023 to install a Jet UV-Light to replace the faulty Salcore light, tested and functioning correctly. Returned on 5/4/2023 for the samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/09/2023 | Alternative | RoutineScheduled Component Maintenance | SD-10-49 | Culpeper | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic/ATU tank due to scum and sludge accumulation in the tank. As noted previously, the drip dispersal system should be mowed and maintained in a mowed condition. Roots are preventing the drip dispersal system from building pressure and operating properly. If corrections are not made, we may not be able to assist you in the future. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/01/2023 | 07:38 AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0043-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Drip system is a continuous flush design and therefore impossible to accurately measure drip rate (unless return line was temporarily shut off) or flush rate. Water level dropped by approximately 50 gallons during 1 complete cycle, so dose is correct. Treatment looks very good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0485-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [7 empty] | 07/26/2023 |  | 10.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
02/23/2023 |  | Reportable Incident |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches |  | 450.000000 | Dispersal System Operation | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | COSS - Maintenance - GMP2018-02 Replaced degraded DBox with new 8 port concrete DBox. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/27/2023 | 06:30 AM
08/31/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-545 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Level Sensor Operation"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Level Sensor Operation"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Septic tank filter was clogged up due to tampons and fabric rags, recommended to get tank pumped and to be careful with what goes down the drain. fluffed media. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
07/19/2023 | Alternative | RoutineScheduled | 02-163-0438 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Advantex |  | Gravity | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Control Operation","Level Sensor Operation","Recirculation Pump"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | 12:00 AM
06/22/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Pressure | Drip | UV |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank-4"sludge 0"scum/ EZ-Treat Recirc. Tank-2"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Recirc. pump intake cleaned and media in good condition/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump-1811 ETM-3h 48m/ High-24/ Peak-27 On-2m 30s Off-24m/ UV-Light sleeve cleaned and working correctly/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/22/2023 |  | Initial Visit | 067-STS-38843 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Control Operation"] | ["Control Operation"] | NA | [17 empty] | Initial startup inspection visit. Programmed timers. Tested floats, pumps and alarm. Verified that all aspects of the installation were complete and functional. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 07:03 PM
03/07/2023 |  | RoutineScheduled | 06-125-086 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Auxiliary Filter","Disinfection","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 3 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/07/2023 | 12:00 AM
12/11/2023 | Alternative | RoutineScheduled | 13-183-116 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/11/2023 | 12:00 AM
10/18/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
05/25/2023 | Alternative | Reportable Incident | 17-118-0020 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm - aerator not working. Serviced system. Checked the pump, panel, and floats (ok). Installed an aerator rebuild kit and changed the filter in the aerator. The septic tank needs to be pumped out as well as the Clearstream tank. The timer is set to 4 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/25/2023 | Dec 30 1899 1:45PM
06/30/2023 | Alternative | RoutineScheduled | -STS-43154 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | AdvantexAX20 | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The RSV was pulled and cleaned. The textile sheets were sprayed off. The effluent filter was pulled and cleaned. The recirculating and discharge pumps were both pulled and cleaned. The spin filter was cleaned. The controls were operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | Jan 1 1900 9:15PM
09/12/2023 | Alternative | RoutineScheduled | 128-06-0312 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | checked sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/25/2023 | Alternative | Reportable Incident | 166-03-172 | Northumberland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NO | [17 empty] | System evaluation - Complaint - Rental Property - found EcoFlo mound failed and surfacing on front side - control panel timers operating properly - just had full service conducted 05/31, peatmoss reported as being in fair condition, and no notes regarding shell fracture, etc. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 07/27/2023 | 07:30 AM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-15 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank and aerobic treatment unit due to scum and sludge accumulation in the tanks. We also recommend replacing the headworks box heater, and further testing the drip dispersal system to check area you identified as being wet. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
05/20/2023 |  | Initial Visit |  | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 | 1000 | Clearstream 600N |  | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation","Other"] | ["Level Sensor Operation","Other"] | NA | None | Clear | [15 empty] | Found clarifier zone high level float not working, aerator air psi alarm not working, and control panel partially not working. Replaced high level float and installed new control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/20/2023 | 12:00 AM
12/01/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:30 AM
03/09/2023 |  | RoutineScheduled | 175-06-0172 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
03/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Microfast blower filter was missing. It was replaced. Bell cap for the hydraulic unit filter had broken. It was replaced. System appears to be functioning as designed now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/21/2023 |  | Routine/Scheduled | 183-STS-10357 | Sussex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/21/2023 | Jan 1 1900 11:00AM
03/07/2023 |  | RoutineScheduled | 12-197-099 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Clearstream |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Auxiliary Filter","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","Effluent Screens","Dispersal System Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 12:00 AM
09/27/2023 | Alternative | Initial Visit | 077-STS-36767 | Carroll | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1000 | Aqua Safe 500 |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | ["SludgeScum Accumulation","BlowerCompressorAerator Operation","Other"] | NA | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | Dec 30 1899 3:00PM
04/05/2023 |  | RoutineScheduled | 177-14-0117-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
10/02/2023 | Alternative | Routine/Scheduled | 11-120-0365AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Water level normal. Outlet tee appears to be intact. Not due for pump out -Discharge/Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Flushed and cleaned discharge pump. Checked and confirmed discharge floats are functioning properly. -Aeration: Water level normal. Not due for pump out -Air Pump/Blower: Checked and confirmed aerator is functioning properly. Cleaned aerator shaft -Control Panel: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. -Distribution Box: Water level normal. Structural integrity of distribution box appears to be intact. Two of the three header lines are clogged with roots -Drain Field: Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 1:03PM
02/13/2023 |  | Reportable Incident | 228-15-0385 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/13/2023 | Jan 1 1900 9:00AM
09/07/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 3.000000 |  | septic | puraflo | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [17 empty] | 0 scum, 2" of sludge. Filter clean., Peat looks good still fluffy & draining well. Both pumptanks are clean with everything working. Field is dry. Septic pump 9056, 120.43 hrs, Sand pump11907, 1660 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 12:00 PM
09/27/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/27/2023 | Dec 30 1899 10:00AM
05/15/2023 | Alternative | Routine/Scheduled | 136-08-0014 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Aeration Tank - normal level - NO mixing present - compressor diaphragm fail. Pump Tank - float sensors, pump and controls operating. DBox - Plastic - | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/30/2023 | 06:30 AM
10/12/2023 | Alternative | RoutineScheduled | 166-04-446 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 |  |  | Pump | Pressure |  |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 12:00 AM
01/17/2023 |  | Routine/Scheduled | 06-120-0682A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/17/2023 | Jan 1 1900 9:08AM
12/27/2023 | Alternative |  | 04-177-1322 | Pulaski | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 2.000000 | 1000 | ECOFLO |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Septic | Cloudy | [14 empty] | Inspected | - peatmoss needs to be replaced - tipping tray needs to be replaced - insulation cover board needs to be installed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/28/2023 | 12:00 AM
05/18/2023 | Alternative | Reportable Incident | 073-STS-102617 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | COSS - Repair Permit Pumped empty, crushed and removed existing septic tank. Installed new 1250 gallon mid seam septic tank Installed new 4" PVC conveyance line Installed new 8 port concrete distribution box. Installed new 4" PVC header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 12:00 PM
02/15/2023 |  | RoutineScheduled | 2018-143-0158 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
05/09/2023 | Alternative | RoutineScheduled | 001-STS-92345 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 300.000000 | [] | [] | YES | [17 empty] | EVERYTHING WORKING AS IT SHOULD. RAKED PEAT. PEAT LOOKS GOOD. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/10/2023 | 09:45 AM
05/16/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo ATU |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Sludge level-Septic tank 2" scum layer. 16" sludge, Treatment tank 3-4" scum on deck and 8" sludge trace on bottom. Reccomend to pump out next year. Maybe after visit.. Discharge pump tank has 8" sludge, Pump is operational. alarm float is good. The socks and septic were pumped out 3 years ago by Foutz septic and may need pumping next year. Clear Effluent , spayed down scum levels in riser. keep soaps to minimal use to prevent sudsing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
09/14/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 |  | Septic | MicroFast | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation"] | NA | [7 empty] | 09/14/2023 | Pump Chamber | 25.400000 | [5 empty] | Attached to this report |  | 3' Liquid Depth, 0 scum, 3" of sludge, Pump tank clean, blower, floats, alarms working . leak in drip field . Repaired. 138 events, 14h30min run time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 02:00 PM
01/26/2023 | Alternative | Initial Visit | 159-10-124 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - FOIA requested. Primary septic tank - normal level - no riser to grade. Aeration Tank - normal level - mixing present - compressor repaired. PUmp Tank- float sensors, pump and controls operating. DBox - Plastic - deformed - 3 laterals accepting effluent. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/30/2023 | 07:30 AM
11/22/2023 | Alternative | Reportable Incident |  | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Norweco. Aspirator has gone bad under the 3 year warranty. Customer approved replacement and warranty exchange fee. Will pay fee when pump is replaced. I left the pump power and alarm off 11/28: -Replace Aspirator under warranty -Bring back defective aspirator and give to Jeff so he can submit for Warranty | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | Dec 30 1899 8:46AM
02/13/2023 | Alternative | Reportable Incident | 133-STS-105906 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced damaged distribution box with new 8 port concrete DBox Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 07:00 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/15/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
01/18/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank to Puraflo Pump Tank | Discharge pump tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-6"sludge 2"scum/ Pump Tank to Puraflo Modules-2"sludge 0"scum/ Pump Tank to Drainfield-1"sludge 0"scum/ No pump out needed at this time/ Puraflo Peat Media fluffed and in good condition/ Controls, pumps, floats and alarms functioning properly/ Counts: Puraflo Pump1-10153 ETM-119h 40m/ Pump2-10083 ETM-118h 54m On-42s Standard Off-2h Peak Off-1h 36m/ Discharge Pump1- 2058 ETM-62h 25m/ Pump2-2010 ETM-61h 16m / Peak-43/ High-35/ No breakout or spongy areas on the drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/17/2023 | Alternative | RoutineScheduled | 03-125-300 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 4 - Blue Crystal tablets added 14 - Bio Max tablets added | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/17/2023 | 12:00 AM
08/19/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 15" of accumulated solids in septic tank. Cleaned septic tank solids filter. 14" of solids in recirculation portion of treatment unit. 14" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Removed some roots from treatment unit. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | 07:03 PM
12/21/2023 | Alternative | RoutineScheduled | 170 92 098 | Patrick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | NONE, Low Pressure System |  | Pump | Pressure | Trenches |  |  | ["None"] | ["None"] | [18 empty] | Annual inspection. 20" of solids in septic tank. 0" in pump tank. Low pressure lines flushed. Very clear effluent. Septic tank and discharge pump tank may need to be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2024 | 07:03 PM
07/03/2023 | Alternative | Initial Visit | 005-STS-42920 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [5 empty] | 06/27/2023 |  | 9.300000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-33 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
06/21/2023 | Alternative | Reportable Incident | 136-08-0060 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | System alarming - found seal at inlet of septic tank failed - heavy rains currently - pumped septic tank and pump chamber empty for storage and to prevent hydraulically overloading biofilter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 01:00 PM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
10/30/2023 | Alternative | Pump-Out Only | 2007-143-0054 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Supervised pump out of 1000 gallon septic tank performed by CWS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 08:52 AM
01/23/2023 |  | RoutineScheduled | 179-STS-87971 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Pump doing 34.4 gpm so we adjusted run time to get rid of full 100 gallon dose, new run time 2m54s. RECIRC: HL 1,LL 17, OVERRIDE 62. DISCHARGE: HL 9, OVERRIDE 37. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
02/21/2023 | Alternative | RoutineScheduled | 08-100-0723 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump |  | Pad |  | 450.000000 | [] | [] | YES | [17 empty] | REPLACED FIBER IN SYSTEM. REPLACED SWEET AIR VENT ON BIOCOIR. EVERYTHING WORKING AS IT SHOULD. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/24/2023 | 11:25 AM
07/21/2023 | Alternative | RoutineScheduled | 175-16-0153 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | NA | [17 empty] | Septic Tank-6"sludge 3"scum/ Microfast ATU- 4"sludge/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-6409 ETM-882h 46m/ Watermeter-0,377,025.26/ Noted: Drip is dosing 2 zones at the same time, need to replace faulty 1" check valves/ No breakout or spongy areas on the drip field. Returned on 8/4/2023 and replaced faulty 1" check valves/ System dosing correctly now at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
09/08/2023 | Alternative | Routine/Scheduled | 147-00-0112 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | YES | [17 empty] | - Septic Tank: Water level normal. Inlet tee appears to be intact. Flushed and cleaned effluent screen. Not due for pump out. - Pump Tank: Water level normal. Checked and confirmed discharge pump is functioning properly. Checked and confirmed discharge floats are functioning properly. - Peat Moss: Raked and tilled peat moss. Peat moss is in good condition. Found no signs of surfacing around dispersal area. - Condition: Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | Dec 30 1899 10:02AM
09/07/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 |  | Septic | Fast | Gravity | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [18 empty] | 0 scum, very little sludge. Alarms, blower working., cleaned filter, Sample box is a couple hundred feet downslope and is intact, Field is dry but grown up. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 12:15 PM
05/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sand filter zone is not functioning as designed. Emitters not functioning as designed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
08/11/2023 | Alternative | RoutineScheduled | 10-117-018 | Carroll | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | R & R Enterprises, Inc | 1942001111 | William | Robinson | 2.000000 | 1375 | AQUA SAFE AS500 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | Dec 30 1899 12:00AM
01/31/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.770000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:00 AM
10/06/2023 | Alternative | RoutineScheduled | 00-197-A11 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination | [21 empty] | Aerator/bubbler working, clear effluent, both tablets are stocked. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-11-0168-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
09/18/2023 | Alternative | Routine/Scheduled | 196-18-0090 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal Level 11" of sludge and 1" of solids Pulled and cleaned filter Filter is discontinued model No signs of infiltration -Discharge/Pump Tank 1: Normal Level All floats and pump are functioning properly No signs of infiltration -Discharge/Pump Tank 2: Normal Level All floats and pump are functioning however they are Aged Crock riser is cracked Pump pulled 9.9amps Alarm audible is working. It is located in guest house -Peat Moss: Peat moss inngood condition Raked Peat moss in all 4 chambers -Control Panel: 120v to each breaker All audible and visual alarms are functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 02:50 PM
03/30/2023 |  |  | 12-142-0085 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Disinfection","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | [17 empty] | Septic-4"sludge 6"scum/ Microfast-6"sludge/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ UV-Light sleeve cleaned and light functioning properly/ Counts: Pump-2367 ETM-523h 27m/ Peak-23 ETM-0h 3m/ High-22/ Watermeter-230,816.9/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/24/2023 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 03:18 PM
09/22/2023 | Alternative | Routine/Scheduled | 151-17-020 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal Level Less than 1"of solids and sludge Pulled and cleaned filter -Recirculation Tank: Normal Level Less than 1" of suspended solids Pulled and cleaned floats and pump screen Pump and floats are functioning properly Floats are Aged -Discharge/Pump Tank: Normal Level 5" of suspended solids Pulled and cleaned floats and pump screen All floats and pump are functioning properly -Media Sheets: Flushed and brushed lateral Sprayed off spinners Sprayed off media sheets Minor build up of biomat between media sheets -Control Panel: 120v to each breaker All audible and visual alarms are functioning properly Recirculation pump pulled 8.23amps Discharge pump pulled 10.78amps -Drain Field: Cleaned tubes for spider valve for drainfield No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 12:55 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Micro Fast is ready for pumping | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/11/2023 | Dec 30 1899 11:24AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 107-00-0721 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 10/03/2023 |  | 4.000000 | [5 empty] | Will be sent separately | Inspected | Primary tank requires pumping and recommend adding riser to inlet | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/22/2023 | 09:18 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Hydro-Action ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/01/2023 |  | Routine/Scheduled | 228-11-0654 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | Jan 1 1900 12:05PM
01/24/2023 |  | Initial Visit | 089-STS-39299 | Henry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | MicroFast |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Initial start-up inspection. Three compartment grease trap - 1st section - 2" crust, 20" in bottom, second section - skim crust, 6" on bottom, third section - 0" crust, 4" on bottom. Septic tank - 1" crust, 10" on bottom. MicroFast septic tank = 1" crust, 0" on bottom. Cleaned tank filter. MicroFast treatment unit solids accumulation - 0" crust, 12" of solids on bottom. Adequate aeration. Pump tank - 0" crust, 0" of accumulated solids on bottom. Tested floats, pump and alarms. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 07:03 PM
12/12/2023 | Alternative |  | 07-184-5011 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/12/2023 |  | 6.480000 |  |  | 4.400000 |  |  | Will be sent separately |  | BOD: 6.48 TSS: 4.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
10/25/2023 | Alternative |  | -STS-90154 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/21/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/21/2023 | Dec 30 1899 4:30PM
03/28/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | Jan 1 1900 7:20PM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/04/2023 | 09:55 AM
04/24/2023 |  | RoutineScheduled | 07-113-154 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","SludgeScum Accumulation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 5 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/24/2023 | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled | 10-163-0026 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/03/2023 |  | RoutineScheduled | 132-03-0083 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 | [] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/04/2023 | 12:00 AM
09/22/2023 | Alternative | Reportable Incident | 157-10-0043 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Came out for an alarm call on a Clearstream. Opened panel and found proper voltage. Opened discharge tank and found water level in alarm. Tested timer and timer worked but pump didn't cut on. Installed new relay and tested and pump began to run. Tested multiple times and system is functioning. Left the relay in as a courtesy since the panel is getting replaced October 2nd. Got system out of alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | 10:06 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2024 | 05:34 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | replaced supply line gauge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/09/2023 | Alternative |  | 86-197-244 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/09/2023 |  | 4.250000 |  |  | 3.600000 |  |  | Will be sent separately |  | BOD: 4.25 TSS: 3.60 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 12:00 AM
11/30/2023 | Alternative | Follow-Up | 98-197-A6 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco | Wchd |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity |  | Discharge | [5 empty] | None | Clear |  |  |  |  | tables no installed | [11 empty] | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12:00 AM
04/28/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The level of the peat is low but there are no signs of ponding failure as described by the manufacturer. Recommend leveling modules that are slightly out of level. Informed homeowner that the peat is nearly the end of its functional life and that he should plan for replacement in the future. Informed the homeowner of alternatives to peat such as aerobic treatment that would get rid of the modules. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/25/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 09/25/2023 |  | 25.000000 | [5 empty] | Will be sent separately | Inspected | Repaired audible alarm Filter clog cleared Please keep all brush 3-4' away from all components | This AOSS should now return to normal function after having provided the above state routine maintenance | 10/13/2023 | Dec 30 1899 1:07PM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92192 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"Control Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"Control Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 07/26/2023 |  | 10.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. HL 1,LL 10, OVERRIDE 0. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
09/25/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV bulb & ballast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 12:15PM
03/20/2023 | Alternative | Routine/Scheduled | 136-15-0219 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Pumped out the septic tank and pumped the scum off the Clearstream. The timer is set to 5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 03:00 PM
12/11/2023 | Alternative | RoutineScheduled | 12-183-207 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/11/2023 | 12:00 AM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection of a conventional pump septic system. The septic control panel is an interior demand dose. There is a clean out with in 5 ft of house. The sewer line was camera snaked and was clear. The septic tank has a plastic riser on the outlet side of the tank. The effluent was at working level. The septic tank was pumped out. The pump tank, riser, electric box, force main, floats and pump were inspected. The plastic 9 port d-box is at ground level. All 4 header lines were camera snaked. Lines 1 and 2 are clear. Lines 3 had small tree roots in it but was able to get camera thru. Line 4 after 20 feet was unable to get thru the tree roots. Probed drain field it was dry. At time of inspection septic system was not in working condition. Will need to dig up section of header line to replace or be able to pull roots out. This inspection does not guarantee the life of the components | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/18/2023 |  | Routine/Scheduled | 234-16-221 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/18/2023 | Jan 1 1900 1:00PM
10/18/2023 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | Dec 30 1899 10:15AM
11/27/2023 | Alternative | RoutineScheduled | 00-197-088 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/27/2023 | 12:00 AM
03/09/2023 |  | Routine/Scheduled | 2016-143-0110 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/09/2023 | 01:45 PM
06/27/2023 | Alternative | RoutineScheduled Component Maintenance | 182-17-0184 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
08/30/2023 | Alternative | RoutineScheduled | 107-06-0275 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 |  |  | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 12:00 AM
10/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/20/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | UV Bulb replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/13/2023 | Alternative | RoutineScheduled | 177-STS-89946 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 0-0 | 0-0 0-0 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 12:00 PM
10/20/2023 | Alternative | Routine/Scheduled | 151-91-180 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 06:52 PM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
03/22/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Off float needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | Jan 1 1900 12:26PM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 107-16-0125 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 12/07/2023 |  | 24.000000 | [5 empty] | Will be sent separately | Inspected | Media cleaner added and primary tank pumped | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | Norweco Singulair ATU | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/12/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:00PM
05/19/2023 | Alternative | RoutineScheduled | R16-180-0102 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Whitewater |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Inspection visit-- Septic Tank 1 " scum and 6" sludge Trace. Treatment Tank 2-3" Scum and 4" sludge Trace, Pump Tank 6-10" sludge light sludge- Blower Runs good, alarm ok, cleaned air filter, discharge pump runs good on timer, Cleaned effluent filter added 2lb Rootx Treatment Drainfield looks good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
11/02/2023 | Alternative | Routine/Scheduled | 036-STS-35295 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/02/2023 | Dec 30 1899 2:24PM
06/01/2023 | Alternative |  | 121-STS-13299 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1500 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [] | NA | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 12:00 AM
10/12/2023 | Alternative |  | 09-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
09/15/2023 | Alternative | RoutineScheduled Component Maintenance | 196-06-082 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The housing lid for the air release valve should be replaced. You can acquire a new one at a local home improvement store or we can provide one for you. Plese contact our office if you would like our assistance with this repair. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
03/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 03/30/2023 | Sample Chamber | 20.000000 | [5 empty] | Attached to this report |  | Septic Tank-6"sludge 4"scum/ Microfast-6"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-681 ETM-17h 25m/ Pump2-662 ETM-17h 0/ Peak-3/ High-3/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/26/2023 | 10:29 AM
02/16/2023 |  | RoutineScheduled | 08-195-065-DIS | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/16/2023 | 12:00 AM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance | 154-05-1034 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens" ,"Dispersal System Operation" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | As noted previously, the Advantex module has settled. We also observed roots growing into the module around the RSV. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
05/02/2023 |  | RoutineScheduled | 107-14-0170 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin clean filters were both cleaned. The controls were operating as designed. There were no visible leaks in the drip field. There was return effluent returning from the drip field. The drip field was operating as designed. The pressure was adjusted on the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/24/2023 | 09:45 PM
10/11/2023 | Alternative | RoutineScheduled | 01-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.500000 | 7.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/12/2023 |  | RoutineScheduled | 196-09-136 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/31/2023 | Alternative | Follow-Up Component Maintenance | 099-STS-89867 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Deleted sample box. Replaced distribution box with above grade monster box. Camera inspected header lines for damage/roots. Repaired crushed header on line 3. Added Root-X to all lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
02/23/2023 |  | Follow-Up |  | Culpeper | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [9 empty] | 22.000000 |  | 2419.600000 | 20.800000 |  |  | Will be sent separately | Inspected | DO 8.99 Effluent sampling only | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/03/2023 | 08:19 AM
09/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["SludgeScum Accumulation","Attached Growth Medium","BlowerCompressorAerator Operation"] | NA | [7 empty] | 09/28/2023 | Sample Chamber | 8.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 5"scum/ Microfast-16"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ Pump out required on the Septic-Microfast Tank (Done by others on 10/3) Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms are functioning properly/ Counts: Pump1-25371 ETM-84h 45m/ Pump2-24878 ETM-80h 11m On 2m 3s Off-6h /Peak-12/ High-12/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/18/2023 | Alternative | RoutineScheduled | 182-02-0481 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation","Attached Growth Medium"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out | FAST and pump tank pumped. Air line fixed. FAST scheduled to dig off for clog | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 12:00 AM
04/20/2023 |  | RoutineScheduled | 02-113-378 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/20/2023 | 12:00 AM
10/25/2023 | Alternative | RoutineScheduled | 03-197-A3 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] |  |  | None | Clear | 6.000000 | 8.000000 |  | 0.000000 | [11 empty] | Tablets need to be stocked. | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
04/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/03/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [28 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 01:57 PM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | SD-10-152 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System did not have effluent to do sampling. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 07/17/2023 | 12:46 PM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic zone 2" Scum layer on top & 8" Sludge layer on bottom- Pump run time 218 this year and 184 Hrs last year- about 34 hours- Pump cycles 2235 cycles this year or 476 cycles since last year. Cleaned blower filter, Good aeration. Drainfield appears dry when walked after runnng the pump, Both alarms and 4 floats all responded, as should. System pump last year and does not need it this year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
01/31/2023 |  | RoutineScheduled | 179-13-0323-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"SludgeScum Accumulation"] | ["Effluent Screens" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | YES | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the Septic Tank/ATU Tank and the Pump Tank due to scum & sludge accumulation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
03/09/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/30/2023 |  |  | 085-STS-34484 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
05/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/17/2023 | 12:02 PM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | ATU needs pumped. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | 12:58 PM
07/13/2023 | Alternative | RoutineScheduled | 104-10-0160 | Amherst | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1000 | Septic Tank | Microfast | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 02:00 PM
04/05/2023 |  | Initial Visit |  | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Trash Tank - normal level Aeration Tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. Surge & Dbox intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | Jan 1 1900 7:30AM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping Microfast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0134-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Recommend to upgrade pump when it fails due to pump only doing 25 gallons per minute. Recommend to install a float tree at time of pump replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
06/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/27/2023 | Alternative | Follow-Up Component Maintenance | 177-STS-88024 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed outlet riser. Resealed Aqua Safe riser. Resealed pump tank outlet riser and return line penetration in tank. Added proper junction box for wiring in pump tank. Bleach flushed zone 3 in attempt to improve slow rate. Resealed inlet and outlet pipes on Aqua Safe as precautionary. Sealed septic tank outlet pipe (was leaking). We will return in 2 weeks to check drip. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
11/14/2023 | Alternative | RoutineScheduled | VAG408102 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/14/2023 | 12:00 AM
02/07/2023 |  | Reportable Incident |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Loudoun | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Aquarobic Mini Plant | [6 empty] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] |  | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/02/2023 | 09:38 AM
08/09/2023 | Alternative | RoutineScheduled | 001-STS-92421 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 |  | FUJI CLEAN CEN 5 |  | Pump | Pressure | Mound | UV | 450.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 6" FROM BOTTOM, 3" FROM TOP EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 09:45 AM
11/28/2023 | Alternative | Routine/Scheduled | 17-142-0078 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/28/2023 | Dec 30 1899 11:25AM
09/25/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired air relief valve & lids. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | Dec 30 1899 12:58PM
01/30/2023 |  | Initial Visit | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - System Commissioning Trash Tank - normal level Aeration Tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | 07:15 AM
04/25/2023 |  | Routine/Scheduled | 234-15-214 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 1:15PM
01/23/2023 |  | Routine/Scheduled | 98-142-0046 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | STE to Drip - Alternative dispersal only. Primary septic tank - normal level. Pump tank - float sensors, pump and controls operating. Drip - headworks serviced - disk filters serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 7:30AM
03/24/2023 | Alternative | Routine/Scheduled | 166-10-192 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 |  | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/24/2023 | 06:43 PM
12/19/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | 01:45 PM
07/01/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | BioMicrobics MicroFast |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Grease trap - 4" crust, 10" on bottom. Septic tank - 24" of accumulated solids, no crust. 20" of solids in treatment unit. 10" of solids in discharge pump tank, very "fluffy". Cleaned blower air filter. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/03/2023 | 07:03 PM
03/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/06/2023 | Alternative | RoutineScheduled | 077-STS-36900 | Grayson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | 12:00 AM
08/14/2023 | Alternative | Routine/Scheduled | 157-09-0142 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 09:30 AM
03/16/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
04/12/2023 |  | RoutineScheduled | 003-STS-32774 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-89388 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
08/01/2023 | Alternative | RoutineScheduled | 133 04 1026 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | BioWheel |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | July 2023 monthly report. Total flow for month of July 2023 - 177,731 gallons. Average daily flow- 5,773 gallons per day. Digester pumped out during the month. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 07:03 PM
02/02/2023 |  | Routine/Scheduled | 093-16-0154 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 11:30AM
06/12/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Cloudy | 7.800000 |  |  |  |  | 06/12/2023 |  | 7.000000 |  |  | 5.100000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/13/2023 | 01:00 PM
08/05/2023 | Alternative | RoutineScheduled | 019-STS-23904 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. Septic tank - 16" of accumulated solids with a 1" solids crust. Cleaned septic tank filter. Flushed treatment unit spray manifold. 10" of solids in recirculation portion of treatment unit. 18" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. Septic tank and treatment unit should be pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/06/2023 | 07:03 PM
02/27/2023 |  | RoutineScheduled | 179-13-0235-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
09/02/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | Modified Extended Aeration |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | Total flow to drain fields August 2023 -207,940 gallons. Average 7,701 gallons per day. All aspects of the system are operational. Wasting of settled mixed liquor from the clarifier to the digester and decanting of supernatant from digester are occurring regularly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 07:03 PM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
08/08/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic / Ecopod ATU Treatment Tank | Pump Tank | Pump | Pressure | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 08/08/2023 | Sample Chamber | 8.000000 | [5 empty] | Attached to this report |  | Septic Tank-14"sludge 2"scum/ Ecopod ATU-18"sludge/ Pump Tank-2"sludge/ Pump out required on the Septic-Ecopod Tank/ Blower air filter cleaned and blower working correctly/ Controls, pumps, floats and alarms functioning properly/ Counts: Pump1-1435 ETM-106h 36m/ Pump2-1385 ETM-103h 6m On-4m 32s Standard Off-7h 55m Peak Off-6h 19m / Peak-124/ High-20 / No breakout or spongy areas on the LPD Pad Site. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/27/2023 |  | RoutineScheduled |  | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Gravity | Gravity | Trenches | Chlorination |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Disinfection" ,"SludgeScum Accumulation"] | ["SludgeScum Accumulation" ,"Disinfection" ,"Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | New blower Septic tank pumped Added riser on tank Recommend relocating tree in bed and maintaining added tablets | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
05/04/2023 | Alternative | Routine/Scheduled | 151-16-090 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 50.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 06:57 PM
03/15/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | BlowerCompressorAerator Operation | BlowerCompressorAerator Operation | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/30/2023 | 12:54 PM
07/14/2023 | Alternative | Routine/Scheduled | 11-142-0279 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | SludgeHammer |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/14/2023 | Dec 30 1899 1:48PM
05/23/2023 |  | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | Control Operation | Control Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 10:16 AM
10/20/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-88639 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation"] |  | NO | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The timer enable float in the drip pump tank is stuck in the up position which would make the pump run constantly. Fortunately the override float is preventing this from happening. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
06/06/2023 |  | RoutineScheduled | 175-17-0410 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
11/15/2023 | Alternative | Reportable Incident | 199-04-0022 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Found panel in alarm. Had proper voltage pump pulling zero amps. Checked connections and all wires were tight. Pulled pump found the empeeller free spinning. Bumped pump on and nothing happened. Bad pump. Quoted for repairs and customer approved. Advised to cut back on water usage much as possible | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | Dec 30 1899 1:35PM
04/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Strongly recommend flushing and balancing lines in the near future | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/02/2023 | Alternative | RoutineScheduled | 09-184-5002 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/02/2023 | 12:00 AM
07/11/2023 | Alternative | Routine/Scheduled | 09-142-0021 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation"] | N/A | [17 empty] | Air filter cleaned. System checked. System appears to be operating normally. Ct 36, etm 2hr 19 min | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/11/2023 | Dec 30 1899 12:36PM
05/21/2023 | Alternative | RoutineScheduled | 047-18-056 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | septic/trash | Singular | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 09:05 AM
06/30/2023 | Alternative | Reportable Incident | 157-01-240 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | AOSS - Alarm - found compressor failed - replaced with new HiBlo 60/80 compressor - restored system to proper function. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 08:45 AM
04/01/2023 |  | RoutineScheduled | 133 18 0194 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 6" of accumulated solids in septic tank. Cleaned septic tank solids filter. Flushed treatment unit spray manifold. Adjusted recirculation pump flow rate, for better treatment quality. 2" of solids in recirculation portion of treatment unit. 0" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 07:03 PM
01/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | Dec 30 1899 11:08AM
09/14/2023 | Alternative | RoutineScheduled | 2016-143-0009 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Carrington Pump & Irrigation | 1942001121 | John | Carrington | 2.000000 |  | Norweco |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Effluent Screens","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation","Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 12:00 AM
02/21/2023 |  | RoutineScheduled | 2032-96-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | Chlorination |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Needs new blower. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 03/13/2023 | 11:23 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/10/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92326 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
03/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/22/2023 |  |  | 13-113-102 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/22/2023 |  | 4.940000 |  |  | 1.600000 |  |  | Will be sent separately |  | BOD: 4.94 TSS: 1.60 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/22/2023 | 12:00 AM
01/26/2023 |  | Routine/Scheduled | 234-16-221 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 10:30AM
09/25/2023 | Alternative | Routine/Scheduled | 175-STS-15038 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 9:40AM
11/01/2023 | Alternative | RoutineScheduled | 00-197-088 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection","BlowerCompressorAerator Operation"] |  |  | Septic | Dark Brown |  | 0.000000 | [14 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-17-0114 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Effluent Screens"] | ["Disinfection" ,"Effluent Screens"] | YES | Musty | Clear | 7.300000 | 14.600000 | [11 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92858 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
09/26/2023 | Alternative | RoutineScheduled | 109-07-0039 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20 |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 18" of accumulated solids in septic tank. Cleaned recirculation pump basket filter. Flushed treatment unit spray manifold. Sprayed solids off of treatment unit "sheets". Unclogged several spray heads in spray manifold. Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/24/2023 | 07:03 PM
11/21/2023 | Alternative | RoutineScheduled | 06-192-226 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation","Disinfection"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/21/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled | 07-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 3 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/18/2023 | 12:00 AM
10/03/2023 | Alternative | RoutineScheduled | 001-STS-92936 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn |  |  | FUJI CLEAN CEN5 |  | Pump | Pressure | Mound | UV | 150.000000 | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | PUMPED SEPTIC TANK, EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/10/2023 | 10:05 AM
04/28/2023 |  | Initial Visit | VAG401973 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | FAST ATU | Constructed Wetland | Pump | Gravity | Discharge | Chlorination |  | ["Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | NA | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/07/2023 | 09:30 AM
02/24/2023 | Alternative | Routine/Scheduled | 18-120-0186A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/24/2023 | Dec 30 1899 3:17PM
01/26/2023 |  | RoutineScheduled | 179-18-0181-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
04/13/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV glass housing & bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/15/2023 | Jan 1 1900 12:48PM
04/17/2023 |  | RoutineScheduled | 087-STS-6199 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Clearstream |  | Pump | Pressure | Drip | UV |  | [] | ["Level Sensor Operation","Effluent Screens","BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 12:00 AM
07/01/2023 | Alternative | RoutineScheduled | 067-STS-39729 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | NONE |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Meters - A - 940, B -670, C - 910. Tested both discharge pumps in "HAND", both pumping. Still no gallons pumped to drain field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | 07:03 PM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 175-18-0213 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 | 3000 | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation"] | ["SludgeScum Accumulation" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Needs Proposal Sewer line from house to septic tank has settled no longer proper fall between inlet/outlet tee structures Electrical junction box @ p.tank damaged Exterior Alarm float does not work. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
02/07/2023 |  |  | 2004-143-0336 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 12:00 AM
03/08/2023 |  | Reportable Incident | 550-STS-6361 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | Control Operation | Control Operation | N/A | [17 empty] | Replaced timer | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/08/2023 | Jan 1 1900 7:30AM
09/07/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-31775 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/09/2023 |  | RoutineScheduled | 003-STS-32844 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Norweco | Gravity | Gravity | Discharge | UV | 450.000000 | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
06/26/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The peat is showing signs of its age, but appears to still have good texture and is not very saturated. Informed the homeowner that while the peat is approaching the end of its life, at this point we believe it is still functioning as specified by the manufacturer. Recommended that the homeowner trim up some of the plants around the modules to make access easier for future operators. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/24/2023 |  | RoutineScheduled | 175-06-0323 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank to Puraflo Modules | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [17 empty] | Septic Tank-6"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Puraflo Peat fluffed in all 6 modules and is acceptable at this time but may need replacement in the near future/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-025227 ETM-0061573 On-66sec. Off-2h/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/11/2023 |  | RoutineScheduled | 179-06-0212-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Pad site not saturated in dry conditions but there is 1" of water in bottom of sample box. Not failing. Padsite needs to be maintained a little more. 1 module has a Crack on a corner of the lid nothing major, will send price for a used 1. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 03:56 PM
05/31/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Damaged riser was replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/03/2023 |  | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | Control Operation | Control Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/03/2023 | 10:10 AM
12/19/2023 | Alternative | RoutineScheduled | 029-STS-22782 | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | purasystem |  | Pump | Gravity | Trenches | Not Applicable | 350.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | Dec 30 1899 11:00AM
11/16/2023 | Alternative |  | 09-184-5003 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/16/2023 |  | 9.930000 |  |  | 6.000000 |  |  | Will be sent separately |  | BOD: 9.93 TSS: 6.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 12:00 AM
08/09/2023 | Alternative | Routine/Scheduled | 550-STS-6497 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 9:50AM
04/29/2023 | Alternative | RoutineScheduled | 136-07-0421 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 | 1,000 gallons | Clearstream |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | None | Clear | [15 empty] | Drain field area located in wooded area. No signs of ponding or any indication of failure. Let homeowner know the area should be hand cleared and maintained to prevent more growth of trees in the area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/29/2023 | 12:00 AM
08/24/2023 | Alternative | RoutineScheduled | 001-STS-92325 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Pressure | Mound | UV | 450.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | PUMPED SEPTIC SYSTEM EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 02:10 PM
01/18/2023 |  | RoutineScheduled | 09-172-0143A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | Advantex |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | Jan 1 1900 12:10PM
06/07/2023 | Alternative | Pump-Out Only | 157-10-0131 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Treatment pumped empty as recommended during last service visit. Found fracture at top of Clearstream unit. Refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 10:00 AM
03/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | 11:23 AM
03/14/2023 |  | Reportable Incident | 228-12-0542 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/14/2023 | Jan 1 1900 8:00AM
01/24/2023 |  | RoutineScheduled | SWP-04-315 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
06/12/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-90122 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We recommend mowing the dispersal area and maintaining it in a mowed condition. Also, the RSV vent tube is missing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
11/01/2023 | Alternative | RoutineScheduled | 06-120-0824A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1150 | 1000 | 150 | Pump | Gravity | Mound | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Disinfection","Auxiliary Filter","Attached Growth Medium","Control Operation"] | YES | Pungent | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 12:00 AM
02/08/2023 |  | RoutineScheduled | 133 06 0436 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | [] | [] | NA | None | Clear | [5 empty] | 02/08/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 07:50 AM
08/30/2023 | Alternative | Routine/Scheduled | 800-STS-15041 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Fuji |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | Dec 30 1899 8:15AM
10/04/2023 | Alternative | RoutineScheduled | 2019-143-0037 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/24/2023 | Alternative | Follow-Up | S800-17-0036 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Meet with the pumping company and pumped and cleaned the Clearstream tank. Replaced the diffuser in the Clearstream tank. Need to go back and hook the pressure switch up. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/24/2023 | Dec 30 1899 12:00PM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance | 182-04-0565 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | cut trees back from system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
04/04/2023 |  | Reportable Incident |  | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | [18 empty] | COSS - Maintenance - GMP2018-02 Replaced structurally failing dbox with new 8 port concrete Dbox. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | 09:00 AM
02/13/2023 |  | Reportable Incident | SR-98-350 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Control Operation"] | ["Recirculation Pump" ,"Control Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm in pump tank (sand filter dosing end and drip pump vault end). Pilot fuse was not fully seated, so cycles were intermittent. Sand filter dosing pump kept tripping off on thermal overload - replaced it. Sand filter lids have a heavy cover of fallen leaves and something was starting to grow in under the lids. Owner advised to keep lids clear. Flow meter not turning when dosing to zone 3. Traced problem to a short in the main motherboard. The part is available, but the control panel is old and the correct Siemens processor is no longer available - recommend replacing the entire panel. Turned off zone 3 as a SHORT-TERM solution to allow the panel to operate. The panel was originally installed about 3" above ground which makes it difficult to work on and potentially makes the panel more vulnerable to rain and snow. The uf cables running to the 2 pumps are in bad shape primarily because the junction boxes are mostly buried and subject to ground moisture. Recommend running new wires in conduit and mounting the junction boxes on short posts to get them above ground (riser lids are flush with top of ground). The flush rate for zone 3 was noted on last inspection to be very low. Drip tubing was installed in the woods so tree roots are probably to blame. Manifolds may need to be uncovered and inspected. The remote solenoid valve assemblies are showing their age (diaphragms are weak and replacements are unavailabe) and are recommended to be replaced. The hydraulic unit is original with over 1,500,000 gals showing on the flow meter. These items are all beyond the average lifespan and are recommended to be replaced before they fail. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
05/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Rejected | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Distribution Pump Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
04/19/2023 |  | Routine/Scheduled | 087-STS-6473 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/19/2023 | 10:37 AM
03/07/2023 |  | RoutineScheduled |  | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Media was clogged and replaced | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/18/2023 | 04:10 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Added media cleaner | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
08/08/2023 | Alternative | RoutineScheduled | SD-86-60 | Clarke | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lord Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","Level Sensor Operation","SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out | Sale inspection on an LPD septic system. And pumped out the septic tank | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/11/2023 | 11:00 AM
11/20/2023 | Alternative | Routine/Scheduled | 179-97-063 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Sandfilter, Recirculating |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 10.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 07:07 PM
08/14/2023 | Alternative | Routine/Scheduled | 157-04-127 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the buzzer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/14/2023 | 10:00 AM
05/17/2023 | Alternative | RoutineScheduled | 121-STS-12162 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [16 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | 12:00 AM
06/06/2023 | Alternative |  | 05-172-0141A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1500 | 750 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Disinfection","Control Operation","SludgeScum Accumulation","Level Sensor Operation","Effluent Screens","Distribution Pump Operation"] | YES | Pungent | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 12:00 AM
03/28/2023 |  | RoutineScheduled | 132-05-0015 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-21131 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Completed annual inspection. Bottom float switch (R.O.) was stuck on, replaced it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
12/15/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/27/2023 | Dec 30 1899 12:40AM
09/30/2023 | Alternative | Initial Visit |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex AX20RT |  | Pump | Gravity | Trenches |  |  | ["Control Operation"] | ["Control Operation"] | NA | [17 empty] | Initial start-up inspection. Adjusted float switch positions in recirculation and discharge portions of treatment unit according to manufacturer's service memorandum for this unit as determined by serial number. Adjusted recirculation pump flow rate. Adjusted pump timers per service memorandum. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 07:03 PM
01/06/2023 |  | RoutineScheduled | 109-18-0007 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 | SEPTIC | Advantex | Gravity | Gravity | Discharge | UV | 450.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Control Operation","Disinfection","Recirculation Pump","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | 10:30 AM
03/06/2023 |  | RoutineScheduled | SWP-02-557 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Water is bridging on the Advantex textile media sheets. Due to the age of the system, the rods are brittle and will break if we attempt to power wash the sheets. We recommend installing a new module replacement kit and pumping the Advantex tank afterwards. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
08/30/2023 | Alternative | RoutineScheduled | 10-125-090 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Mound | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | 12:00 AM
05/05/2023 |  | Routine/Scheduled | 17-120-0159AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Flow Equalization Tank - pump and controls operating. Processing Tank - recirc - pump, media drapes & spray grid serviced. Processing Tank - discharge - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | Jan 1 1900 8:45AM
09/28/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 8.110000 | 7.300000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 03:45 PM
06/01/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
02/23/2023 |  | Routine/Scheduled | {FIPSCode}-STS-5382 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | Jan 1 1900 3:30PM
05/02/2023 |  |  | 07-184-5007 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/02/2023 |  | 10.600000 |  |  | 9.800000 |  |  | Will be sent separately |  | BOD: 10.6 TSS: 9.80 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 182-07-0145 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 09/26/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected | Gauge replaced Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Distribution box has lots of roots in in. Restricting flow from the modules to the field. Alarm was not functioning. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
08/22/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/15/2023 | 12:00 AM
12/04/2023 | Alternative | RoutineScheduled | 166-07-087 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wind River Environmental | 1942001775 | Anthony | Santucci-Curci | 1.000000 | 1000 | Pete Moss |  | Pump | Pressure | Pad | Not Applicable |  | ["None"] | ["None"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/07/2023 |  |  | 2017-143-0209 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Aquaklear | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2023 | 12:00 AM
07/17/2023 | Alternative | Routine/Scheduled | 08-120-0496A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Hoot |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/17/2023 | Dec 30 1899 10:32AM
06/03/2023 | Alternative | RoutineScheduled | 175-14-0130 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | EcoVirginia LLC | 1942001235 | William | Poindexter | [9 empty] | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | 12:00 AM
07/18/2023 | Alternative | RoutineScheduled | 04-142-0393 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 1250 | PremierTech EcoFlo |  | Pump | Pressure | Trenches |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation","Level Sensor Operation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","Other"] | YES | [6 empty] | Peatmoss replaced in all pods | [9 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | Dec 30 1899 1:00PM
10/18/2023 | Alternative | RoutineScheduled Component Maintenance | 113-18-104 | Madison | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There is effluent coming to the surface in multiple places in the dispersal area. W did not change the timer setting, but it is worth noting that under the normal setting, the system is only delivering approximately 160 gal/day, but in override it is delivering nearly 590 gal/day. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/01/2023 | 07:38 AM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
08/09/2023 | Alternative | RoutineScheduled | VAG408149 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Multi flo |  |  | Gravity | Discharge | Chlorination |  | ["Disinfection"] | ["Disinfection"] | [18 empty] | no discharge. Tablets added | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/09/2023 | 12:00 AM
03/30/2023 |  | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Orenco Advantex | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 03/30/2023 |  | 65.000000 | [5 empty] | Will be sent separately | Inspected | alarm unplugged union was leaking, tightened | This AOSS should now return to normal function after having provided the above state routine maintenance | 04/28/2023 | 02:17 PM
06/22/2023 | Alternative | RoutineScheduled | 17-137-0175 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | EZ Treat |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Distribution Pump Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 12:00 AM
10/09/2023 | Alternative | Routine/Scheduled | 157-13-0088 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 02:45 PM
02/09/2023 |  |  | SWP-04-216 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/19/2023 | 12:00 AM
11/09/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | 180 day | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/09/2023 | 12:00 AM
05/18/2023 |  | RoutineScheduled | 179-STS-90116 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. RECIRC: HL 17, LL 21, OVERRIDE 1458. DISCHARGE: HL 3, OVERRIDE 3. "R" counts to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 04:39 AM
10/06/2023 | Alternative | Routine/Scheduled | 151-09-0017 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level 2 in of sludge and less than 1 in of solids Pulled and cleaned filter Filter housing intact Current filter is discontinued however is still functioning No sings of infiltration -Discharge/pump Tank 1: Normal level Tested floats and pump all functioning properly Splice box and plumbing intact Pump is working and moving water as should No signs of infiltration however pump chamber is bulging from ground pressure -Discharge/Pump Tank 2 (pump station in basement): Found at normal level Tested floats and pump all working as it should The vent is hard piped so lid cannot be moved Noted toilet paper getting built up on floats removed toilet paper while on site Tested multiple times Cannot adjust the pump placement do to the plumbing But station is functioning Pump pulled 10.1 amps -Peat Moss: Tipping bucket and dispersal trays are intact Peat moss is spent and saturated as well as roots intruding Raked and moved peat moss around to help with puddling No cracks or breaks in peat moss module -Control Panel: 120 volts coming in All visual and audible alarms functioning properly pump pulled 6.99 amps -Drain Field: Verified inspection port is not holding water No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 10:14 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend evaluation of the distribution boxes. Trees on neighboring lot could potentially cause damage to the system (Force main, Distribution Boxes, Headers, Lines). The septic tank is listed as a plastic tank but was replaced in 2014 with concrete tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/31/2023 | Alternative | Routine/Scheduled | 04-163-0152 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Level Sensor Operation","Recirculation Pump"] | ["Level Sensor Operation","Recirculation Pump"] | N/A | [17 empty] | Have had frequent / intermittent alarm events - replaced all float sensors in both recirc tank and discharge tank. Noted recirc pump being hot to the touch - replaced with new. System due for full service in December. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | Dec 30 1899 7:00AM
01/23/2023 |  | Routine/Scheduled | SP-04-498 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - Dosing - float sensors, pump and controls operating. BioFilter - 4 Modules - peatmoss in good condition - raked / turned. Pump tank - Discharge - float sensors, pump and controls operating. Drip - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 07:15 AM
04/20/2023 | Alternative | RoutineScheduled | 2018-143-0253 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Other"] | ["Other"] | [17 empty] | Pumped Out | Pumped 1000 gallons | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/14/2023 |  | Initial Visit | 550-STS-6372 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 5.000000 | [7 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the diffuser in the Clearstream. Changed the filter in the aerator. Installed the filter in the Clearstream. Installed a 3/4" brass check valve in the pump tank. The timer is set to 3.5 minutes every 2 hours. Took BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | Jan 1 1900 4:30PM
10/23/2023 | Alternative | RoutineScheduled | 14-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] |  |  | None | Clear | 6.500000 | 3.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/17/2023 |  | RoutineScheduled | 179-STS-90370 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | Musty | Clear | [5 empty] | 01/17/2023 |  | 4.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Conduit for junction box broken inside pump tank. Clip for float bracket missing. HL 3, LL 9, OVERRIDE O. Blower 3.08 amps. Pump doing 34 gallons per minute so we adjusted run time to get rid of full 100 gallon dose. New run time 2m56s. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
02/07/2023 |  | RoutineScheduled | 099-07-0127-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | A tree has fallen on the dispersal area. We recommend that it be removed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/26/2023 | Alternative | RoutineScheduled | SD-15-115 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
03/29/2023 |  | Routine/Scheduled | NYII-BD4LT5 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Jan 1 1900 12:50PM
11/06/2023 | Alternative | Follow-Up Component Maintenance | SD-12-285 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Augered peat. Shop vac drainage piping from sample box, restored drainage. Video inspected drainage piping, piping OK. Peat is degraded, will make a site visit in the spring to check condition since drainage was restored. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
08/18/2023 | Alternative | RoutineScheduled | 107-17-0191 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Dispersal System Operation"] | ["Effluent Screens","Dispersal System Operation"] | YES | Musty | Clear | [15 empty] | replaced broken valve box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1125 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 10/30/2023 | Sample Chamber | 6.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance | SD-10-109 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity |  | Chlorination |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Attached Growth Medium"] | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy |  | 5.430000 | 7.000000 |  |  | 05/17/2023 | Sample Chamber | 21.000000 |  | 2419.600000 | 50.200000 |  |  | Will be sent separately | Inspected | As noted previously, the sand filter is holding water. It may be advisable to replace the sand. We recommend pumping the pump tank due to sludge accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
01/09/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/20/2023 |  | Reportable Incident |  | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced collapsed dbox with new 8 port concrete DBox Replaced conveyance line with new 4" PVC Replaced three header lines with new 4" PVC | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/24/2023 | 07:00 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
08/01/2023 | Alternative | RoutineScheduled | 18-120-0203A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","SludgeScum Accumulation","Effluent Screens","Level Sensor Operation"] | YES | None | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/01/2023 | Dec 30 1899 10:30AM
02/23/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 2.000000 | 2500 | Double -Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Level Sensor Operation"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | New Client -1st trip- Routine Inspection - Checked effluent filter which was clean. found no scum in specti tank and 6-12" sludge on bottom. Recir zone/Discharge zones of advantex 12" light sludge trace. Owner may lower soil about 2 inches below the lids to reduce infiltration. Tank water was very clear and has minimal use.Tested floats found dishcahrge middle 5th floats sending no to very week signal to the board casuing a delay in discharge pump operation. Owner wants to upgrade to internet monitoring in future. Recirc pump run time 1787.5 Min and 50501 cycles, discharge pump run time 1570.7 min and 39746 cycles. Will return to replace float soon. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/24/2023 | 09:30 AM
07/07/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower was replaced and the aeration component of the system appears to be functioning as designed at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
07/21/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
11/16/2023 | Alternative | Routine/Scheduled | 06-120-0837A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Ecoflo |  | Pump | Gravity | Trenches |  |  | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/16/2023 | Dec 30 1899 10:09AM
07/17/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 12:00 AM
11/11/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 18" of solids in first section of septic tank. 10" of solids in second section of septic tank. 0" of solids in recirculation portion of treatment unit. 0" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Cleaned septic tank solids filter. Tested floats, pumps and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 07:03 PM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/13/2023 | Alternative | RoutineScheduled | 182-17-0340 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Recirculation Pump","Septic Tank Baffles","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Recirculation Pump","Septic Tank Baffles"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/13/2023 | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/25/2023 | Alternative | Reportable Incident | 128-08-0185 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed lift pump. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/22/2023 |  | RoutineScheduled | MWAR-A8LH9Q | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Treatment is clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
03/29/2023 | Alternative | RoutineScheduled | 061-STS-22110 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ- Treat Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [17 empty] | Septic side-2"sludge 7"scum/ EZ-Treat Recirculation side-2"sludge 2"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Noted: EZ-Treat spray nozzle upper left corner was clogged, removed and cleaned, spraying properly now at this time/ Counts: Discharge Pump- 0000744 ETM-00042.32h/ Recirc pump-9.8 amps/ Discharge pump-10.2 amps/ No breakout or spongy areas on the drainfield area and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/22/2023 |  | Reportable Incident | 00-142-0592 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | Found a broken drip line at the end loop. Fixed it. System appears to be operating normally | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/22/2023 | Jan 1 1900 11:17AM
08/10/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | 12:00 AM
01/23/2023 |  | RoutineScheduled | 179-11-0181-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Sample box and cleaned out near of D-box full of water causing pods not to drain correctly. Recommend to check them on a dry week to be able to camera snake drainfield. Peat moss is saturated and degraded Recommend to get it replaced. Pump not pumping enough to doze 9 gpm to each pod, recommend to upgrade or replace. Will send proposal for repairs. Fluffed peat to help dry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
11/01/2023 | Alternative | Routine/Scheduled | 228-17-0185 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | Dec 30 1899 1:10PM
10/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1800 |  |  | Pump | Gravity | Pad | Not Applicable | 900.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/26/2023 | Dec 30 1899 9:50AM
04/26/2023 |  | RoutineScheduled | 154-04-0511 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 12:00 AM
11/06/2023 | Alternative | RoutineScheduled | 107-09-0399 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Control Operation"] | [18 empty] | replaced splice box in ground at pump tank | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/12/2023 | 12:00 AM
04/26/2023 |  | Initial Visit | 550-STS-6575 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The UV is not working - burnt up- needs to be fixed and/or replaced. The wires are too short to pull the pump. The water level was high in the septic tank. The septic tank needs additional risers on the outlet end to be properly inspected in the future - could not check the filter. The timer is set to 5.5 minutes every 1 hour. Could not take samples due to the UV not working. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/26/2023 | Jan 1 1900 2:30PM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88698 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Level Sensor Operation" ,"Control Operation" ,"Disinfection" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | ["Level Sensor Operation" ,"Control Operation" ,"Disinfection" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. Zone number 1 had a wet spot and gpm was 2 gallons higher due to broken adapter, replaced fitting ( wet spot should dry out). System had 3 missing valve covers, replaced with new. Treatment looks bad due to something being used at the house, spoke to customer and left copy of DO's and Don'ts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
04/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/22/2023 | 11:22 AM
06/15/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/19/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 04/19/2023 |  | 34.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | Jan 1 1900 12:48PM
03/29/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Septic / Advantex Recirculation Tank |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank-4"sludge 4"scum/ Advantex Recirc. Side-3"sludge 0"scum/ No pump out needed at this time/ Controls, pump, floats and alarms functioning properly/ Recirc. pump intake cleaned/ Counts: Pump Run Time-1285.0 Total Cycles-3319.0 VCOM ID RTU142534/ No breakout or spongy areas on the drainfield and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/21/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | MicroFast | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
07/17/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-87455 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
10/18/2023 | Alternative | RoutineScheduled | 109-06-0255 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Effluent filter installed or maintained | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | System was pumped spring 2022 by FOUTZ- Pump floats opperational, alarm operational on pump. Found high level in the tanks and reset air diaphram to help return to normal level and lowered the settling on the pump tank. about 6-8 inches sludge in septic tank and minimal scum. Treatment tank had ligh water over weir but returned to normal after correcting pump setting and air leveler. Trace of sludge in tank and 2 inch slduge on deck. Pump tank had 8 inch of sludge on bottom. Drainfield appears fine and no leaks in drip apparent. Flushed the drip filter housing filter. System uses timed dosing. System is Operational | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/21/2023 | 09:30 AM
04/20/2023 | Alternative | RoutineScheduled | -STS-43176 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MICROFAST |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | SYSTEM DID NOT NEED TO BE PUMPED. THE BLOWER AND SPIN FILTER WERE CLEANED. CONTROLS WERE OPERATING AS DESIGNED. THE TREATMENT UNIT WAS FUNCTIONING AS DESIGNED. THERE WERE NO VISIBLE LEAKS IN THE DRIP FIELD. LIDS WERE SECURED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | Jan 1 1900 10:00PM
04/01/2023 | Alternative | RoutineScheduled | 133 13 0155 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | [] | [] | [18 empty] | Annual inspection. 2" of accumulated solids in septic tank. Cleaned septic tank solids filter. Septic tank and treatment unit recently pumped out for home sale. Flushed treatment unit spray manifold. 2" of solids in recirculation portion of treatment unit. 0" of solids in discharge portion of treatment unit. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/04/2023 | 07:03 PM
12/11/2023 | Alternative | RoutineScheduled | 2015-143-0069 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/26/2023 |  | Routine/Scheduled | 234-13-18 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 2:30PM
04/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/19/2023 | Alternative | Routine/Scheduled | 157-12-0123 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream (was stopped up - a lot of trash in bottom of tank), changed the filter in the aerator, and changed the mesh screen in the spinfilter. The UV is not working. The septic tank needs to be pumped out and pump the trash from the bottom of the Clearstream tank when doing so. The timer is set to 8 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 09/19/2023 | 10:30 AM
05/02/2023 |  | Initial Visit | 165-STS-335938 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip |  |  | ["Control Operation"] | ["Control Operation"] | [18 empty] | System start up. (was not turned on) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 12:00 AM
05/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/16/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | 12:00 AM
04/13/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Musty | [15 empty] | Inspected | Routine Scheduled inspection on Exhisting system. Septic Tank lite scum 4" sludge, Recirc 14" sludge trace- Pump tank fine sludge trace. Ran in test mode - Alarm and both pumps are operational. Pulled and cleaned RSV & Biofilter. Flushed & Brushed sprayer lines-one 3/4 in ball valve is not openeing and needs replaement, Float switches all operational. Checked settings, Looks good. pumping last year. Hinges are broken on advantex treatment lid but it is still secure with screws. Recirc pump Meter reading 1518.7hours vs 1378.9 hours and 99865 cycles vs 72,216 cycles, Discharge Pump and 152hours vs 139 hours 12835 cycles vs 11760 cycles on discharge pump. Memory is corrupt alarm history is not available. However System is fully operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
03/08/2023 |  | RoutineScheduled | 179-STS-91613 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [5 empty] | 03/08/2023 |  | 19.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Blower 3.15 amps. Little settlement around tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
09/28/2023 | Alternative | Reportable Incident | 157-18-0030 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Came out for alarm call and performed annual maintenance and repairs: -Septic Tank: Normal level 5 in if sludge less than 1 in of solids No signs of infiltration -Discharge/Pump Tank: Normal level Less than 1 in of suspended solids Tested all floats properly working Pulled and cleaned filter Pulled pump took pictures of date code Plumbing intact Pump is properly working and moving water -Aeration: Normal level 10 in of suspended solids Pulled and cleaned diffuser Pulled and cleaned weir Tested float it is functioning properly Air Line intact No signs of infiltration -Air Pump/Blower: 120 volts coming in Pulled cleaned filter Air pressure sensor intact and properly working Air pump housing intact -Control Panel: 120 volts coming in All visual and audible alarms functioning properly Discharge pump pulled 4.13 amps Air pump pulled .86 amps Everything intact and properly working -Drip Field: No signs of surfacing - installed clearstream air pump -installed diffuser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 10:06 AM
10/18/2023 | Alternative | RoutineScheduled | 07-197-A14 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 8.000000 |  | 0.000000 | [11 empty] | Clear, tablets stocked, aerator running, no odor. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
06/03/2023 | Alternative | RoutineScheduled | 133 09 0395 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Flushed treatment unit spray manifold. Sprayed off treatment unit "sheets". Cleaned recirculation pump basket filter. Tested floats, pump and alarm. Excellent treatment. I would suggest replacing air vent, to provide better air flow. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 07:03 PM
05/05/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [9 empty] | 3.000000 | [5 empty] | Will be sent separately | Inspected | Installed new blower Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
11/22/2023 | Alternative | Routine/Scheduled | 07-120-0096A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Trash Tank: Normal level 12 in of sludge less than 1 in of solids No signs of infiltration -Recirculation Tank: Normal level 15 in of suspended solids Tested floats and pump all working as should Pulled and cleaned filter All plumbing intact and pump moving water properly No signs of infiltration Recommend pumping and refilling Pump and floats are aged -RSV (Recirculating Splitter Valve): Male slide intact Took apart and cleaned check ball and housing Intact and properly working -Media Sheets: Brushed and flushed laterals Sprayed sheets off clean Flushed module until water ran clear -Control Panel: 120 volts coming in All visual and audible alarms functional Pump pulled 11.84 amps All components working as should -Distribution Box: Normal level 4 lines all intact and taking water Speed balancers intact and working as should Pulled heavy roots from lines and sidewalls -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | Dec 30 1899 9:03AM
11/27/2023 | Alternative | RoutineScheduled | VAG408203 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.390000 | [14 empty] | Blower replaced on 12/5/2023 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/13/2023 | 02:45 PM
04/04/2023 |  | Pump-Out Only | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic & Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Other"] | NA | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | Jan 1 1900 2:00PM
04/25/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT-3 to Trenches |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | instal IP UPGRADE kit, ran Cat5 cable shallow trenched to home and connected to exhisting wire outside home. Lights blinking, confirmed connection RTU149021 , System is connected to monitoring | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/03/2023 | Alternative | Routine/Scheduled | 073-STS-95066 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Annual Maintenance: -Septic Tank: Found at normal level, found 2in of sludge and 3 in of solids. Pulled and cleaned filter -Discharge/Pump Tank: Found at normal level, found 1in of sludge and less than 1in of solids. Tested floats and pump all working as they should. -Aeration: Found at normal level, 12in of sludge and 4in of solids. Recommend take being pumped and refilled. -Air Pump/Blower: Air pump is not running due to a torn diaphram. Customer Was in a meeting will call in to address air pump. -Control Panel: 120 volts, audio and visual alarms working as they should. Pump pulled 5.7 amps -Distribution Box: Found at normal level, all lines balanced and taking water. No roots or cracks -Drain Field: No signs of surfacing in drainfield area 11/06: * Arrived for pump and refill of aeration tank * Pumped 1000 gallons 11/06: -Installation of a rebuilt Clearstream Compressor No Warranty/Guarantee -Case of Bio One additive (6 Bottles) | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/13/2023 | 08:50 AM
11/08/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.740000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 02:30 PM
03/17/2023 |  | RoutineScheduled | 09-184-5003 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/17/2023 | 12:00 AM
09/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and pumping | 1942001330 | Michelle | McKim | 2.000000 | 1250 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:40PM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | House is not occupied at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
12/27/2023 | Alternative | RoutineScheduled | 107-07-0038 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | [5 empty] | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | return to repair leak in blower air pipe | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
04/13/2023 |  | Routine/Scheduled | 133 17 0032 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 10:15 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-06-0252-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Our staff observed what appeared to be paper towels in the Septic Tank. As a reminder, only toilet paper should be flushed into your system. Paper Towels, or wipes can clog the effluent filter and cause the system to back up. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
03/28/2023 | Alternative | RoutineScheduled | 159-07-0041 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 2.000000 | 1250 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["None"] | [18 empty] | Audio alarm not working on alarm between bldg 4&5 Also primary tank should be pumped in near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | 12:00 AM
03/04/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | MultiFlo ATU |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Cleaned drip manifold spin filter. Removed solids from several treatment unit "socks". Redirected rainfall drainage away from treatment unit and septic tank. 12" of solids in discharge pump tank. I would anitcipate that the septic tank, treatment unit and discharge pump tank will need to be pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 07:03 PM
07/19/2023 | Alternative | RoutineScheduled Component Maintenance | 179-17-0418-VU | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Peat is showing signs of its age (18 years old), but due to light use still providing some treatment (as evidenced by effluent quality in d-box). Recommend proactive replacement of the peat by end of year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
03/20/2023 |  |  | 2007-143-0236 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 1.000000 | 1200 | 1200 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","SludgeScum Accumulation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | None | Clear | 7.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/20/2023 | 11:00 AM
08/10/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV bulb & chord. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
04/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 6"scum/ Microfast-4"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-2484 ETM-377h 8m On-9m 42s Off-1h 51m Peak off-1h 10m/ Peak-14/ High-32/ Watermeter-0,088,763.2/ GPM Zone Rates: Z1-3/ Z2-3 Z3-3 Z4-3/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/20/2023 | Alternative | Reportable Incident | 16-137-0067 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2250 | Norweco |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | NA | Septic | Cloudy | [14 empty] | Inspected | Aerator/Mixer Replaced. Media Filter Cleaned Sludge/Scum Accumulation - Septic 8", ATU, 4" | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/20/2023 | Dec 30 1899 1:30PM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/17/2023 |  | RoutineScheduled | 2105-11-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["Disinfection" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | 6.900000 | 16.900000 |  |  |  | 05/17/2023 |  | 14.000000 |  | 110.000000 | 30.000000 |  |  | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 06/15/2023 | 12:05 PM
02/07/2023 | Alternative | RoutineScheduled | 171-09-0179 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Called due to owner finding pump running long times when not needed. After trouble shooting discivered the Transducer error adjustment was out of spec tricking the board to not function proper. The circuit board has a lot of damager from where a battery had leaked acid and erroded the circuits. Replaced the circuit board and adjusted the transducer setting to which allows it to function like it should. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/01/2023 | 09:30 AM
08/22/2023 | Alternative | RoutineScheduled | 13-113-145 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Distribution Pump Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/22/2023 | 12:00 AM
05/05/2023 | Alternative | Routine/Scheduled | 149-STS-10960 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 2.000000 | 1000 |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | Dec 30 1899 12:00PM
04/27/2023 | Alternative | RoutineScheduled | 115-05-0429 | Campbell | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Best 1 |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/23/2023 | 01:30 PM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | Dec 30 1899 1:44PM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 175-04-0237 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
09/14/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/23/2023 | Dec 30 1899 4:00PM
05/16/2023 | Alternative | Routine/Scheduled | 128.00.166 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Multiflo FTB |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration tank - normal level - mixing present - submersible compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 08:30 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0109 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled Component Maintenance | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 2.000000 | 16600 | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation"] | ["Attached Growth Medium" ,"Dispersal System Operation"] | NA | Musty | Clear | 7.100000 | 4.100000 | [11 empty] | Will be sent separately | Inspected | Report covers the month of October 2023 10-16-23 Mow and weed eat around plant, spread lime 10-19-23 routi9ne site visit, checked drip field, conditions unchanged, finished washing down media and cleaned spinners. Checked airline under AX-1 no water found. Septic tanks: Okay Flow EQ pump tank and lids: Okay no service needed AX Max Units: Spinners Okay Pump Operations: Pumps Operable Drip Field Walkover: Drip field walkover issues, Drip Field needs mowing. Southeast corner of fence has bent post and bent support rods. Chain-link fence is intact. Pump 7 Meter reading: - 16334992.2 Pump 8 Meter Reading: - 12731522.5 Return Meter Reading: - 1206562.77 10-9-2023 pumped 4200- Advantage 10-12-2023 pumped 4200 advantage 10-23-2023 pumped 4200 Advantage 11-1-23 pumped 4000 Advantage | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/16/2024 | 01:58 PM
07/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
08/25/2023 | Alternative | RoutineScheduled | 051-STS-16137 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ATL - Sand System |  | Gravity | Gravity | Pad | Not Applicable | 200.000000 | ["Septic Tank Baffles","Dispersal System Operation","SludgeScum Accumulation"] | ["Septic Tank Baffles","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 12:00 AM
11/03/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1250 | Septic | Pure flow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/08/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-1174 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/08/2023 | Dec 30 1899 2:10PM
07/20/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
05/18/2023 | Alternative | RoutineScheduled | 06-100-1254 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | JEF Septic LLC | 1942001131 | Jason | Fulbright | 8.000000 | 10000 | Nitrex Denitrification Unit | EcoFlo Biofilter | Gravity | Gravity | Mound | UV | 3900.000000 | [] | [] |  | None |  | 7.380000 | 2.850000 |  |  |  | 05/18/2023 | Sample Tap | 3.000000 |  | 1.000000 | 5.000000 | 3.500000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/09/2023 | 12:00 PM
10/20/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation"] | [18 empty] | FAST cleaned, pumped out and filter replaced | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/20/2023 | 12:00 AM
05/18/2023 | Alternative | RoutineScheduled | 09-100-0388 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Puraflo | Gravity | Pressure | Pad | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/25/2023 | 02:45 PM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-91954 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation"] | NA | Musty | Cloudy | [5 empty] | 10/30/2023 |  | 29.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Treatment cloudy due to grease and wipes, spoke to customer and provided copy of Do's and Don'ts. Leak on pump tank riser (grommet for J-box) 2 dial flows need a little adjustment, called installer and he said he will take care of both problems this week. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
03/16/2023 |  | RoutineScheduled | 12-192-022 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation","Effluent Screens","Dispersal System Operation","Control Operation","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | 12:00 AM
03/01/2023 | Alternative | Initial Visit | 157-16-0105 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Pressure | Pad | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - Real Estate Inspection. Trash Tank - normal level Aeration Tank - mixing present - compressor serviced. PUmp Tank - float sensors, pump and controls operating. UV - Obsidian Pressure unit - bulb functioning - not able to be serviced. LPP Pad - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/02/2023 | 08:00 AM
07/20/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Other"] | ["Other"] | [8 empty] | 07/20/2023 | Sample Chamber |  |  | 23.000000 | [5 empty] | Follow up only: Sample for Fecal Coliform | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/10/2023 | Alternative | RoutineScheduled | 18-100-0018 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/13/2023 | Alternative | Routine/Scheduled | 127-STS-35225 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 9:30AM
12/26/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-15876 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 250.000000 | [] | [] | NA | [7 empty] | 12/19/2023 | Sample Chamber | 2.000000 |  |  | 23.800000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/09/2024 | 12:00 AM
09/06/2023 | Alternative | RoutineScheduled | 11-100-0163 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1500 | BIOCOIR |  | Pump | Gravity | Mound | UV | 450.000000 | [] | [] | YES | [16 empty] | Pumped Out | REPLAED UV LIGHT BULB, REPIPED DRAINAGE PIPE FROM BOTTOM OF BIOCOIR TANK, REPLACED FIBER, | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/05/2023 | 12:25 PM
03/17/2023 |  | RoutineScheduled | 2016-143-0145 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 3000 | 1500 | 1500 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","Control Operation","Attached Growth Medium","Distribution Pump Operation","SludgeScum Accumulation"] | YES | None | Clear | 7.000000 |  | 6.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | 01:00 PM
12/11/2023 | Alternative | Routine/Scheduled | 136-08-0560 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal level 2 in of sludge less than 1 In of solids Pulled and cleaned filter No signs of infiltration Discharge/Pump Tank Condition of above Component Notes for above Component Normal level Tested floats and pump all working as should All plumbing intact and pump moving water properly No signs of infiltration Peat Moss Condition of above Component Notes for above Component Dispersal trays and tipping bucket intact Peat moss in good condition no standing water or root intrusion Raked peat moss and module is intact Control Panel Condition of above Component Notes for above Component 120 volts coming in Visual alarm light is functional however audible buzzer is not Pump pulled 7.5 amps All components working as should Panel is aged and starting to deteriorate Distribution Box Condition of above Component Notes for above Component Normal level 3 lines all intact and properly taking water No cracks or bowing Speed balancers intact and functional Drain Field Condition of above Component Notes for above Component No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:43 PM
01/19/2023 |  | RoutineScheduled | 154-10-0116 | Louisa | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Disinfection" ,"Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Pungent | Discolored | [13 empty] | Will be sent separately | Inspected | As noted on last year's inspection, the UV light is not working. Because of this, we did not take an effluent sample. We also continue to recommend replacing the EZ Set lid on the Septic Tank. Finally, we also recommend pumping the septic tank & Advantex RT unit (with our staff present) due to scum & sludge accumulation in the tanks. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/01/2023 | 12:05 PM
08/04/2023 | Alternative | Reportable Incident |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation"] | NO | [17 empty] | AOSS - Initial Visit - ALARM EVENT Discharge pump failed - high level alarm event. Replaced discharge pump and float sensors. Need to reschedule for any other maintenance after water level in biofilter pumps down. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 10:45 AM
03/21/2023 |  | Routine/Scheduled | 036-STS-34313 | Charles City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/21/2023 | Jan 1 1900 3:44PM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-499 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. System was on high level when we showed up due to a bad Omron timer, replaced timer and R.O float and panel started working. Advised customer to minimize water usage. Media showing its age and is breaking down, looks like will need replacement next year, will evaluate it next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
03/13/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Floats replaced. System should begin to function correctly shortly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/28/2023 | Alternative | RoutineScheduled | SD-13-062 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic Tank | PuraFlo | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles","SludgeScum Accumulation","Attached Growth Medium","Effluent Screens"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | Septic | Cloudy | [5 empty] | 05/01/2023 | Sample Chamber | 230.000000 | [5 empty] | Attached to this report |  | Pump-out is scheduled | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/25/2023 | 12:00 AM
10/27/2023 | Alternative | RoutineScheduled Component Maintenance | 177-10-0130-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
01/02/2023 |  |  | 01-192-214 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 01/02/2023 |  | 6.200000 |  |  | 1.600000 |  |  | Will be sent separately |  | BOD: 6.20 TSS: 1.60 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/02/2023 | 12:00 AM
07/14/2023 | Alternative | RoutineScheduled Component Maintenance | 179-11-0110-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
05/02/2023 |  | RoutineScheduled | 107-00-0242 (LEGACY ALT. SYSTEM) | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | repaired float | This AOSS should now return to normal function after having provided the above state routine maintenance | 06/21/2023 | 03:35 PM
12/08/2023 | Alternative | Follow-Up | 07-197-A10 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination | [9 empty] | 0.000000 | [11 empty] | Tablets are now installed | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12:00 AM
02/02/2023 | Alternative | Routine/Scheduled | 166-07-208 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | 05:44 PM
12/20/2023 | Alternative | RoutineScheduled | 08-120-0097R | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 12:00 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
07/07/2023 | Alternative | RoutineScheduled | 2007-143-0004 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 12:00 AM
10/19/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/03/2023 | 12:00 AM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Strongly recommend moving the new tree that is in between the lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/23/2023 | Alternative | RoutineScheduled | SD-15-62 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1800 | septic | AquaSafe | Gravity | Pressure | Discharge | UV |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/12/2023 | 12:15 PM
08/18/2023 | Alternative |  | 18-100-0472 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
01/03/2023 |  | RoutineScheduled | TWOR-9ZARVG | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | JEF Septic LLC | 1942001131 | Jason | Fulbright | 1.000000 | 1000 |  |  | Pump | Pressure | Drip | UV | 300.000000 | [] | [] | YES | None | Clear | 7.110000 | 3.150000 |  |  |  | 01/03/2023 | Pump Chamber | 2.000000 |  | 8.000000 | 14.200000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | Jan 1 1900 11:00AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance | 2090-04-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 6.900000 | 5.900000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 07/11/2023 | 11:24 AM
03/15/2023 |  | RoutineScheduled | 02-172-0347A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | Advantex |  | Gravity | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/16/2023 | Jan 1 1900 11:10AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
12/06/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
06/15/2023 |  |  | 033-18-0154-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Advantex | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/08/2023 | Alternative | Routine/Scheduled | 159-STS-94977 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/08/2023 | 02:53 PM
12/06/2023 | Alternative | RoutineScheduled | 175-08-0565 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-10"sludge 4"scum/ Microfast ATU-16"sludge/ Pump Tank-2"sludge/ Pump out required on the Septic-Microfast Tank/ Blower air filter cleaned and blower working correctly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-79407 ETM-118217/ No breakout or spongy areas on the drainfield and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/05/2023 | Alternative | Routine/Scheduled |  | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chickahominy | James Lee Miller III | 1942001468 | Kevin | Blasing | [29 empty] | Maintenance and Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/14/2023 | Dec 30 1899 10:02AM
01/15/2023 | Alternative | RoutineScheduled | SD-02-323 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 2000 | septic | Advantex | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/18/2023 | 10:00 AM
01/03/2023 |  | Routine/Scheduled | 234-14-131 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 8.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2023 | Jan 1 1900 2:10PM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 137-STS-24526 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Auxiliary Filter"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The EZ Set lid on the septic tank is damaged and should be replaced. When we replace the lid, we would like to further evaluate the lower area of the drip dispersal field. We would want to turn off the pump long enough to allow there to be sufficient water to fully test the system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
07/28/2023 | Alternative | RoutineScheduled Component Maintenance | SP-05-212 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 2.73 amps. Treatment is crystal clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
10/18/2023 | Alternative |  | 124-STS-2379 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge |  |  | David | Paley | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/15/2023 |  | Follow-Up | 179-14-0124-SP | Stafford | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 2.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed inlet riser on septic tank. Sealed wedge lid on pump tank. Assisted pumper with cleaning of tanks. | This AOSS should now return to normal function after having provided the above state routine maintenance | 06/01/2023 | 04:39 AM
06/15/2023 | Alternative | Routine/Scheduled | S102-07-0063 | Alleghany | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | EcoPure |  | Gravity | Gravity | Trenches | Not Applicable |  | Attached Growth Medium | ["Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/15/2023 | Jan 1 1900 10:15PM
05/30/2023 |  | Reportable Incident | {FIPSCode}-STS-1492 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | Jan 1 1900 1:00PM
02/07/2023 |  | RoutineScheduled | 03-197-A3 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 10 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/07/2023 | 12:00 AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Two of the lines (2/5) appeared to be more nitrified and receiving more effluent. Distribution Box was uncovered and Dialflows were adjusted. System should return to proper design function now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/29/2023 |  | Follow-Up |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] | [18 empty] | I reivisited to resample due to a high BOD result. I determined that the BOD had been collected pre- treatment and there is not a location from which to collect a final sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 02:00 PM
06/19/2023 | Alternative | Follow-Up | 09-160-0019 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | [18 empty] | 06-01-23 visited site, completed inspection, blower non functional 06-19-23 replaced blower, everything functioning at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/11/2023 | Alternative | RoutineScheduled | 115-11-0204 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank | Ecoflo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge levels-under 1" scum & 4-6" Sludge in Septic tank. Pump Chamber trace-2" fine sludge. Cleaned Effluent screen. Minor backup. Alarm functional and pump is operational, Peat had puddling in all four quadrants. Turned peat and broke up clumps allowing for ponding water to drain. Tested pump and alarm and both floats operational however, I noted the Pump float has some hesitiation to start when engaged. System was pumped 2 years ago | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 09:30 AM
09/13/2023 | Alternative |  | 177-07-0411-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
02/13/2023 |  |  | 2016-143-0141 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/15/2023 | 12:00 AM
06/26/2023 | Alternative | Routine/Scheduled | 043-04-0099 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  | 450.000000 | Effluent Screens | Effluent Screens | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | 11:04 AM
07/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
09/11/2023 | Alternative | RoutineScheduled | 181-05-0401 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system did not need to be pumped. The blower and spin filters were both cleaned. The treatment unit was in good operating condition. The controls were operating as designed. There was return effluent returning to the pump tank, so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | 09:45 PM
05/23/2023 | Alternative | RoutineScheduled | 171-12-0164 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20-RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | RTU126896 - Sludge level-1-2" scum layer on top(fat,oil,grease)-14" sludge on bottom in Septic tank - Recirc zone of tank 10" sludge, Discharge zone of pump tank 6-10" sludge, Clear Effluent on top, Pump Dosing tank in Field had a trace of sludge. We cleaned Effluent filter,Pump is PF0150311), Spray pattern improved after cleaning and flushing the pump. Dischagre pump operational . Both Alarms operational, all floats tested operational. RK control panel in drainfield had a reading. Meter readings- Recirc pump -1804.5hrs and 17633 cycles vs 1378.6 hours and 86,136 Cycles - Discharge Pump 404 min and 4773 Cycles. RK Control panel dosing Pump test good.discharge pump run time 524,8 hours and 6191 cycles, 2577 days in history. Found leak in drip drainfield and owner repaired after my visit | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | 09:30 AM
08/25/2023 | Alternative | Routine/Scheduled | 155-STS-12881 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 10.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 04:30 PM
08/11/2023 | Alternative | RoutineScheduled | 15-192-034 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ELJEN |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation"] | ["Septic Tank Baffles","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
02/22/2023 | Alternative | Routine/Scheduled | 157-06-0005 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - no riser access. Secondary septic tank - normal level - effluent screen serviced. Pump Basin - float sensors, pump and controls operating - minor bulging of chamber noted. BioFilter - peatmoss in poor condition - recommend replacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/23/2023 | 08:15 AM
03/30/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | replaced discharge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/22/2023 | 11:15 AM
06/13/2023 | Alternative | Routine/Scheduled | 136-08-0060 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Biofilter - concrete - peatmoss in good condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact - recommend replacing seals. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 09:00 AM
04/06/2023 |  | RoutineScheduled | 177-10-0201-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
02/28/2023 | Alternative | Routine/Scheduled | 18-174-0103 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/28/2023 | Dec 30 1899 11:38AM
04/05/2023 |  | Reportable Incident |  | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced fractured plastic DBox with new 8 port concrete DBox. Spliced to existing conveyance line. Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/06/2023 | Jan 1 1900 7:00AM
02/03/2023 |  | Routine/Scheduled | 234-16-385 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | Jan 1 1900 9:15AM
09/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | check about payment | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/13/2023 | 01:07 PM
04/19/2023 |  | RoutineScheduled | VAG408147 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | SEPTIC TANK ONLY | SAND FILTER | Pump | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | NA | [17 empty] | SYSTEM DID NOT NEED TO BE PUMPED. THE CONTROLS WERE OPERATING AS DESIGNED. THERE WERE NO VISIBLE LEAKS IN THE CONVEYANCE LINES. THE SAND FILTER WAS OPERATING AS DESIGNED. CHLORINATION AND DECHLORINATION TABLETS WERE ADDED TO THE TABLET FEEDER. THERE WAS NO DISCHARGE AT TIME OF VISIT. LIDS WERE SECURED. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/01/2023 | 09:50 PM
11/29/2023 | Alternative | Routine/Scheduled | 228-16-0418 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/29/2023 | Dec 30 1899 11:50AM
09/12/2023 | Alternative | RoutineScheduled Component Maintenance | 179-15-0126-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Blower 2.84 amps. Septic tank needs pump out due to solids in treatment side. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
06/17/2023 | Alternative | RoutineScheduled | 2116-06-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.300000 |  |  | 1.900000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/02/2023 | 12:00 AM
04/17/2023 |  | Reportable Incident |  | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | Dispersal System Operation | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Replaced dilapidated DBox with new 8 port concrete dbox. Spliced to existing conveyance line Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | 07:00 AM
05/18/2023 |  | Routine/Scheduled | 234-18-098 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | Jan 1 1900 10:55AM
09/18/2023 | Alternative | RoutineScheduled Component Maintenance | 107-16-0043 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | NA | [7 empty] | 09/18/2023 |  | 53.000000 | [5 empty] | Will be sent separately | Inspected | Fixed...pump electrical, psi, air vent Installed spin clean filter Repaired leak in drainfield cause by installing fence through field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
02/28/2023 |  | RoutineScheduled | 101-06-0216 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | BEST1 |  | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
12/18/2023 | Alternative | RoutineScheduled | 06-160-0260 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 3.000000 | 3000 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/20/2023 | 12:00 AM
07/12/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20280 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Sulphitic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
07/13/2023 | Alternative | RoutineScheduled | 09-172-0132A Disc | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco | Sand Tank | Gravity | Pressure | Discharge | UV | 450.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES |  |  | 6.500000 | 8.300000 |  |  |  | 07/13/2023 | Sample Chamber | 5.000000 |  | 1.000000 | 2.660000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 12:00 AM
01/19/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | DeHaven's Backhoe Service Inc. | 1942001541 | Wayne | Edmonson | 1.000000 | 1500 | Advantex |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | 01:00 PM
05/05/2023 | Alternative |  | 065-STS-32239 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Mark | Griffin | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/07/2023 |  |  | ST-04-322 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Puraflo | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
08/22/2023 | Alternative | Routine/Scheduled | 2016-143-0137 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | NO | [17 empty] | Flushed manifold and disc filter. Changed uv bulb. Not enough water to flush field. Cleaned rsv. Changed discharge off time to 3 hrs. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | 01:49 PM
10/12/2023 | Alternative | Routine/Scheduled | 228-13-0311 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | Dec 30 1899 10:20AM
09/29/2023 | Alternative |  | 14-100-0361 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
10/24/2023 | Alternative | RoutineScheduled | 182-04-0629 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/24/2023 | 12:00 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0039-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Clogged septic filter, cleaned. Roots in all 5 pods cut them on outside if they grow back in will need to take trees down next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 07:39 AM
12/23/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 300 | BioMicrobics MicroFast |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | NA | [17 empty] | 2023 annual inspection. Blower not operational. Replaced blower on 1-13-2024. Cleaned drip manifold spin filter. Cleaned discharge pump intake screen. 22" of accumulated solids in septic tank. 20" of solids in treatment unit. Septic tank and treatment unit will have to be pumped out next year. This system has been very problematic over the years with electrical issues. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/16/2024 | 07:03 PM
02/02/2023 | Alternative | RoutineScheduled | SD-15-62 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1800 | septic | Aquasafe | Gravity | Pressure | Discharge | UV |  | [] | [] | YES | None | Clear |  | 8.600000 | [13 empty] | Informal | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/17/2023 | 08:20 AM
03/15/2023 | Alternative | RoutineScheduled | SD-04-111 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation" ,"Disinfection" ,"Attached Growth Medium"] | ["Disinfection" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Discolored |  | 5.440000 | 5.000000 | 0.030000 |  | 03/15/2023 | Sample Chamber | 13.000000 |  | 1.000000 | 5.800000 |  |  | Will be sent separately | Inspected | We recommend pumping the Septic Tank due to sludge accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
07/25/2023 | Alternative | RoutineScheduled | 179-07-0385-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Pad | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/28/2023 | 10:45 AM
04/18/2023 |  | RoutineScheduled | 2019-143-0049 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Pressure | Drip |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Auxiliary Filter","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | 12:00 AM
10/04/2023 | Alternative | Initial Visit | S 800-17-0228 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the aerator not running. Serviced system. Checked the pump and panel (ok). Installed an aerator rebuild kit. The aerator needs to be raised. Re-secured the pump float. Replaced the alarm light bulb. The Clearstream tank needs to be pumped as well as the septic tank. The timer is set to 3 minutes every 2 hours. Could not get the sample due to the aerator not working on arrival. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | Dec 30 1899 3:30PM
12/19/2023 | Alternative |  | {FIPSCode}-STS-19461 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/19/2023 |  | 4.530000 |  |  | 6.700000 |  |  | Will be sent separately |  | BOD: 4.53 TSS: 6.70 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
04/27/2023 |  | Routine/Scheduled | 228-14-0398 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | Jan 1 1900 3:15PM
01/31/2023 |  | Routine/Scheduled | {FIPSCode}-STS-1841 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [14 empty] | Replaced diffuser and air assembly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 3:03PM
08/10/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | McKim Septic and Pumping | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Dispersal System Operation"] | NA | [17 empty] | Repaired all 6 air release valves and piping that were broken. septic system is working as it should | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/11/2023 | Dec 30 1899 11:00AM
08/04/2023 | Alternative | Reportable Incident Component Maintenance | SD-11-168 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm would randomly sound, but the red light was not illuminated. Float switch was intermittently closing part way, enough to sound the alarm. Replacing the alarm float switch cleared all of that up. Did a quick check of the pump intake and found it to be clear. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0079-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Bionest | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Home is only periodically occupied. Treated effluent looks very good. The monitored rate of 5.5 gpm was obtained by running the drip pump with the filter flush and field flush ball valves left in their normal positions (so continuous flushing was occurring). After a 6 min run time, the water level had dropped approximately 37.5 gallons. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 09:40 AM
12/12/2023 | Alternative | Routine/Scheduled | 095-STS-6957 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | Dec 30 1899 9:00AM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
07/17/2023 | Alternative |  | 17-142-0391 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
04/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank riser has a big hole in it and needs to be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
01/17/2023 | Alternative | Routine/Scheduled | 151-03-352 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/17/2023 | 06:36 PM
01/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/29/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 12" of accumulated solids in septic tank. Flushed treatment unit spray manifold. Cleaned recirculation pump basket filter. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 07:03 PM
11/17/2023 | Alternative | Routine/Scheduled | 136-14-0282 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Real estate inspection: Septic Tank Depth to the top of the Septic Tank 0-12" below grade Riser present? Yes Condition of Lid: Intact Was Septic Tank pumped? No Does tank require pumping? No Size of the Septic Tank 1000 gallons Tank Level Normal operating level Sludge Judge Levels Less than 1"of sludge and solids Condition of Inlet Tee Satisfactory Condition of Outlet Tee Satisfactory Effluent Filter present? No Septic Tank - Additional Notes Discharge Tank Depth to the top of the Discharge Tank 0-12" below grade Riser present? Yes Was the Discharge Tank pumped? No Does tank require pumping? No Sludge Judge Levels Less than 1in of suspended solids Condition of Lid: Intact Discharge Tank - Additional Notes Peat Moss Number of modules 1 Was peat moss serviced at time of inspection? Yes Condition of Peat Satisfactory Peat Moss - Additional Notes Peat moss is in New condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 10:37 AM
11/27/2023 | Alternative | Initial Visit Component Maintenance | 099-STS-93139 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | New 4 bedroom house & septic, daily flow set for maximum of 480 gallons. Reset all "R" counts to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
02/10/2023 |  | RoutineScheduled | 179-12-0196-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 2-2 0-5 | 0-2 | Pump | Pressure | Mound | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 6.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 02:00 PM
12/07/2023 | Alternative | Routine/Scheduled | 07-120-0044A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Water level normal. No riser access. Not due for pump out Discharge/Pump Tank Condition of above Component Notes for above Component Water level normal. Tested and confirmed that discharge pump is operating properly. Tested and confirmed that discharge float sensors are operating properly. Discharge riser is concrete. Discharge floats are not properly secured and have exceeded life expectancy. Discharge pump plumbing is not within serviceable reach. Groundwater infiltration within discharge tank Aeration Condition of above Component Notes for above Component Water level normal. Effluent screen assembly is breaking apart. Did not service effluent screen. Not due for pump out Air Pump/Blower Condition of above Component Notes for above Component Checked and confirmed aerator is functioning properly. Flushed and cleaned aerator. Control Panel Condition of above Component Notes for above Component Checked and confirmed components within control panel are functioning properly. Checked and confirmed audible alarm is functioning properly. Checked and confirmed visual alarm is functioning properly. Distribution Box Condition of above Component Notes for above Component Water level normal. Removed root infiltration. Distribution box is degrading. Roots have grown through the sidewall Drain Field Condition of above Component Notes for above Component Found no signs of surfacing on dispersal field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 12:02PM
01/05/2023 |  | RoutineScheduled | 175-17-0567 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Advantex Recirc. Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [7 empty] | 01/05/2023 | Pump Chamber | 26.000000 | [5 empty] | Attached to this report |  | Septic-3"sludge 2"scum/ Advantex Recirculation Treatment Side-3"sludge 0"scum/ Pump Tank-0"sludge 0"scum/ No pump out needed at this time/ Recirc pump intake cleaned/ Controls, pump, floats and alarms functioning properly/ Counts: Pump Run Time-47.6 Cycles-443/ Recirc Run Time-83.6 Cycles-15970/ Watermeter-00316/ AX-20 media in good condition at this time/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/22/2023 |  | Pump-Out Only | 01-120-0209A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Supervised pumpout of primary septic tank by Commonwealth Waste Solutions. No refill required. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | Jan 1 1900 7:30AM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | NA | [17 empty] | Septic Tank-4"sludge 8"scum/ Microfast ATU-12"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ Septic-Microfast Tank requires chemical cleaning and pump out due to clogging of the media/ Blower air filter cleaned and blower working correctly/ UV-Light sleeve cleaned and light is functioning properly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-6304 ETM-630h 8m On-6m Off-1.5h/ Peak-15/ high-12/ Watermeter-0,176,427.67/ No breakout or spongy areas on the drip field and dosing correctly. Returned on10/20/2023 for the chemical cleaning and pump out. Microfast now functioning properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
10/26/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced 4 control floats. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/15/2023 | Dec 30 1899 2:02PM
08/09/2023 | Alternative | Routine/Scheduled | 06-120-0217A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/09/2023 | Dec 30 1899 10:00AM
03/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92602 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | We did not see any evidence that the drip dispersal system was not working properly, but we were unable to locate the air release valves. A follow-up for more exploration is planned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
09/25/2023 | Alternative | RoutineScheduled | 166-14-055 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | sludge checked, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/05/2023 | Alternative |  | -STS-92398 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank lid has some cracks. Strongly recommend before it becomes a safety hazard. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/09/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
03/06/2023 |  | RoutineScheduled | 153-STS-20305 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
01/16/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
09/21/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Gravity | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
06/28/2023 | Alternative | Routine/Scheduled | 151-10-0066 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Ecoflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/28/2023 | 04:07 PM
06/23/2023 | Alternative | Routine/Scheduled | 234-18-242 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | Dec 30 1899 8:00AM
03/07/2023 |  | RoutineScheduled | 051-STS-17598 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ATL |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 12:00 AM
08/25/2023 | Alternative | RoutineScheduled | 03-125-239 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Septic Tank Baffles","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/25/2023 | 12:00 AM
01/04/2023 |  | RoutineScheduled | 175-04-0935 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | 11:08 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0101 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
01/30/2023 |  | RoutineScheduled |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
03/10/2023 | Alternative | RoutineScheduled | 04-160-0229 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 1000 | Ecoflo (peat moss) |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [16 empty] | Inspected | - recommend septic tank (1000gal) to be pumped/cleaned | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/20/2023 | 12:00 AM
05/12/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Pressure | Pad |  | 450.000000 | None | None | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | 12:26 PM
01/24/2023 | Alternative | Reportable Incident | 151-03-123 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump tank - float sensors, pump and controls operating. BioFilter - 5 Modules - peatmoss in good condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | 10:15 AM
05/23/2023 |  | RoutineScheduled | 175-02-0566 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-4"sludge 2"scum/ Microfast ATU-6"sludge/ Pump Tank-2"sludge/ No pump out needed at this time/ Blower air filter cleaned and working correctly/ Controls, pump, floats and alarms functioning properly/ Counts: Pump-6005 ETM-48070/ Watermeter-362,233.07/ No breakout or spongy areas on the drip field and dosing properly on all 3 zones. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/29/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20503 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
03/29/2023 |  | RoutineScheduled | {FIPSCode}-STS-8890 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Disinfection","Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 4 Chlorine 6 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/29/2023 | 12:00 AM
04/14/2023 |  | RoutineScheduled | 132-06-0263 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | 12:00 AM
12/05/2023 | Alternative | Reportable Incident Component Maintenance | SD-05-457 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | High level alarm at inside panel after fairly significant rain. Infiltration observed at septic riser joints on septic inlet and pump tank outlet - need to be resealed. May also have infiltration where Microfast plastic top meets top of concrete tank, no way to see. Recommended removal of mulch from around tanks as it acts like a giant sponge and increases infiltration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | 12:58 PM
09/05/2023 | Alternative | Follow-Up Component Maintenance | 061-16-335 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sealed field flush return line in pump tank. Sealed all 3 sets of risers on FAST tank. Sealed airline grommet on FAST. Sealed pump tank inlet and outlet risers. Sealed outlet pipe on pump tank. Float cord would not pull through so we installed an internal splice box and used existing floats. Homeowner had tanks pumped out prior to repairs by others. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
11/01/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/01/2023 | Dec 30 1899 12:39PM
04/03/2023 | Alternative | RoutineScheduled | 159-09-0024 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/26/2023 |  | Routine/Scheduled | {FIPSCode}-STS-5697 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/25/2023 | Jan 1 1900 11:00AM
04/26/2023 |  | RoutineScheduled | 033-16-0117-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air line from blower to the Whitewater unit appears to be obstructed. No aeration is occurring. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0104 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
01/31/2023 |  | Follow-Up | 179-10-0086-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [7 empty] | 01/03/2023 |  | 6.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
08/14/2023 | Alternative |  | 147-12-0098 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Parsley Septic Tank , Inc. | 1942001106 | James | Parsley | 1.000000 |  | Clearstream |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/15/2023 | 12:00 AM
01/19/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 1.000000 | 1500 | Septic To Fast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [18 empty] | 4" of scum at the inlet, full of sludge. thin layer of scum and 24' of sludge in the middle. effluent at the sample box is clean, blower is working, Alarm is working, Field looks good, Working as designed, but recommend hat the tank is pumped and everything is cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/19/2023 | 11:00 AM
11/08/2023 | Alternative | RoutineScheduled | 109-14-0120 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge level-scum under 1" and 8-10" Sludge in Septic tank. 6" trace Sludge in treatment, 6" trace sludge in Pump tank. Found No leaks in the drain field. Cleaned air filter, Effluent filter and spin filter. flushed both solenoid control valves in manual. Good aeration noted in treatment tank. Pump cycle count 6555vs 5532 last year - 1023 cycles since last visit , ETM( time) 20739 vs 17099 min last year = 36401 min or 60.6 hours since last visit. 48 HLA-high alarm, secondary county 774, Power failure 83 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
08/03/2023 | Alternative | RoutineScheduled | 2010-143-0012 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | REPLACED: MICROFAST BLOWEE,ALARM FLOAT, AND INSPECTION CAP | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/04/2023 | 12:00 AM
09/28/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/31/2023 | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled | -STS-26126 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | MicroFast .075 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["Effluent Screens","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | 09:30 AM
09/30/2023 | Alternative | RoutineScheduled | 151-17-002 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service | 1942001034 | Kent | Cuthbertson | 4.000000 | 45000 | 15000 | 15000 | Pump | Gravity | Trenches | UV | 22077.000000 | ["None"] | ["None"] | YES | [15 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/30/2023 | 03:00 PM
01/20/2023 |  | RoutineScheduled | 177-17-0129-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
03/01/2023 | Alternative | RoutineScheduled | 047-17-198 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
12/14/2023 | Alternative | RoutineScheduled Component Maintenance | SD-14-243 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 02:30 PM
04/25/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Gravity | Drip | Not Applicable |  | ["None"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | None | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | 12:00 AM
12/05/2023 | Alternative | Routine/Scheduled | 166-09-034 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Trash Tank Condition of above Component Notes for above Component Normal level 1 in of sludge less than 1 in of solids No signs of infiltration Recirculation Tank Condition of above Component Notes for above Component Normal level 12 in of suspended solids Tested floats and pump all working as should Pulled and cleaned pump All plumbing intact and pump moving water properly No signs of infiltration RSV (Recirculating Splitter Valve) Condition of above Component Notes for above Component Taken apart cleaned check ball and flushed inside Male slide intact and working as should Discharge/Pump Tank Condition of above Component Notes for above Component Normal level Less than 1in of suspended solids Tested floats and pump all working as should All plumbing intact and pump moving water properly No signs of infiltration Media Sheets Condition of above Component Notes for above Component Brushed and flushed laterals Sprayed media sheets clean All cups in correct places and functional Flushed module until water ran clear Control Panel Condition of above Component Notes for above Component 120 volts coming in All visual and audible alarms functional Recirc pump pulled 11.4 amps Discharge pump pulled 10.1 amps All components working as should Distribution Box Condition of above Component Notes for above Component Unable to locate Drain Field Condition of above Component Notes for above Component No signs of of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 09:47 AM
09/28/2023 | Alternative | RoutineScheduled | 177-06-0460-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 1.000000 | 1500 | 0-2 | 0-4 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Control Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 4.000000 | [11 empty] | Inspected | system cleaned and functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/28/2023 | 10:00 AM
10/11/2023 | Alternative |  |  | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Crater | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation"] | YES | Pungent | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/11/2023 | Dec 30 1899 1:00PM
07/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Tanks were pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
12/06/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/06/2023 | Dec 30 1899 9:00AM
05/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
07/31/2023 | Alternative | Routine/Scheduled | 550-STS-6912 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | Dec 30 1899 11:35AM
01/18/2023 |  | Routine/Scheduled | 234-15-182 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [12 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/26/2023 | Jan 1 1900 8:50AM
01/27/2023 |  | Reportable Incident | Legacy | York | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | Dispersal System Operation | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | COSS - Maintenance - GMP2018-02 Primary septic tank - normal level Replaced dbox with new 8 port concrete DBox spliced to existing Conveyance Line Spliced to existing header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/30/2023 | Jan 1 1900 9:00AM
04/20/2023 | Alternative | Reportable Incident Component Maintenance | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Drip | UV |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired force main in sewage pump tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | Dec 30 1899 1:44PM
09/27/2023 | Alternative | RoutineScheduled | 04-100-0266 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 2.000000 | 750 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 300.000000 | [] | [] | [18 empty] | SLUDGE JUDGE OF SEPTIC TANK REVEALED 2-3" FROM BOTTOM AUGERED PEAT-LEAKS GOOD EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/08/2024 | 10:40 AM
10/18/2023 | Alternative | Reportable Incident | 166-14-137 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced uv bulb, ballast, & pump relay | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
02/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/20/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Gravity | Gravity | Pad | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Puraflo modules holding water. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
01/23/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 08:25 AM
12/14/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-489 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 02:30 PM
01/26/2023 |  | RoutineScheduled |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Gravity | Discharge | UV | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/28/2023 | 12:00 AM
03/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
02/10/2023 |  | RoutineScheduled | 04-197-176 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Advantex |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/10/2023 | 12:00 AM
02/15/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The plastic d-box is broken and filled with roots. D-box needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1250 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/15/2023 | Alternative | RoutineScheduled | 16-137-0134 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1000 | Multiflo |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
04/26/2023 |  | Routine/Scheduled | 550-STS-5887 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 9:05AM
09/23/2023 | Alternative | RoutineScheduled | 163-STS-337566 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only |  | Pump | Pressure | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | The system did not need to be pumped. The controls were operating as designed. The spin filter was pulled and cleaned. There were no visible leaks in the LPD leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 05:30 PM
10/10/2023 | Alternative | RoutineScheduled | 182-07-0084 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | pump set on "hand" at arrival | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/10/2023 | 12:00 AM
10/23/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-15912 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/24/2023 | Alternative | RoutineScheduled | 10-100-0305 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | BIOCOIR |  | Pump | Gravity | Pad | UV | 600.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE TEST REVEALED 3-4" FROM BOTTOM CHANGED UV LIGHT UNIT EVERYTHING WORKING AS IT SHOULD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/16/2023 | 02:35 PM
04/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
02/06/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | reccomend pump all tanks | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
04/25/2023 | Alternative | RoutineScheduled | SD-12-329 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens"] | YES | [7 empty] | 04/25/2023 | Sample Chamber | 21.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | 04:00 PM
06/06/2023 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [9 empty] | Level Sensor Operation | Level Sensor Operation | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/13/2023 | 01:13 PM
01/05/2023 |  | RoutineScheduled | {FIPSCode}-STS-25788 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton |  |  | Advantex |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Recirculation Pump","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | 12:00 AM
04/08/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/09/2023 | 12:00 AM
08/31/2023 | Alternative | Routine/Scheduled |  | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Pump tank - float sensors, pump and controls operating DBox - not examined - ground bees present! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/06/2023 | Dec 30 1899 11:00AM
07/13/2023 | Alternative | RoutineScheduled | 175-08-0071 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Pump Tank to Puraflo Modules to Discharge Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [17 empty] | Septic Tank-5"sludge 0"scum/ Pump Tank to Puraflo Modules-2"sludge/ Discharge Pump Tank-2"sludge/ No pump out needed/ Puraflo Peat turned in all 6 modules and in good condition at this time/ Controls, pumps, floats and alarms functioning properly/ Counts: Puraflo Pump- 17500 ETM-22029/ Counts: Discharge Pump-4992 ETM-25121/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/14/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/30/2023 | 12:00 AM
10/13/2023 | Alternative | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Biomicrobics Fast 1.5 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Checked sludge volume - Minimal scum layer on top and 3 inch sludge on bottom in big tank. Treatment tank had minimal scum and 10 inches of sludge on bottom. Noted 1 wipe floating in tank visable, do nut use wipes and post for renter to not use them. Tank does not need pumping. Alarm test good. Initial visit on a recent upgrade install of a Biomicrobics Fast 1.5 treatment system. It has a 1/2hp 0.5 Hp blower motor, Motor running good, good aeration in tank. Motor produces a slight wine but appears to be fine. Cleaned Blower air filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/17/2023 | 09:30 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend mowing the drainfield area to aid in evapotranspiration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/05/2023 | Alternative | Routine/Scheduled | 149-STS-10851 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Crater | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 1000 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/05/2023 | Dec 30 1899 1:30PM
01/16/2023 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced timer enable float. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/15/2023 | Jan 1 1900 7:20PM
03/02/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/13/2023 | Jan 1 1900 11:23AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0261 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
08/28/2023 | Alternative | RoutineScheduled | 98-197-428 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 | [11 empty] | None | Clear | 7.500000 | 7.000000 |  | 0.000000 | [11 empty] | Added tablets during inspection. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
12/13/2023 | Alternative |  | 06-184-5005 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/13/2023 |  | 3.380000 |  |  | 4.400000 |  |  | Will be sent separately |  | BOD: 3.38 TSS: 4.40 SV | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | 12:00 AM
08/23/2023 | Alternative | RoutineScheduled | 175-04-0177 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Advantex Recirculation Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [17 empty] | Septic Tank3"sludge 0"scum/ Advantex-4"sludge 0"scum/ Pump Tank-1"sludge 0"scum/ No pump out needed at this time/ Recirculation Pump intake cleaned/ AX-20 Media in good condition/ Controls, pump, floats and alarms were functioning properly/ Counts: Discharge Run Time-543.7/ Total cycles-41468/ Recirc. Run Time-4068.7/ Total cycles-99999.9/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic and fuji tank need pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
03/08/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
06/05/2023 | Alternative |  | 17-100-0507 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 10:00 AM
10/07/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20 RT |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. 12" of solids in recirculation portion of treatment unit. 12" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Cleaned drip manifold spin filter. Tested floats, pumps and alarm. The treatment unit may need to be pumped out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 07:03 PM
04/21/2023 |  | Initial Visit | VAG401996 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 2.000000 |  | Constructed Wetlands |  | Pump | Gravity | Discharge | Chlorination |  | ["Disinfection"] | ["Control Operation","Disinfection","Distribution Pump Operation"] |  | None | [17 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 05/07/2023 | 09:30 AM
02/02/2023 |  | Routine/Scheduled | 800-12-0232 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 12:24PM
12/07/2023 | Alternative | Routine/Scheduled | 800-12-0020 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/07/2023 | Dec 30 1899 2:29PM
02/28/2023 | Alternative | RoutineScheduled | 17-177-1082 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 2.000000 | 1500 | Orenco Advantex |  | Gravity | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/02/2023 | 12:00 AM
10/31/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [18 empty] | See attached analytics | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/13/2023 | 12:00 AM
08/31/2023 | Alternative | RoutineScheduled | 18-125-131 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | 3 - Blue Crystal tablets installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/31/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/14/2023 | Alternative | RoutineScheduled Component Maintenance | SD-04-150 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | As noted previously, the conduit is broken going into the Advantex recirculation tank and the junction box is broken inside the tank. We recommend contacting a local electrician for assistance with this repair. We also recommend pumping the Pump Tank due to accumulation in the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/10/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-91591 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
12/17/2023 | Alternative | Reportable Incident | 18-120-0489MM | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the control panel in alarm condition due to a failed UV bulb. I checked and confirmed the UV power lead was intact. Homeowner gave written approval to upgrade UV bulb. I upgraded UV bulb while on site and checked and confirmed it was functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | Dec 30 1899 10:31AM
08/30/2023 | Alternative | Routine/Scheduled | S 800-14-0128 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/30/2023 | Dec 30 1899 12:45PM
05/20/2023 | Alternative | Routine/Scheduled | 095-STS-5062 | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Drainfields LLC | 1942001219 | Gene | Shanks |  |  |  |  | Pump | Pressure | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/20/2023 | Dec 30 1899 9:00AM
10/06/2023 | Alternative | Reportable Incident | 157-10-0139 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to some wet spots on the drainfield. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Pumped out the septic tank and pumped the sludge from the bottom and top of the Clearstream tank. There are wet spots on the drainfield - need to flush out drip tubing, perform a draw down test, and adjust timer. The timer is set to 10 minutes every 1 hour. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/06/2023 | 03:45 PM
11/15/2023 | Alternative | Routine/Scheduled | PPIE-AD5HJ5 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/15/2023 | Dec 30 1899 4:30PM
12/12/2023 | Alternative |  | 12-184-5001 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/12/2023 |  | 7.020000 |  |  | 6.400000 |  |  | Will be sent separately |  | BOD: 7.02 TSS: 6.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 12:00 AM
01/06/2023 | Alternative | RoutineScheduled | 151-10-0001 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1250 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
04/17/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20271 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Chlorination |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | 7.800000 | 7.500000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 11/15/2023 | 02:02 PM
03/08/2023 |  | Reportable Incident | 234-15-218 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator, diffuser, hose assembly and alarm bulb | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/08/2023 | Jan 1 1900 9:00AM
01/03/2023 |  | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1060 | Multiflo FTB |  | Gravity | Gravity | Trenches |  | 450.000000 | ["Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/09/2023 | 03:27 PM
11/08/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | [9 empty] | [] | [] | [18 empty] | Routine Annual, did replace pressure gauge (oil filled) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/08/2023 | 12:00 AM
04/07/2023 |  | Pump-Out Only |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | McKim septic and pumping | 1942001330 | Michelle | McKim | 2.000000 | 1250 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out | Tanks were pumped out but abandoned by another company | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 02:00 PM
10/16/2023 | Alternative | RoutineScheduled | 2016-143-0013 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Septic Pro of Virginia | 1942001780 | Eric | Tambourine | 1.000000 |  | Norweco Singulair 960-600 |  | Pump | Pressure | Drip | Not Applicable | 360.000000 | ["SludgeScum Accumulation","Effluent Screens","Dispersal System Operation"] | ["Effluent Screens","Dispersal System Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [14 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/25/2023 | 12:15 PM
12/15/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-70 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Inlet and outlet risers leak on septic tank and outlet riser on pump tank. Disassembled and resealed all risers. Replaced failed timer float. Augered all 4 pods.Replaced broken lids on the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
05/24/2023 |  |  |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
09/06/2023 | Alternative | RoutineScheduled Component Maintenance | 177-STS-92865 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 06:05 AM
09/11/2023 | Alternative |  | 18-100-0018 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:00 AM
08/15/2023 | Alternative | RoutineScheduled Component Maintenance | 061-STS-24902 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
06/17/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
04/26/2023 | Alternative | RoutineScheduled | 166-18-102 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/15/2023 | Alternative | Routine/Scheduled |  | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/15/2023 | Dec 30 1899 8:36AM
09/20/2023 | Alternative | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 3181.000000 | [] | [] |  |  |  | 7.510000 | 6.600000 | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/15/2023 | 04:35 PM
12/19/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20280 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Sulphitic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/16/2024 | 01:58 PM
02/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
10/04/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [5 empty] | 10/04/2023 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
09/19/2023 | Alternative | RoutineScheduled | 196-05-573 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced faulty relay, cleaned filters | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
01/24/2023 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | 03:27 PM
01/24/2023 |  | Routine/Scheduled | 234-15-230 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 1:45PM
06/02/2023 |  | RoutineScheduled | 153-STS-20273 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
02/03/2023 |  | RoutineScheduled | 177-06-0643-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 1.000000 | 1500 | 2-1 0-3 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 5.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 10:00 AM
02/16/2023 | Alternative | Initial Visit | 800-STS-15049 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 25.000000 | [7 empty] | Owner called due to an alarm - replaced the circuit board in the control panel. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. The timer is set to 2.5 minutes every 2 hours. Took initial BOD sample. NOTE : BOD sample was a tad high - system should function properly after service. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/16/2023 | Dec 30 1899 11:00AM
06/06/2023 |  | Routine/Scheduled | 15-142-0248 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the override float. The septic tank needs to be pumped out as well as the Clearstream tank. The timer is set to 6 minutes every 5 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | Jan 1 1900 9:00AM
04/13/2023 |  | Routine/Scheduled | 133 07 0097 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/13/2023 | 04:45 PM
01/11/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/02/2023 | Jan 1 1900 11:08AM
11/30/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0375 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 09:34 AM
03/12/2023 | Alternative | RoutineScheduled | 154-04-0137 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | Puroflo |  | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/12/2023 | 01:05 PM
03/18/2023 |  | Routine/Scheduled | 2012-143-0120 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/18/2023 | 10:54 AM
08/09/2023 | Alternative | Reportable Incident |  | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Cajun Aire ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | None | N/A | [17 empty] | Other tradesman on property and noticed that red light was on in septic control panel - no audible alarm - found silenced. Found circuit breakers in residence for Aeration and discharge tank OFF - re-activated breakers, system pumped down on own accord - found no issues with treatment system indicating cause for house breakers to be OFF. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | 09:30 AM
02/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/07/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Effluent surfacing in area of distribution box. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/31/2023 | Jan 1 1900 12:26PM
12/26/2023 | Alternative | RoutineScheduled Component Maintenance | 177-10-0145-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/06/2023 |  | RoutineScheduled |  | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 1-9 0-5 | 0-2 | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 18.000000 | [11 empty] | Inspected | system functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/06/2023 | 11:00 AM
06/06/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/12/2023 | Dec 30 1899 3:00PM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium"] | ["Auxiliary Filter" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/06/2023 | 03:05 PM
04/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 047-16-019 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | UV |  | ["Recirculation Pump" ,"BlowerCompressorAerator Operation" ,"Disinfection" ,"Attached Growth Medium"] | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
07/26/2023 | Alternative | Reportable Incident | S 800-18-0156 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Installed an aerator rebuild kit. Meet with the pumping company and pumped the septic tank (inlet tee was full of grease), pumped the trash out of the Clearstream tank, and cleaned the pump tank. It had rained the previous night and could not the drainfield or mound. The timer is set to 8 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/26/2023 | Dec 30 1899 9:30AM
05/23/2023 |  | RoutineScheduled |  | Cumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | EZ Treat | Pump | Gravity | Trenches | Not Applicable | 350.000000 | ["Effluent Screens","Recirculation Pump"] | ["Effluent Screens","Control Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/23/2023 | Jan 1 1900 9:45AM
04/20/2023 |  | RoutineScheduled | 2019-143-0006 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Advantex |  | Pump | Pressure |  |  |  | [] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation","Disinfection","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/20/2023 | 12:00 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | ATU needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
05/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92054 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
12/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Orange | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Clearstream | none | Pump | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Blowers have been replaced. We continue to recommend replacing the Salcor UV bulb. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 01/02/2024 | 11:12 AM
03/23/2023 | Alternative |  | 154-05-0507 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Tony | Hamilton | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/06/2023 | Alternative | Reportable Incident | 073-STS-93299 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Owner called due to an alarm. Replaced the UV light bulb and replaced the UV circuit board. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/06/2023 | 12:00 PM
07/19/2023 | Alternative | Routine/Scheduled | 04-172-0335A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | Dec 30 1899 7:30AM
07/27/2023 | Alternative |  | 12-113-215 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/27/2023 |  | 2.270000 |  |  | 6.800000 |  |  | Will be sent separately |  | BOD: 2.27 TSS: 6.80 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/27/2023 | 12:00 AM
11/27/2023 | Alternative | RoutineScheduled | 115-14-0009 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Distribution Pump Operation","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge levels-Scum layer 1-2" in. and 10" sludge in upper Septic tank #1 -Septic zone/recirc minimal scum and 10" Sludge and 20" Sludge in Discharge zone of tank. Pump tank fine sludge. System was pumped 2 years ago and does not need pumping this year. Upper tank effluent screen was clogged and we cleaned. The bio filter was very clogged and was cleaned(called due to a clogged filter alarm). Both Pumps are operational. sprayed off media and manifold, Pulled and cleaned RSV. floats all responding. Ran system in test mode to flush it. Drainfield has been cut over and trees had fallen, large equipment used for tree work appears to have not damaged the drip drainfield but the pipes are very close to surface. Rememebr to keep equipment off the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
11/20/2023 | Alternative |  | 13-183-116 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/20/2023 |  | 26.500000 |  |  | 10.600000 |  |  | Will be sent separately |  | BOD: 26.5 TSS: 10.6 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/20/2023 | 12:00 AM
07/21/2023 | Alternative | RoutineScheduled | 09-173-090 | Prince Edward | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Norweco |  | Pump | Gravity | Pad | Not Applicable | 350.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Cloudy | [14 empty] | Inspected |  | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/21/2023 | Dec 30 1899 10:30AM
01/26/2023 |  | RoutineScheduled | 19-138-034 | Grayson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 750 | Aqua Safe 600 |  | Gravity | Gravity | Trenches | Not Applicable | 600.000000 | ["None"] | ["SludgeScum Accumulation","Other"] | NA | Septic | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/26/2022 | Jan 1 1900 1:45PM
03/21/2023 |  | RoutineScheduled | 027-STS-17718 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 8 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/21/2023 | 12:00 AM
12/13/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | Septic | Clear | 7.000000 | 4.000000 | [13 empty] | Replaced UV bulb & UV ballast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 12:45PM
10/12/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/27/2023 | Alternative | RoutineScheduled | VAG408349 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Christopher Eavers Inspections | 1942001746 | Chris | Eavers | 1.000000 |  | FAST |  | Gravity |  |  |  |  | [] | ["BlowerCompressorAerator Operation","Disinfection"] | NA | None | [16 empty] | Not discharging at time of inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/12/2023 | 09:30 AM
12/19/2023 | Alternative | RoutineScheduled | 2006-143-0120 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/16/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.480000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/23/2023 | 12:15 AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/10/2023 | 11:17 AM
01/18/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/02/2023 |  | RoutineScheduled | 07-137-0187 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | Puraflo |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/04/2023 | 12:00 AM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance | 047-STS-25519 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Disinfection"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Disinfection"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
01/27/2023 |  | Follow-Up |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm. Replaced badly corroded terminal strip and ground lugs in junction box at tank. Alarm float switch failed to open during testing, replaced it. New drip pump was just installed yesterday (same model WE1512HH). Ran a test cycle to verify system operation. Re-piping the filter flush line to eliminate the churning of the water near the pump was successful as the spin filter was still clean. Even with a brand new pump, clean spin filter, and return line ball valves set correctly, water level only dropped 2.5 inches (at most 90 galllons) in an hour long cycle. That equates to an extremely low drip rate and suggests that the drip emitters are clogged. It is noted that there are 4 returns (ball valves and pressure gauges), but no zone distribution valve to separate the zones. Additional field work and testing is highly recommended. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
11/20/2023 | Alternative |  | 027-STS-15565 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/20/2023 |  | 11.900000 | [5 empty] | Will be sent separately |  | BOD: 11.9 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 12:00 AM
12/13/2023 | Alternative | Follow-Up Component Maintenance | 179-14-0367-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced all EZ treat spray heads. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/13/2024 | 11:49 AM
02/20/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | None | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | 08:35 AM
03/23/2023 |  | RoutineScheduled | 08-113-152 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 4 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/23/2023 | 12:00 AM
05/29/2023 |  |  | 113-18-074 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/12/2023 | 12:00 AM
07/17/2023 | Alternative |  | {FIPSCode}-STS-26543 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 12:00 AM
03/28/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | 154-04-0904 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
10/11/2023 | Alternative | RoutineScheduled | 01-172-0354A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C & E Mechanical Corporation | 1942001339 | Louis | Timberlake | 1.000000 | 1,500 gallons | Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Inspected | Recommend pumping in 2 years | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | Dec 30 1899 1:20PM
01/23/2023 |  | RoutineScheduled | {FIPSCode}-STS-4284 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | Aqua Safe AS 750 E2 |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Cleaned effluent screens, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | 12:00 AM
06/01/2023 |  | Routine/Scheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 2000 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:10 PM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/28/2023 | Alternative | Initial Visit Component Maintenance | 099-STS-92880 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/11/2024 | 06:22 AM
03/01/2023 |  | RoutineScheduled | SP 00-250 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Routine inspection. 2 bad floats (peak and high level) replaced both with proper kind (wide angle). Disc filters were clogged bad, cleaned. Drip rates a bit below design but should be enough to meet needs of the home occupants however drip flush has dropped considerably from bleach flush last year, system does not have any pre treatment. Recommend drip flushing both zones again . WILL SEND PROPOSAL. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 165-STS-335223 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | replaced gauge and buzzer Pumping is required let us know when want this performed | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
03/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/13/2023 | Alternative | RoutineScheduled | C10-180-0013 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Level Sensor Operation"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Septic zone minimal 1" scum - 12" sludge-- Recirc zone 1" scum - 18-20" sludge treatment tank needs pumping. Called Halls Septic who came back to pump it out. Called due to an alarm- it was due to dirty clogged filter, Cleaned Biofilter (Very Dirty-backed up), cleaned effluent filter, clogged and backed up- Pulled and cleaned-RSV, Flushed and brushed sprayer manifold, sprayed off media, float switches operational. Both pumps are good and control operate fine in auto mode. recirculation pump PF300511. Good Spray after service. Recirc pump 2634.9 hours 49167 cycles, discharge pump shows 3911.3hours and 95525 cycles. Water infiltration has occurred due large rain events. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | Dec 30 1899 9:30AM
05/31/2023 |  | RoutineScheduled |  | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | LPD |  | Pump | Pressure | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation","SludgeScum Accumulation"] | NA | [16 empty] | Inspected | - siphon pump is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/08/2023 | 12:00 AM
02/23/2023 | Alternative | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced pump #2 contactor in control panel. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/31/2023 | Dec 30 1899 12:26PM
08/05/2023 | Alternative | RoutineScheduled | S17-111-0100 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke |  | 1942001505 | John | Burch | 1.000000 | 1000 | Microfast .625 |  | Gravity | Gravity | Trenches | Not Applicable | 150.000000 | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Other"] | NA | None | Cloudy | 6.900000 | 6.200000 | 0.000000 |  | Secondary side sludge depth - Flocculent level 25" | [10 empty] | Primary and secondary zones of the treatment unit recommended pumping due to sludge depth. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/05/2023 | Jan 1 1900 3:00PM
07/29/2023 | Alternative | Reportable Incident Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced 3 control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
07/25/2023 | Alternative | RoutineScheduled | 97-100-0673 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | SAND FILTER |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | [] | [] | NA | [17 empty] | EVERYTHING WORKING AS IT SHOULD | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/27/2023 | 02:00 PM
04/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/15/2023 |  |  | 2013-143-0073 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["Control Operation","Distribution Pump Operation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [17 empty] | Inspected | Replaced blower 3/15/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
11/03/2023 | Alternative | RoutineScheduled Component Maintenance | 175-15-0235 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
01/09/2023 |  | RoutineScheduled | VAG408095 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.180000 |  |  | 0.720000 | [11 empty] | Advised client to have system pumped and scheduled sock replacement/cleaning. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | 12:15 PM
01/16/2023 |  | RoutineScheduled | 179-13-0316-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation" ,"Septic Tank Baffles"] | ["BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for rountine inspection. Two compartment micro fast tank needs to be pumped out due to sludge levels. Homeowner will call pumper to schedule. Line 4 in distribution box had new growth roots growing into header line. Removed roots and added root-x. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/23/2023 | 05:35 AM
08/23/2023 | Alternative | RoutineScheduled Component Maintenance | 179-14-0367-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Puraflo peat needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 11/15/2023 | 02:02 PM
07/07/2023 | Alternative | RoutineScheduled | VAG408474 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Discharge | UV |  | ["Auxiliary Filter","Other"] | ["Auxiliary Filter","Other"] | YES | Musty | Clear | [15 empty] | no discharge during visit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
07/20/2023 | Alternative | Routine/Scheduled | 151-06-0365 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | On arrival the alarm was muted. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Replaced the alarm light bulb. Cleaned the filter in the septic tank (by the house). | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/20/2023 | 11:15 AM
12/21/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-31006 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled | SD-14-033 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Effluent Screens","Attached Growth Medium"] | ["SludgeScum Accumulation","Control Operation"] | YES | Sulphitic | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/01/2023 | 02:40 PM
08/09/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-1317 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/09/2023 | Dec 30 1899 1:34PM
05/16/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [16 empty] | Inspected | Sludge level- minimal scum layer on top-6-8" sludge on bottom in Septic tank-- Pump tank has 5" of sludge, the pump and alarm are operational- Timer is operational. Septic tank alarm box is corroded like last year and scheduled to replace in future. Cleaned effluent filter, turned over peat moss in treatment tanks. Peat look in ok condition for 2 and new condition for other 2 pods. Peat was moist with no ponding- Pump counter at 23112 vs 21839 vs 20,000ct 2 years = 1,8273 cycles since last year- Pump timer is 216.21Hrs vs 200.15hr vs 170.21Hr 2 years ago = 16hrs pumped since last years inspection. Alarm test operational, floats test operational. System appears fully operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
04/18/2023 | Alternative | RoutineScheduled | 88-184-93 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 2 Chlorine 11 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/18/2023 | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Module closest to the house is ponding. Module second from the house has severe roots. The tank structure appears to be good from the surface view through the risers. The distribution box appeared lower than dialflow openings. Drainfield lines are saturated but not surfacing. Recommend homeowner contact AOSE regarding options for replacement of peat and field. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/12/2023 | 03:17 AM
05/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/26/2023 | Alternative | Reportable Incident | {FIPSCode}-STS-4297 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/26/2023 | Dec 30 1899 11:00AM
09/25/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Pad | Not Applicable | 750.000000 | ["None"] | ["None"] | NO | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/09/2023 | Dec 30 1899 1:35PM
08/09/2023 | Alternative | RoutineScheduled | 2016-143-0013 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Control Operation","BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/10/2023 | Alternative | Follow-Up Component Maintenance | 099-12-0042-SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed all 3 concrete risers. Added 2 ft. of riser to septic tank inlet. Resealed two wedge lids. Resealed outlet pipe on discharge tank, inlet OK. Sealed root penetration on the end wall of the discharge tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
06/20/2023 | Alternative | Reportable Incident Component Maintenance | 179-09-0161-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for water coming out of pod due to failed on/off float. Alarm horn was disconnected in the panel. Replaced on/off float. Replaced tipping tray that was broke. Peat moss is very compacted due to lack of maintenance. Roots in D-box not allowing all header lines to get equal waste water. Will make follow up visit to after tank is pumped out to auger peat and try to remove roots from header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
11/06/2023 | Alternative | Routine/Scheduled | 151-04-035 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 25.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/06/2023 | 01:18 PM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/09/2023 |  | RoutineScheduled | 17-137-0143 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2000 | EZ-Treat |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Auxiliary Filter"] | NA | Musty | Clear | [14 empty] | Inspected | Effluent Filter Cleaned Septic Tank Sludge Scum Accumulation - 8" Pump Tank Sludge Scum Accumulation - 3" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | 12:00 AM
06/29/2023 | Alternative | Reportable Incident Component Maintenance | 175-14-0053 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed AP80 compressor & repaired broken clean out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/30/2023 | 10:30 AM
12/11/2023 | Alternative | RoutineScheduled | 061-17-460 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | McKim Septic & Pumping | 1942001330 | mckim | Pumping | 5.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/12/2023 | 11:30 AM
11/15/2023 | Alternative | RoutineScheduled | 03-120-0469A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/30/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
10/06/2023 | Alternative | RoutineScheduled Component Maintenance | 175-03-0481 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
09/11/2023 | Alternative | RoutineScheduled | 14-177-1074 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 |  | Aqua Safe 500 Duo |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Other"] | ["Other","SludgeScum Accumulation"] | NA | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/11/2023 | 04:00 PM
06/27/2023 | Alternative | Reportable Incident Component Maintenance | 175-13-0031 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Complaint inspection. High alarm due to bad alarm float for recirc tank, Replaced float and all wire nuts. Everything back to normal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
06/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/28/2023 | Alternative | Routine/Scheduled | 159-13-020 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Was flooded due to on/off float not working Was pumped down on site Unable to get accurate sludge reading Discharge/Pump Tank Condition of above Component Notes for above Component Installed new on/off float Pump and floats working properly Aeration Condition of above Component Notes for above Component Unable to get proper sludge reading due to system being flooded Pulled and cleaned wier Alarm float working properly Air Pump/Blower Condition of above Component Notes for above Component Working properly Pulled and cleaned filter Control Panel Condition of above Component Notes for above Component Panel working properly Visual and audible alarms working Pump pulling 7amps Drain Field Condition of above Component Notes for above Component Showing no signs of surface There was standing water in the area due to heavy rain and high tide | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 09:24 AM
03/30/2023 |  | RoutineScheduled | 153-STS-19017 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
05/17/2023 |  | Routine/Scheduled | 234-15-421 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/17/2023 | Jan 1 1900 12:30PM
07/17/2023 | Alternative | Reportable Incident Component Maintenance | 175-03-0824 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed N140 effluent pump, 2" brass check valve & (2) control floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
11/21/2023 | Alternative |  | -STS-92104 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
11/15/2023 | Alternative | RoutineScheduled | 07-184-5004 | Scott | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/15/2023 | 12:00 AM
03/27/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | PURAFLO |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [16 empty] | Inspected | Septic tank -No Access, Pump Tank Minimal scum and 8" Sludge, Pump Alarm and FLoats are operational, Time dosing panel operational, Pump Operational, Pump Count 14339 Cycles, Run time 316.15 Hours. Pump ran about 31.35 hours since last year. Turned Peat Moss in all three pods. Peat appears dry and fluffy with minimal moisture. Minor roots noted in all 3 pods from the surrounding bushes, Please keep bushes trimmed back and the soil at under 2" from lid lip. System fully operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 09:30 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | 2088-04-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | UV |  | ["Disinfection"] |  | NA | Musty | Clear | 7.600000 | 9.200000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 11/15/2023 | 02:02 PM
04/20/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
09/15/2023 | Alternative | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [9 empty] | [] | ["BlowerCompressorAerator Operation"] |  |  |  | 4.520000 | 5.490000 | 47.000000 |  |  | 10/15/2023 |  | 17.000000 |  |  | 53.900000 | 102.900000 |  |  |  | Replaced Blowers and check valves on 9/18. Will resample in October. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/15/2023 | 04:35 PM
04/25/2023 | Alternative | RoutineScheduled | SD-13-059 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 1.000000 | 1500 | Aerobic Treatment Unit 0.75 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [7 empty] | 04/25/2023 | Sample Tap | 88.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/08/2023 | 12:00 AM
02/21/2023 | Alternative | Reportable Incident | 150-07-0218 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2900 | Septic Tank | Delta Whitewater | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Cloudy |  |  | 50.000000 | [12 empty] | Service call for aerator alarm. Delta Whitewater aerator had torn diaphragms. Rebuilt aerator. DWW treatment tank 50% SS, should go down with rebuild. ST- 6" FOG, 4" sludge, does not need pumping. PT- Pump, alarm, floats, controls operating properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/26/2023 | 02:30 PM
03/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/13/2023 | Alternative | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","Auxiliary Filter"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/10/2023 | 12:00 AM
06/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/02/2023 | Alternative | Routine/Scheduled | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Effluent filter was found clogged and it was cleaned. Septic tank and treatment unit need to be pumped out. The recirculation pump had 45 overrides in the past 30. The outlet tee needs to be adjusted. It appears the there is inadequate air flow through the treatment train. Flushable wipes do not break down well in the septic tank. There is excessive grease in the septic tank and is in the treatment unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 10:41 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | 033-16-0098-SP | Caroline | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | The aerator tip in your aerobic treatment unit is missing. We recommend installing a new aerator tip and shaft. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | 08:44 AM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/17/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | all tanks pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/06/2023 | 08:40 AM
07/14/2023 | Alternative | Initial Visit | 151-15-0085 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit - Requested FOIA Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - reported deep and located under driveway. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 09:15 AM
12/08/2023 | Alternative | Routine/Scheduled | -STS-5094 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Septic Tank Condition of above Component Notes for above Component Normal Level 6" of sludge and 1" of solids Cast in section riser with lid buried below grade. Discharge/Pump Tank Condition of above Component Notes for above Component Normal Level Less than 1"of suspended solids All floats and pump are functioning properly No signs of infiltration Aeration Condition of above Component Notes for above Component Normal Level Heavy sludge and solids Alarm float functioning properly Air Pump/Blower Condition of above Component Notes for above Component 120v All audible and visual alarms are functioning properly Pulled and cleaned air filter Air pump pulled 1.6amps Control Panel Condition of above Component Notes for above Component 120v All audible and visual alarms are functioning properly Pump pulled 9.1amps Distribution Box Condition of above Component Notes for above Component Plastic distribution box at grade in good condition at normal level with 7 lines balanced and taking water All seals are intact. Minor roots removed by hand Drain Field Condition of above Component Notes for above Component No signs of surfacing Pumped and refilled on 12/12/2023 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/13/2023 | Dec 30 1899 12:14PM
09/25/2023 | Alternative | Reportable Incident | 147-15-0052 | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Came out for alarm call and performed annual maintenance insection: -Septic Tank: Normal level 10" of sludge and 1" solids Pulled and cleaned filter No signs of infiltration -Recircualtion Tank: Above normal level Pulled and cleaned pump Pulled and tested floats all working properly however are aged -Discharge/Pump Tank: Above normal level Pump not working All floats working as should however are aged -Media Sheets: Flushed and brushed lateral Sprayed and cleaned media sheets Buildup of biomat between sheets -Control Panel: 120 volts coming in Recirc pump pulled 8.43amps All visual and audible alarms functioning properly -Distribution Box: Normal level 5 lines intact taking water properly -Drain Field: No signs of surfacing Removed minor roots Repair 9/26/26: --Installation of 3 Floats -Installation of 3 Floats -Replacement of orenco discharge pump -Advantex Treatment Unit Engineered Textile Media Filter Cleaning - includes use of a specialized wanding tool -Tested all components upon completion and everything is functioning as it should. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/11/2023 | Dec 30 1899 10:14AM
05/09/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/20/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | First Yearly Inspection- of system installed many years ago, Just turned on for first time and set pump run times and other settings. System in Start up mode and looking to trend 5 days use data. Owner has not completed the home yet but wnts to attach his RV soon. System is ready for use. Sludge levels- Septic tank trace sludge layer, Recir zone trace sludge, discharge zone trace sludge- High water on arrivial and clear water to tank bottom, level corrected after running in test mode. Recirc pump run time 0 hours 2 cycles and 0.5 hours discharge and 4 cycles Recirc pump pulled 8.6 amps-Discharge pump pulled 11.5 amps, Flushed spin filter, effluent filter clean. System ready for use | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
11/02/2023 | Alternative | RoutineScheduled Component Maintenance | 179-09-0082-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Small roots in 2 pods ,removed. Pump has slowed down, will upgrade when fails. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 10:51 AM
05/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens" ,"Dispersal System Operation"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Dec 30 1899 12:05PM
09/20/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Septic Tank Baffles","Dispersal System Operation"] | ["Septic Tank Baffles","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/20/2023 | 12:00 AM
01/13/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Pad | Not Applicable | 750.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/01/2023 | Jan 1 1900 3:15PM
03/06/2023 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [18 empty] | Spoke with the owner about the Puraflo Media needing replacement and he stated he has a contract for replacement of the peat and will be addressed soon. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/30/2023 | Alternative | RoutineScheduled | SD-14-268 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [17 empty] | Septic Tank-6"sludge 2"scum/ Pump Tank-1"sludge0"scum/ No pump out needed at this time/ Fluffed Puraflo Peat in all 3 modules, 1 module had peat that was compacted but was able to fluff the peat and it's taking water/ Unable to gain access to the control box inside the house. No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/21/2023 | Alternative | RoutineScheduled | 043-STS-34936 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 12:00 AM
12/19/2023 | Alternative | RoutineScheduled |  | Page | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Puraflo |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [18 empty] | Drip tube repaired | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/19/2023 | 12:00 AM
05/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
01/06/2023 |  | Pump-Out Only | 234-14-80 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/06/2023 | Jan 1 1900 9:00AM
01/11/2023 |  | RoutineScheduled | 10-120-0254AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 2.000000 | 2250 | Clearstream |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Attached Growth Medium"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 9:20AM
02/07/2023 |  | RoutineScheduled | 099-16-0099 SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/17/2023 | Alternative | Follow-Up Component Maintenance | 061-18-237 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Ecopod blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
03/21/2023 | Alternative | Reportable Incident | SD-13-290 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | High level alarm. Recirc pump was not running due to corroded hot wire connection. Cut and stripped new connections for all 3 pump wires and the other 2 float switches. Put panel into test mode to confirm operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
06/12/2023 | Alternative | Reportable Incident | 234-19-0033 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [16 empty] | Pumped Out | Replaced aerator and diffuser | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/12/2023 | Dec 30 1899 2:00PM
03/13/2023 | Alternative | RoutineScheduled | SD-04-176 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1000 | septic | Puraflo | Gravity | Pressure | Discharge | Chlorination |  | [] | [] | YES | Musty | Cloudy | 6.800000 |  |  | 1.040000 | eff do. 5.9 | 03/13/2023 | Sample Chamber | 24.000000 | 0.000000 |  | 15.000000 |  |  | Attached to this report |  | Formal | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/28/2023 | 08:10 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/29/2023 | Alternative | RoutineScheduled Component Maintenance | 2107-05-153 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  |  |  | NA |  |  | 603.000000 | 6.400000 | [11 empty] | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 09/15/2023 | 02:41 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
03/27/2023 |  | RoutineScheduled | 177-10-0158-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Defective timer float was replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
09/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Page | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 09/13/2023 |  | 170.000000 | [5 empty] | Will be sent separately | Inspected | power was off all floats not working leak effluent outlet pipe unlevel control panel low | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/13/2023 | 01:07 PM
03/14/2023 | Alternative | Routine/Scheduled | 175-07-0070 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Dec 30 1899 10:46AM
05/17/2023 | Alternative | RoutineScheduled | 154-11-0035 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/19/2023 | 12:00 AM
11/02/2023 | Alternative | RoutineScheduled | 175-04-0601 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [7 empty] | 11/16/2023 | Sample Chamber | 56.000000 | [5 empty] | Attached to this report |  | Septic Tank-6"sludge 8"sludge/ Microfast-4"sludge 0"scum/ Pump Tank-0"sludge/ Blower air filter cleaned and blower is working correctly/ Found the timer enable float was faulty and was replaced during inspection/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-3141 ETM-561h 39m On-11m Off-3h 12m/ High level-23/ No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
04/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/29/2023 | 12:05 PM
09/29/2023 | Alternative | RoutineScheduled | SD-05-47 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Septic tank | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["SludgeScum Accumulation","Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/22/2023 | 07:20 AM
01/28/2023 |  | Routine/Scheduled | 228-12-0542 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/28/2023 | Jan 1 1900 8:15AM
07/10/2023 | Alternative | RoutineScheduled | 171-07-0408 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Ecoflo STB 650 |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/26/2023 | 03:45 PM
02/27/2023 |  |  | 06-137-0114 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | We will be pumping the tank 3/8/23 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 12:00 AM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/19/2023 | Alternative | RoutineScheduled | 121-STS-13628 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | [17 empty] | Inspected | - recommend septic tank pumped/cleaned - recommend riser installation for maintenance/access purposes | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 10/27/2023 | 12:00 AM
03/17/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Dispersal System Operation"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Step 20 pump need replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/15/2023 | Jan 1 1900 12:05PM
06/08/2023 | Alternative | Reportable Incident Component Maintenance | 179-14-0243-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to failed blower. Replaced failed blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
07/21/2023 | Alternative | Routine/Scheduled | 136-96-0531 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - vegetation cleared from treatment modules. Primary septic tank - normal level - effluent screen serviced. PUmp Tank - float sensors, pump and controls operating. BioFilter - four modules - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 09:00 AM
10/12/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-0049-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Rountine inspection. Septic tank will be due for a pump out next due to sludge levels. Roots are starting to grow into pods. Recomend augering all 5 pods next year. Replaced effluent pump as it was not pumping at the proper rate to dose all 5 pods. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System appears to be functioning as designed at this time. There are three emitter spots near the far side of the drainfield that appear highly nitrified but it might just be less cover as the line ends. Recommend homeowner monitor and notify if there are any changes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/22/2023 | Alternative | RoutineScheduled | 171-05-0421 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | NA | [16 empty] | Inspected | Sludge level-1-2" scum layer on top-20" sludge on bottom in Septic tank-- Pump tank has a light trace sludge, the pump and alarm are operational- Cleaned effluent filter, turned over peat. In ok condition for age.. Alarm is working, Peat was moist with no ponding, Added 1/2 a 2lb rootx treatment to the dbox below the peat pods to prevent a root intrusion- Pump counter 18461 vs 16433 cycles last year= 2028 cycles this year. Pump run time 70.1762.39 vs 62.39 Hrs last year = 7.78 hours pumping last years inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
09/08/2023 | Alternative | Routine/Scheduled | 159-STS-104624 | Richmond | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 05:50 PM
04/28/2023 |  | Routine/Scheduled |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact - two minor fractures (repairable) noted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/01/2023 | 08:00 AM
11/01/2023 | Alternative | RoutineScheduled | 07-142-0060 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/14/2023 |  | RoutineScheduled | 18-100-0472 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/10/2023 | 12:00 AM
05/15/2023 |  | Routine/Scheduled | 234-13-23 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | Jan 1 1900 11:25AM
07/11/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There is a suspect area just before the drainfield. It looks like it could be an issue with the force main. Informed homeowner and gave recommendations for further investigation. Will update as more information is available. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/12/2023 | 03:17 AM
12/08/2023 | Alternative | RoutineScheduled Component Maintenance | 177-14-0058-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend pumping the aerobic treatment unit due to sludge accumulation in the tank. It may be advisable to pump the septic tank side of this tank at the same time. Roots have grown in around the seals of the distribution box and are growing down the header lines. This was noted on last years inspection. Also the roots in the header lines can result in uneven distribution of water to the drainfield lines. We recommend excavation by machine to repair the distribution box seals and to repair or replace header lines as necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/02/2024 | 11:12 AM
12/06/2023 | Alternative | RoutineScheduled | VAG408187 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.600000 |  |  | 1.170000 |  | 12/06/2023 |  | 11.000000 |  |  | 25.000000 | [5 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/28/2023 | 02:00 PM
10/04/2023 | Alternative | Initial Visit | 810-STS-4059 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 16.000000 |  | 114.000000 | [5 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the diffuser in the Clearstream. Replaced the UV light bulb. The timer is set to 3.5 minutes every 1 hour. Took initial BOD and Fecal samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/04/2023 | Dec 30 1899 10:45AM
08/07/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/08/2023 | Alternative | RoutineScheduled | S-13-111-0011 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Delta Environmental Products, DF Series |  | Siphon | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 15" of accumulated solids in septic tank with a skim crust. 22" of solids in treatment unit. 6" of solids in discharge pump tank. Suggested all tanks be pumped out. Homeowner lined up pump out. Adequate aeration. Cleaned blower filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/25/2023 | 12:00 AM
04/13/2023 | Alternative | RoutineScheduled | 107-07-0509 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
04/24/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | septic tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
08/02/2023 | Alternative | RoutineScheduled Component Maintenance | 107-08-0391 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Pump Intake clogged was cleaned Recirc Pipe needed repaired Repaired recirc alarm float THIS INSPECTION IS REQUIRED YEARLY FOR VDH .Please provide us new owner information | This AOSS should now return to normal function after having provided the above state routine maintenance | 08/23/2023 | 06:57 AM
04/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
08/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
07/12/2023 | Alternative | Reportable Incident | 228-12-0024 | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump with WE20, screen filter and timer enable float | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/12/2023 | Dec 30 1899 3:30PM
02/01/2023 | Alternative | RoutineScheduled | SD-02-775 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] |  | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/13/2023 | 08:47 AM
12/11/2023 | Alternative |  | 027-STS-17718 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/11/2023 |  | 3.710000 |  |  | 1.700000 |  |  | Will be sent separately |  | BOD: 3.71 TSS: 1.70 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | 12:00 AM
05/04/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
01/19/2023 |  | RoutineScheduled | 09-100-0399 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1500 | BIOCOIR |  | Pump | Gravity | Pad | Not Applicable | 900.000000 | [] | [] | YES | [17 empty] | EVERYTHING WORKING PROPERLY | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/24/2023 | 12:25 PM
12/07/2023 | Alternative | RoutineScheduled Component Maintenance | 177-13-0135-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | Musty | [14 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/17/2023 | 09:07 AM
01/23/2023 | Alternative | RoutineScheduled | 13-195-124-SP | Washington | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | FAST |  | Pump | Pressure | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | Musty | Clear | [15 empty] | No power on alternative treatment unit. 6" Solids and 6" scum in pretreatment HD Notes - site visit 10/20/23, house has been removed, therefore no power. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/23/2023 | 12:00 AM
11/15/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Microfast needs pumping. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | Dec 30 1899 10:33AM
09/08/2023 | Alternative | RoutineScheduled | 041-STS-260242 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Pad | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Pungent | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/08/2023 | 12:00 AM
11/20/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | Dec 30 1899 1:40PM
01/11/2023 |  | Routine/Scheduled | 17-142-0419 | Hanover | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 400 | Norweco Singulair ATU |  | Pump | Pressure | Drip | Not Applicable | 300.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [17 empty] | Homeowner reported that he cleaned the spin-filter recently because system had a high alarm for the pump tank. The BioKinetic system was extrememly clogged and causing the effluent to back up into the sewer. Biostatic Sludge Return was inspected and it was not seated in its proper position. This component comes pre-installed by the manufacturer and their local representative should be contacted to insure its proper positioning and installation. The spin-filter was cleaned before and after flushing the dripfield. The contracted pump-out of the trash tank(Pre-treatment Chamber) is due in one year, but the pump tank may need to be pumped out if the spin-filter continues to clog, prematurely. Effluent is surfacing on the dripfield because there is not a enough dirt covering the dripfield. More topsoil needs to be added. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/12/2023 | Jan 1 1900 8:54AM
08/17/2023 | Alternative | RoutineScheduled | 107-99-0389 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | LP |  |  | Pressure | Trenches | Not Applicable |  | ["Other"] | [] | [18 empty] | Homeowner replacing damaged cleanout caps on LP | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/17/2023 | 12:00 AM
07/07/2023 | Alternative | Routine/Scheduled | PPIE-AX9JYH | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/10/2023 | Dec 30 1899 8:30AM
03/15/2023 | Alternative | Initial Visit | {FIPSCode}-STS-8395 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/17/2023 | 08:40 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
12/21/2023 | Alternative | Reportable Incident | 175-15-0037 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation","Other"] | ["BlowerCompressorAerator Operation","Other"] | [18 empty] | Service call only: Replaced VCF200 Microfast Blower/ Added 20" x 6" riser/ Resealed inlet and outlet of the septic tank plus the inlet of the pump tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/06/2023 | Alternative |  | 06-197-A8 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/06/2023 |  | 2.340000 |  |  | 1.000000 |  |  | Will be sent separately |  | BOD: 2.34 TSS: 1.00 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 12:00 AM
04/04/2023 |  | RoutineScheduled | 175-05-0351 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/15/2023 | 07:20 PM
03/14/2023 |  | RoutineScheduled | 033-07-0422-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/10/2023 |  | Follow-Up | 175-17-0409 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Repair Only: Completed repair of the UV-Light . Tested and now working properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/27/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT-3 to Trenches |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Control Operation"] | ["Effluent Screens","Control Operation"] | NA | [16 empty] | Inspected | Initial Routine yearly inspection visit -Found the Advantex AX20 Control Panel wet and moist inside and not operational, I returned the next day and discovered and replaced the circuit board and rewired the floats switched when had melted possibly due to lightning. NEW RTU149021, Box 436743 - Alarm sounds, ran in test mode. . Pumps are PF100511 and PF300511 - Septic Tank no scum 6" sludge-Recir zone Ttrace - Dischagre - Trace sludge- Pump meter reading recirc xx min xx cycles, discharge xx min xxcycles- | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/29/2023 | 09:30 AM
01/18/2023 |  | RoutineScheduled | 107-02-0253 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
08/09/2023 | Alternative |  | 132-06-0054 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Russell | Day | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/30/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/13/2023 |  | RoutineScheduled | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001682 | Frank | Hogan | 2.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Multiple site visits made to identify and correct leaks, turned off zone 2, rewired panel so zones in field match zones in control panel and zones on as built. Samples from plant not collected | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 02/14/2023 | 08:41 AM
11/17/2023 | Alternative |  | 10-184-5001 | Scott | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | SCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination | [22 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
10/16/2023 | Alternative | Routine/Scheduled | 2006-143-0034 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/16/2023 | 09:34 AM
08/21/2023 | Alternative | Initial Visit | 124-STS-2379 | Prince George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the light being on. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Fixed the grade on the pipe in the Clearstream. The drainfield has visible wetness - is bleeding out - needs to be addressed and/or fixed. Could not locate vacuum breakers - no valve boxes. The timer is set to 5.5. minutes every 5 minutes - need the septic plans/permit (from homeowner) to see if this is correct. Took initial BOD sample. NOTE - BOD sample was high. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/21/2023 | Dec 30 1899 9:00AM
11/07/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 0.000000 | 0 | BioWheel |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | October 2023 monthly report. Total flow for month of October 2023 - 58,463 gallons. Average daily flow- 1,886 gallons per day. Reduced Biowheel speed for colder weather. Digester was pumped out in October. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/08/2023 | 07:03 PM
12/21/2023 | Alternative |  | 13-120-0371A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 2.000000 | 1750 | 1000 | 750 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Disinfection","Control Operation","Attached Growth Medium","Auxiliary Filter"] | YES | None | Discolored | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/21/2023 | Dec 30 1899 9:00AM
05/02/2023 | Alternative | RoutineScheduled | 02-100-0496 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 750 | AERODIFFUSER |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [18 empty] | REPLACED AERATOR BLOWER. EVERYTHING WORKING AS IT SHOULD. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/18/2023 | 12:00 AM
06/09/2023 | Alternative | RoutineScheduled | 033-07-0186-ST | Caroline | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | NA | [17 empty] | Replaced float switch on 6-9-23 Replaced Blower on 6-27-23 | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/14/2023 | 12:00 AM
01/18/2023 |  | Routine/Scheduled | 147-09-0099 | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 3000 | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches | Not Applicable | 1000.000000 | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - Grease Trap - effluent screen serviced. Primary septic tank - requires pumpout. Secondary septic tank - effluent screen serviced. Aeration tank - Compressor FAILED - NO ALARM Call from Owners! Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/19/2023 | Jan 1 1900 8:00AM
01/06/2023 | Alternative | RoutineScheduled | SD-07-167 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Control Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. First and last lines of drainfield are now covered by brush and leaves. Owner has agreed to clear it back. Septic/ recirc tank will most likely need pumped out by next year's inspection. Phone line is active for Vericomm panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
05/15/2023 |  |  | 179-16-0192-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | [7 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | replaced blower motor | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/15/2023 | 12:00 AM
09/12/2023 | Alternative | Follow-Up Component Maintenance | 099-18-0122 C-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Pressure | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Follow up. Replaced broken air vent for ax20 unit. Replaced 3 broken valve covers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
10/13/2023 | Alternative | Reportable Incident | 136-18-0297 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm call: -Arrived on site found a wet spot 6-7 ft away from vacuum, breakers near magnolia tree. Ran pump and water started coming to the surface. Dug down and found return line supply line and three drip lines that went into an ezflow. Water started pouring out of the ezflow. Underground needs to follow up -10/27 underground: Met with owner and reviewed findings. According to the permit, the drip tubing that was installed inside the EZ Flow was having issues anyways. Need to send an email to American onsite and ask for some guidance/feedback to determine what steps need to be taken | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/27/2023 | 04:10 PM
05/11/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1800 | Biomicrobics Micro Fast 0.5 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Sludge levels-- 1-2" Scum 16-18" sludge in Septic tank. Fast septic tank 24" slduge - Fast side port 1-2"scum 16-24" sludge- May pump prior to inspection next year. Blower alarm good, Cleaned air filter. All Opperational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
01/24/2023 |  | Routine/Scheduled | 550-STS-6679 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/24/2023 |  | 26.000000 |  | 700.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/24/2023 | Jan 1 1900 8:26AM
03/28/2023 |  | RoutineScheduled |  | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT-3 to Trenches |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Control Operation"] | ["Effluent Screens","Control Operation"] | NA | [16 empty] | Inspected | Follow up visit -Found the Advantex AX20 Control Panel wet and moist inside and not operational, the breaker had tripped at the house and when resseting the panel did not function, We replaced the circuit board and rewired the floats switched when had melted possibly due to lightning. NEW RTU149021, Box 436743 - Alarm sounds, ran in test mode. . Pumps are PF100511 and PF300511 - Septic Tank no scum 6" sludge-Recir zone Ttrace - Dischagre - Trace sludge- Pump meter reading recirc xx min xx cycles, discharge xx min xxcycles- | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/29/2023 | 09:30 AM
04/18/2023 | Alternative | Routine/Scheduled | 093-16-0133 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs to be pumped out as well as the Clearstream tank. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/18/2023 | Dec 30 1899 1:30PM
08/08/2023 | Alternative | RoutineScheduled Component Maintenance | 182-15-0146 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Primary tank pumped and sir supply repaired | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
02/14/2023 |  | Follow-Up |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | When we arrived both tanks were in high water. Air blower is not working at this time. There is about 12" of solids now in pump tank. Both tanks were pumped to the concrete 17 days ago. Only place it could be coming from is the micro fast unit. It only has 6" pvc pipes to look in no access. I would recommend digging up micro fast lid and pulling it off and pressure washing unit and pumping all tank again. Get as much of the solids out of the micro fast unit. Replace air blower if still not working. Also draw down of drip is only 3.2 gal a minute its low. The disc filter and the pump screen keep getting clogged. I believe by getting rid of what's in micro fast unit it will fix some if not all the issues that we found. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
11/28/2023 | Alternative | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus |  |  | Microfast | [25 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/29/2024 | 12:44 PM
03/31/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/18/2023 | Alternative | RoutineScheduled | SWP-04-728 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 | 1500 | 0-0 0-3 0-3 | 0-1 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | None | Clear |  |  | 5.000000 | [11 empty] | Inspected | cleaned and septic tank pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 01:00 PM
07/19/2023 | Alternative | Routine/Scheduled | 234-14-232 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/19/2023 | Dec 30 1899 2:05PM
12/21/2023 | Alternative | RoutineScheduled | 109-11-0213 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | NA | [16 empty] | Inspected | Sludge Levels- 2" scum layer and 12 in sludge in septic tank-Treatment tank has sludge @ recirc zone 20", discharge zone 16" sludge, System needs pumping out- both tanks- Cleaned effluent screen, it was fully clogged and had been alarming due to the filter clogging. Both pumps are functional, alarm functional. Found 1 of the 6 float switches good and replaced the bad alarm float switch. Recirc pump 4007.5 hours and 54,849 vs 93773(it reaches 100,000 and resets) cycles and discharge pump has 1752.8 hrs vs 511 hours last visit and 4,375 cycles- it also clocked over. Ran in test mode and sprayed off the media, fully operational and system was pumped after our visit by Foutz | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/28/2023 | 09:30 AM
02/10/2023 |  | Initial Visit | 234-00-7645 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes ponding and bridging - recommend replacing drapes - serviced best able. Pump Tank - float sensors & pump operating - Panel is original to system - recommend replacing / updating. DBox - intact - pads intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/13/2023 | Jan 1 1900 9:30AM
04/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | Puraflo | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
08/17/2023 | Alternative | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Ecoflo |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | 09:49 AM
07/07/2023 | Alternative | RoutineScheduled | 109-06-0493 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [16 empty] | Inspected | Trouble Shooting . float repairs. Wires have settled into the ground and are not able to be reused for but test ok. Reprogrammed the circuit board and it went ok. Ran in test mode. Still gets intermittent alarms for high water but single owner uses little water. Suspect float issue or wiring issue. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/30/2023 | 05:30 PM
07/10/2023 | Alternative |  | 07-113-079 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/10/2023 |  | 6.730000 |  |  | 1.300000 |  |  | Will be sent separately |  | BOD: 6.73 TSS: 1.30 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/10/2023 | 12:00 AM
08/18/2023 | Alternative | Routine/Scheduled | 234-19-0033 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/18/2023 | Dec 30 1899 10:50AM
06/14/2023 | Alternative | Reportable Incident | 151-08-0126 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Believe Service Provider is Churchview Septic Service. Primary septic tank pumped empty for biofilter replacement. Removed spent biofilter media and replaced with new. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/21/2023 | 10:30 AM
06/26/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The peat is showing signs of its age, but appears to still have good texture and is not very saturated. Informed the homeowner that while the peat is approaching the end of its life, at this point we believe it is still functioning as specified by the manufacturer. Recommended that the homeowner trim up some of the plants around the modules to make access easier for future operators. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/03/2023 | Alternative | RoutineScheduled | 019-STS-29338 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 2000 | Puraflo Peat Moss |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Alarm call due to Septic alarm sounding. Upon arrival system was in normal automatic mode and levels were normal. Checked float switches and Pump, All testing operational. Pump pulled between 9.8 and 10.2 amps in normal range. Alarm call possible due to the switch panel being in off position. System is operational. Pump run time 183.67 hrs and 19,705 Cycles on meters. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
01/13/2023 |  | Reportable Incident | 234-14-267 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Pressure | Drip | UV | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit by Millers Services. Primary septic tank - normal level after clearing pump/drip clog. Aeration tank - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. U.V. - Ballast Fail - UV Not functioning. Drip - screen 100% clogged - serviced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/16/2023 | Jan 1 1900 12:30PM
10/13/2023 | Alternative |  | 17-120-0321A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | 3.000000 | 2250 | 750 | 750 | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation","Distribution Pump Operation"] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | Dec 30 1899 9:00AM
06/21/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/05/2023 | 12:00 AM
04/07/2023 | Alternative | Follow-Up | SD-12-174 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn | 2.000000 | 4000 | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Recirculation Pump"] | NA | Musty | Clear | [5 empty] | 03/30/2023 | Pump Chamber | 37.000000 |  |  | 16.000000 | 11.400000 |  | Will be sent separately | Inspected | Lab Samples BOD 37 / TSS 16 / TN 11.4 4,000 gallons removed from Septic tank 1 4-5-2023 Dosing rates checked and run times adjusted 4-7-2023 Auger holes excavated into wet areas and lime applied 4-7-2023 Preliminary layout of 4 potential repair areas 4-7-2023 Recirc pump 6 is not working, parts ordered. Tried to replace the motor only 4-7-2023 but was not working so reirc in POD 2 only operating at 1/2 capacity Met with Peter Brooks and Tom Ashton by email several times during the week regarding history and options for repair | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/17/2023 | 01:00 PM
02/01/2023 |  | RoutineScheduled | 2005-143-0326 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1500 | Orenco Advantec |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 12:15 PM
09/05/2023 | Alternative | RoutineScheduled | 08-183-100 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | FAST |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 09/05/2023 | 12:00 AM
03/31/2023 |  | RoutineScheduled | 13-183-116 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | Discharged sign installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/31/2023 | 12:00 AM
03/30/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | pump tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
01/24/2023 |  | RoutineScheduled | C122-18-0022 | Craig | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001094 | David | King | 3.000000 | 1000 | Norweco |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Cleaned effluent screens, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/24/2023 | 12:00 AM
11/14/2023 | Alternative | RoutineScheduled Component Maintenance | 099-STS-92110 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
07/20/2023 | Alternative |  | 195-STS-26918 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/20/2023 |  | 3.950000 |  |  | 5.800000 |  |  | Will be sent separately |  | BOD: 3.95 TSS: 5.80 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/20/2023 | 12:00 AM
11/29/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | [] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
03/30/2023 |  | Routine/Scheduled | 234-13-340 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | Jan 1 1900 2:45PM
12/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Mound | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | Septic Tank-6"sludge 1"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Interior demand dose control panel has no counts or ETM/ Controls, pumps, floats and alarms are functioning properly/ No breakout or spongy areas on the mound area and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air release valve was damaged. It was replaced at time of inspection. Inlet tee is same as noted in original inspection, but does not appear to be causing an issue at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/20/2023 |  | RoutineScheduled | 17-125-039 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/20/2023 | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled | 165-STS-334249 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Level Sensor Operation"] | ["Septic Tank Baffles","Level Sensor Operation","Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 12:00 AM
09/14/2023 | Alternative | RoutineScheduled Component Maintenance | SWP 98-570 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Follow up work to locate and replace drip system components as needed is planned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
09/22/2023 | Alternative | RoutineScheduled | 14-197-A3 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco | [33 empty] | Septic Inc sent pictures of the tablets in the chambers. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12:00 AM
01/27/2023 |  | Reportable Incident | 179-17-0073-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Recirculation Pump" ,"Level Sensor Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Owner called about alarm. Water level normal on arrival. Panel user log did not record a clogged filter alarm as expected because of lack of maintenance. It did record a couple of contactor alerts and a 30 day average pump cycle run time of .7 minutes (programmed for .3 minutes). Panel performed perfectly in test mode. If alarms persist, the contactor (and perhaps the motherboard) should be replaced. Recommend a 5-year tank pumping be completed in September. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
05/05/2023 | Alternative | RoutineScheduled | SD-05-44 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 1500 | Pura Flo |  | Pump | Gravity | Trenches |  | 45.000000 | ["SludgeScum Accumulation","Effluent Screens","Dispersal System Operation"] | ["SludgeScum Accumulation","Effluent Screens","Dispersal System Operation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/09/2023 | 10:25 AM
03/02/2023 |  | RoutineScheduled | 179-17-0233-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | The vent top is missing the lid above the aerator. We were advised by a Norweco distributor to obtain a new Polylock lid & fabricate a vent for it with PVC pipe & fittings. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
05/10/2023 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/21/2023 | 12:00 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Hydro-Action ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/13/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["None"] | ["None"] | NO | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | Dec 30 1899 12:20AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
07/31/2023 | Alternative |  | SD-10-247 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
09/13/2023 | Alternative |  | 2018-143-0255 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/24/2023 |  | Follow-Up |  | James City | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Peninsula | Miller's Septic Service | 1942001468 | Kevin | Blasing | 6.000000 | 9000 | None | None | Pump | Pressure | Trenches | Not Applicable | 4000.000000 | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Fully excavated area around pump tank where leakage is identified. Repaired / replaced leaking fernco fittings with proper pressure rated fittings. Crossover noted between forcemains - this is an issue - company AOSE in reviewing plans and specifications finds that crossover is NOT designed to be there. this is causing the pumps to be "undersized" as the AOSE cannot match the design headcurve when the forcemain lengths and fittings are doubled. Believe that the pumps do not have enough "oomph" to dose four fields so only ONE field is receiving effluent, causing a hydraulic issue for that field. Also, we have located only TWO absorption fields out of the FOUR that were permitted and reportedly installed! Further evaluation, possible camera of forcemain to locate required. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/25/2023 | Jan 1 1900 7:00AM
10/03/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/20/2023 | 12:00 AM
03/01/2023 | Alternative | Initial Visit | 157-02-133 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Primary septic tank - recommend pump out - effluent screen serviced. Aeration Tank - compressor replaced - mixing present Pump Tank - float sensors, pump and controls operating. dBox - intact - lid fractured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/02/2023 | 07:30 AM
01/31/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.460000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/14/2023 | 08:00 AM
03/30/2023 |  | Routine/Scheduled | 15-120-0219A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Trash Tank - normal level - feminine hygiene products and wipes present. Aeration Tank - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/03/2023 | Jan 1 1900 6:45AM
06/09/2023 |  |  | 099-14-0094-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1500 | 3-2 0-6 | 0-0 | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | None | Clear |  |  | 7.000000 | [11 empty] | Inspected | system functioning properly at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/09/2023 | 02:00 PM
12/02/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Dabney & Crooks, Inc. | 1942001489 | Bob | Fessler |  |  | PuraFlo |  | Pump | Gravity | Pad | Not Applicable | 500.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation","Distribution Pump Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation","Distribution Pump Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | 12:00 AM
07/31/2023 | Alternative | RoutineScheduled | 14-177-1059 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Microfast | [6 empty] | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | NA | [16 empty] | Inspected | - installed ground access riser cover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/03/2023 | 12:00 AM
12/21/2023 | Alternative | RoutineScheduled | 03-197-151 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/21/2023 | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX25 RT to Drip |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Septic system, minimal Scum and trace of slduge in old Septic tank/pump tank-pump and floats work, New septic tank 10-12" sludge- Recirc zone 8" sludge and discharge zone 10" sludge trace. Alarm Test Good - Floats test Good - Recirc Pump time & count 1124.5 Hours 82654 Cycles - Discharge pump time 332 hours 8113 cycles. trended 551 days in history- No alarms in history for 2022-2023 on advantex- 11.5 amp on recirc pump and 12.0-12.2 amp on discharge pump. Confirmed factory reccomended setting. Cleaned effluent filter in septic and drip spin filter was flushed. Adjusted spray pattern - alarm works but audible tweeter disconnected by owner - Roots have been noted growing into the new septic tank and reccomend to remove the maple tree near the system to prevent a root issue. tree expert was contacted by owners, | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
08/23/2023 | Alternative | RoutineScheduled | 09-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | MULTIFLO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/23/2023 | 12:00 AM
04/08/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Gravity | Trenches |  |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/22/2023 | 12:00 AM
05/12/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
11/10/2023 | Alternative | RoutineScheduled Component Maintenance | 179-07-0357-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Owner is planning to reseal pump line to prevent root intrusions and to replace vent cap. Dispersal area also needs to be cleared and maintained in a mowed condition. We are planning to scrape the sheets and pump the tanks at the next fall?s inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
09/01/2023 | Alternative | Pump-Out Only | 04-120-0643A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Supervised pumpout of treatment system by Commonwealth Onsite Solutions. System refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | Dec 30 1899 8:00AM
11/13/2023 | Alternative | RoutineScheduled Component Maintenance | 107-17-0310 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | blower circuit board replaced | This AOSS should now return to normal function after having provided the above state routine maintenance | 01/15/2024 | 10:39 AM
04/08/2023 | Alternative | RoutineScheduled | SD-07-17 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump |  | Trenches |  |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/22/2023 | 12:00 AM
04/26/2023 |  | Routine/Scheduled | 234-15-216 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/26/2023 | Jan 1 1900 10:30AM
06/29/2023 | Alternative | Follow-Up Component Maintenance | 175-17-0411 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Installed Norewco UV Unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/30/2023 | 10:30 AM
11/15/2023 | Alternative | RoutineScheduled | 109-18-0191 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Scum level-under 1"- 10-12" sludge in Septic tank, 6" backup at effluent filter. Treatment unit - Recirculation zone 5-6" sludge - Discharge zone 3-4" sludge, Owner has addressed the surroundof septic tank and run off around tank area, Clear effluent on top of discharge. Cleaned Effluent filter-very dirty/clogged, sprayed off media, Ran in test mode, all floats tested ok, Alarm functional. Soil was about 1" high around the center septic tank lid and thus had some minor runoff mud in the lid seal-it was cleaned and removed. Box 428520 and RTU 136855 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 09:30 AM
12/08/2023 | Alternative | RoutineScheduled | 154-08-0188 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [14 empty] | Inspected | Sludge/Scum Accumulation - Septic 6", ATU 18" Blower Amperage - 2A | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/08/2023 | 09:00 AM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/23/2023 | Alternative | RoutineScheduled | 043-03-283 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/13/2023 | 12:00 AM
02/21/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.600000 |  |  |  |  | 02/21/2023 |  | 13.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/13/2023 | 03:00 PM
03/24/2023 | Alternative | Initial Visit | 800-STS-15282 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 16.000000 |  | 380.000000 | [5 empty] | Owner called about an alarm. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and diffuser in the Clearstream. Changed the filter in the aerator and cleaned the UV light bulb. The aerator should be raised. Replaced wire connectors with silicone wire nuts. The timer is set to 3.75 minutes every 3 hours. Took initial BOD and Fecal samples. NOTE : Fecal sample was a tad high - system should function properly after service. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/24/2023 | Dec 30 1899 3:30PM
09/15/2023 | Alternative | Routine/Scheduled | 136-03-103 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal level Less than 1 in of sludge and solids Pulled and cleaned filter No signs of infiltration -Discharge/Pump Tank: Normal level Pulled and tested floats all functioning properly Pump is functioning properly Plumbing and floats tree intact No signs of infiltration -Peat Moss: Tipping bucket and dispersal trays are intact Peat moss saturated and infiltrated with roots -Control Panel: 120 volts coming in All visual and audible alarms functioning properly However the panel is aged Pump pulled 6.8 amps | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 01:28 PM
07/13/2023 | Alternative | Reportable Incident Component Maintenance | 177-06-0594-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system in alarm due to clogged RSV. Cleaned RSV. Recomend pumping out recirc tank during next years inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/18/2023 | 11:45 AM
07/04/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/12/2023 | 12:00 AM
07/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/19/2023 | Alternative | Reportable Incident | 093-16-0216 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream | [6 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/19/2023 | Dec 30 1899 9:00AM
02/07/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
09/07/2023 | Alternative | RoutineScheduled | 08-160-0192 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001094 | David | King | 1.000000 | 1500 | Delta DF50 |  | Pump | Pressure | Mound | Not Applicable | 150.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Cleaned effluent screens, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/12/2023 | 12:00 AM
11/17/2023 | Alternative |  | 179-STS-87675 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/30/2023 | Alternative | RoutineScheduled | 127-STS-31954 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton | 2.000000 |  | Purasys |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/30/2023 | 12:00 AM
11/27/2023 | Alternative |  | 107-05-0586 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/27/2023 | 12:00 AM
08/07/2023 | Alternative | RoutineScheduled | 015-STS-335994 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
03/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Valve box riser cover needs to be replaced as it is broken. Low pressure does not appear to be functioning as designed. Homeowner is contacting company for repairs. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 03/04/2023 | 06:02 AM
12/05/2023 | Alternative | Reportable Incident |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a smell in backyard. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream - was stopped up. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1 minute 30 seconds every 2 hours 30 minutes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/05/2023 | Dec 30 1899 12:30PM
10/26/2023 | Alternative | Reportable Incident | 093-11-0075 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Cleaned filter | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/26/2023 | Dec 30 1899 4:00PM
04/20/2023 | Alternative | Initial Visit | 015-STS-337151 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [15 empty] | no local lab available | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/06/2023 | 12:00 AM
04/18/2023 |  | RoutineScheduled | 175-17-0104 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
02/10/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
02/14/2023 |  | RoutineScheduled | 179-11-0115-SWT | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation"] | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
04/28/2023 | Alternative | RoutineScheduled | 13-197-048 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/28/2023 | 12:00 AM
11/16/2023 | Alternative | RoutineScheduled | 08-192-128 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Fast |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 11/16/2023 | 12:00 AM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/20/2023 | Dec 30 1899 12:57PM
03/27/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air release valve was damaged. It was replaced at time of inspection. Inlet tee is same as noted in original inspection, but does not appear to be causing an issue at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
09/29/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001763 | Jessica | Young |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/29/2023 | 12:28 PM
09/27/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1875 | Septic | pu | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/31/2023 |  | Follow-Up | 550-STS-6781 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/31/2023 |  | 26.000000 |  | 60.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 8:25AM
02/24/2023 |  | Follow-Up | 179-10-0072-STWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Cleaned FAST media, pump out of tank by others. Dug up FAST unit. Removed unit from tank. Removed roots. Sealed root penetration in tank. Replaced 1 ARV box lid. Cut down 12 trees. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 08:46 AM
01/31/2023 |  | RoutineScheduled |  | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/20/2023 | 12:00 AM
06/10/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 | 1000 |  |  | Pump |  | Drip |  |  | [] | [] | YES | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
10/02/2023 | Alternative |  | 02-197-091 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None |  | 6.500000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
01/20/2023 |  |  | 06-142-0398 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/03/2023 | 12:00 AM
01/16/2023 |  | RoutineScheduled | 107-02-0262 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","None"] | ["Effluent Screens","None"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/08/2023 | 12:00 AM
01/06/2023 |  | Routine/Scheduled | 02-120-0775A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level Processing Tank - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray gird serviced - sheets beginning to pond. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2023 | Jan 1 1900 9:15AM
04/27/2023 | Alternative | Initial Visit | 097-STS-95811 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to some issues. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the aerator. The timer is set to 2 minutes every 2 hours. Did not take sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 10:30 AM
07/10/2023 | Alternative | Reportable Incident Component Maintenance | 177-12-0170-SR | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for system alarming for a contactor fail and recirc high level. Changed local alarm delay per orenco to prevent the contactor alarms as the contactor has not failed. Ants got in recirc junction box causing a false high level alarm. Redid all wire connections in the recirc junction box. Recirc pump relay was sticking tapped relay and it released. may need a new board if relay continues to stick. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
01/10/2023 |  | RoutineScheduled | 00-197-224 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Dispersal System Operation","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2023 | 12:00 AM
11/01/2023 | Alternative | Pump-Out Only | 02-120-0269A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [16 empty] | Pumped Out | Came out to pump septic tank and processing tank Met pump truck on site Resealed recirculation tank riser inside only. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/02/2023 | Dec 30 1899 10:41AM
11/02/2023 | Alternative | Routine/Scheduled | 087-STS-6473 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/02/2023 | 08:32 AM
06/15/2023 | Alternative | Routine/Scheduled | S 800-16-0021 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Advanced Septic |  | Pump | Pressure | Drip | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service - Aquasafe ATU Primary septic tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. PUmp tank - float sensors, pump and controls operating. Drip Field - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | Dec 30 1899 7:15AM
01/05/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2724 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Pad | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/05/2023 | Jan 1 1900 9:30AM
08/09/2023 | Alternative | RoutineScheduled | 175-07-0051 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank to Delta DF-75 ATU | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [17 empty] | Septic Tank-6"sludge 0"scum/ Delta DF-75 ATU-4"sludge/ Pump Tank-4"sludge/ No pump out needed at this time/ ATU Blower in alarm due to moisture in the junction box - repaired/ Blower air filter cleaned and blower now functioning properly/ Replaced faulty Off Float/ Controls, pump, floats and alarms now functioning properly/ Found faulty 1 1/4" check valve on the forcemain and returned on 8/24/2023 to replace, tested and now functioning properly/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
11/08/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [8 empty] | 0.000000 | [] | [] | [18 empty] | NO FLOW | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/20/2023 | 07:03 PM
05/19/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/23/2023 | 07:57 AM
04/04/2023 |  | RoutineScheduled | 177-STS-89562 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
01/06/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3737 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 01/06/2023 | Jan 1 1900 10:10AM
06/29/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-04-441 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation"] | ["Recirculation Pump" ,"Septic Tank Baffles" ,"Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | Musty | Cloudy | [5 empty] | 06/29/2023 |  | 202.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Sample will fail, blower was not pumping any air, reset and treatment started to work. Nibbler number 1 looks very dirty and has 13" of sludge, recommend pumping it. Pumped about 4" of sludge back to grease trap. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/13/2023 | 10:41 AM
03/22/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend evaluation of the distribution boxes. Trees on neighboring lot could potentially cause damage to the system (Force main, Distribution Boxes, Headers, Lines). The septic tank is listed as a plastic tank but was replaced in 2014 with concrete tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System is connected to 36001 and has the same issues. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/26/2023 | Alternative | RoutineScheduled | 047-17-148 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens" ,"Control Operation" ,"Level Sensor Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots on septic tank wedge lid but no water infiltration at this time, inspection was done after rain. Roots on ATU tank around inlet pipe gasket, no water infiltration at this time (removed roots) . Pump tank needs to be pumped due to sludge level 9". Recommend to skimmed scum layer in atu at time of pumping pump tank. Feminine products in septic tank, left copy of Do's and don'ts. Will send proposal to remove roots from wedge lid and add acces point on septic tank inlet side and to seal gasket on atu tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
01/27/2023 |  | RoutineScheduled |  | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Rappahannock-Rapidan | McKim Septic and Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/29/2023 | 01:20 AM
01/16/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip |  | 600.000000 | ["Auxiliary Filter","Dispersal System Operation"] | Auxiliary Filter | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/10/2023 | 02:22 PM
06/19/2023 | Alternative | Reportable Incident | 151-07-0172 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Attached Growth Medium | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | 06/19/2023 - pumped septic tank for biofilter changeout. 06/22/2023 - biofilter changeout conducted - ONE single PuraFlo Module! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/22/2023 | 03:00 PM
07/28/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
06/10/2023 | Alternative | RoutineScheduled | 12-100-0146 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Pressure | Trenches |  | 450.000000 | [] | [] | [18 empty] | EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/16/2023 | 02:00 PM
04/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
04/13/2023 |  | RoutineScheduled | 101-17-0244 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Advantex |  | Gravity | Pressure | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/16/2023 | 12:00 AM
03/13/2023 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches |  | 600.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | BlowerCompressorAerator Operation | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 04/11/2023 | 11:53 AM
01/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
06/01/2023 | Alternative |  | 09-192-012 | Tazewell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/01/2023 |  | 2.820000 |  |  | 1.400000 |  |  | Will be sent separately |  | BOD: 2.82 TSS: 1.40 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/01/2023 | 12:00 AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0069-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | We recommend replacing the Clearstream riser lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
10/13/2023 | Alternative | Reportable Incident | 193-STS-94787 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced leaky uv housing, repaired uv alarm panel | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Alarm was on upon arrival. Audible had been unplugged and was plugged back in. Recirculation float was stuck down. The system should return to proper operation now. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/06/2023 | Alternative | RoutineScheduled | 14-100-0361 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/14/2023 | 08:45 AM
10/17/2023 | Alternative | RoutineScheduled Component Maintenance | 182-03-0315 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 10/17/2023 |  | 28.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
06/21/2023 | Alternative | Follow-Up Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Pressure | Drip | UV |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repair air relief valve. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/07/2023 | Dec 30 1899 6:25AM
09/25/2023 | Alternative | RoutineScheduled | 107-19-0086 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex |  |  |  | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles"] | ["Auxiliary Filter","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | 12:00 AM
03/30/2023 | Alternative | Pump-Out Only | 18-177-1049 | Pulaski | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner |  |  | Aquasafe | [6 empty] | [] | [] | [18 empty] | - customer informed us that she will not proceeding with maintenance as she will be selling the home - she has blower replaced, unsure of maintenance provider, informed customer of codes stating this needed to be reported electronically to the State by a licensed operator/maintenance provider | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/11/2023 | 12:00 AM
04/12/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Drip |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic system, minimal Scum and minimal slduge in old Septic tank/pump tank, New septic tank 10-12" sludge- Recirc znoe 8" sludge and discharge zone 10" sludge trace. Alarm Test Good - Floats test Good - Recirc Pump time & count 1124.5 Hours 82654 Cycles - Discharge pump time 332 hours 8113 cycles. trended 551 days in history- No alarms in history for 2022-2023 on advantex- 11.5 amp on recirc pump and 12.0-12.2 amp on discharge pump. Confirmed factory reccomended setting. Cleaned effluent filter in septic and drip spin filter was flushed. Adjusted spray pattern - alarm works but audible tweeter disconnected by owner - Roots have been noted growing into the tank and reccomend to remove the maple tree near the system to prevent a root issue. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
07/15/2023 | Alternative | RoutineScheduled | 109-16-0148 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | EZ Treat |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | NA | [17 empty] | Annual inspection. Septic Tank - 4" solids crust, 4" solids in bottom. 1" solids accumulation in recirculation pump/discharge pump tank. Tested floats, pumps and alarms. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/14/2023 | 07:03 PM
07/18/2023 | Alternative | RoutineScheduled | 179-STS-91626 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 9557.000000 | [] | [] |  |  |  | 7.360000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
09/15/2023 | Alternative | Reportable Incident | 166-18-078 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Alarm Call: Customer stated alarm light was on Found panel in high level Tested floats and found high level alarm float was stuck in on position Replaced both floats under warranty Tested and confirmed all components were functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/05/2023 | 02:00 PM
05/31/2023 | Alternative | RoutineScheduled | 07-160-0276 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | LPD |  | Pump | Pressure | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation","SludgeScum Accumulation"] | NA | [16 empty] | Inspected | - siphon pump is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 06/08/2023 | 12:00 AM
05/03/2023 | Alternative | RoutineScheduled | 095-STS-5878 | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Peninsula | Hutchens Septic Services LLC | 1942001509 | Robert | Hutchens, Jr. | 1.000000 | 1500 | Advantex AX-20 |  | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | None | Clear | [15 empty] | Drip field is surfacing onto the ground | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/03/2023 | 12:00 AM
05/23/2023 | Alternative | Routine/Scheduled | 151-10-0002 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. BioFilter - concrete - peatmoss in poor condition - raked / turned. Pump Basin - float sensors, pump and controls operating. DBox - intact - re-balanced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/01/2023 | 09:15 AM
08/28/2023 | Alternative | RoutineScheduled Component Maintenance | 175-02-0324 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
08/23/2023 | Alternative | RoutineScheduled | 099-STS-89319 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Elite Onsite | 1942001726 | Drew | Saunders | 2.000000 | 2000 | 1000 | 1000 | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 03:35 PM
12/19/2023 | Alternative |  | 09-197-A1 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/19/2023 |  | 4.590000 |  |  | 8.600000 |  |  | Will be sent separately |  | BOD: 4.59 TSS: 8.60 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
06/21/2023 | Alternative | Reportable Incident | NYII-ATHMZU | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/21/2023 | Dec 30 1899 10:00AM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | 107-01-0447 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 10/16/2023 |  | 7.500000 | [5 empty] | Will be sent separately | Inspected | Recommend uncovering septic tank and adding riser on septic tank and inlet of microfast tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/22/2023 | 09:18 AM
01/17/2023 |  | Reportable Incident | 177-STS-90172 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Recirc tank was barely in high level, drip tank normal level. No problem found with operation, no obvious infiltration, and no running water seen coming into the recirc tank. Suspect owners, not yet familiar with the system, used too much water in a given period. Pumped the level down enough to get it out of high level and then reset all "R" counts in the recirc panel back to zero. Informed owner that she had 2 tanks that pumped on a time-dosed basis and that too much water use, including a running toilet, could cause a high level alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2023 | 06:07 AM
07/05/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-03-831 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend removing the trees growing on the drip mounds. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 06:26 AM
09/29/2023 | Alternative | Follow-Up Component Maintenance | SP-01-593 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced zone 1 & 2 check valves. Replaced bad blower. Media is clogged, proposal to be sent to clean media and pump out both tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/02/2023 | 05:18 AM
04/18/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/26/2023 | Alternative | RoutineScheduled Component Maintenance | {FIPSCode}-STS-63692 | Caroline | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | fabric sheet replacement was completed by others. Manufacturer?s representative confirmed that system is currently lacking total number of sheets (50 vs 60) needed to get proper treatment. We recommend adding the additional ten sheets. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 12/01/2023 | 08:44 AM
08/04/2023 | Alternative | RoutineScheduled | 182-98-0203 (LEGACY ALT. SYSTEM-spray) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation","Effluent Screens"] | ["SludgeScum Accumulation","Effluent Screens"] | YES | Musty | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
08/01/2023 | Alternative | Routine/Scheduled |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Purasys |  | Pump | Gravity | Pad | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service - PuraSys - Sequential Batch Reactor. Primary septic tank - normal level Processing Tank - Sludge Return - functioning. Processing Tank - Aeration - mixing present - submersible compressor serviced. Processing Tank - dosing - float sensors, pump and controls operating. DBox - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/02/2023 | 07:15 AM
08/22/2023 | Alternative | RoutineScheduled | 12-114-081 | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 3.000000 | 6000 | EZ Treat |  | Pump | Gravity | Trenches | Not Applicable | 1400.000000 | ["Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Control Operation","BlowerCompressorAerator Operation","Effluent Screens","SludgeScum Accumulation","Septic Tank Baffles"] | YES | Musty | Cloudy | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | Dec 30 1899 4:00AM
07/13/2023 | Alternative | Pump-Out Only | 136-18-0297 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Biomicrobics Retrofast |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [16 empty] | Pumped Out | Pumped primary septic tank Replaced leaking access riser on tank. Refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/17/2023 | 07:45 AM
07/21/2023 | Alternative |  | 033-07-0020-SR | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
05/13/2023 |  | Reportable Incident | 550-STS-5883 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/12/2023 | Jan 1 1900 8:00AM
08/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Septic | Clear | [13 empty] | Will be sent separately | Inspected | 8/23/23 On arrival, blowers were not running because someone had turned off the little switch at the bottom of the Omron processor. Turned them back on and replaced the missing locks. Observed roots growing under the manways which created a point of groundwater infiltration. Removed both manways, power-brushed clean the tank top and manway flanges, applied sealant, and reattached the manways with Tapcon screws. During that repair, the bulkhead adapters (for pump connections) were found to be cracked and the seals practically disintegrated. Replaced the bulkhead adapters and pvc fittings in order to correct the pipes settling. Also repaired settling damage to the conduit at the blower housing. Remaining work halted by rain. 8/24/23 Unions added to pump piping in tank to facilitate pump maintenance. Finished connecting pump lines at new bulkhead adapters. Replaced the boards in blower housing that support the blowers. Junction box terminal strip (for pumps and blowers) had screws that would no longer tighten. Terminal strip replaced and larger ground lug added. Filter element for blower canister filter was replaced and the air pre-filter cleaned. When the blowers were restarted, bubbling started at the 4 newer diffusers first. After about 3 minutes, aeration developed at the other diffusers. Filterbed maintenance is required, grass is too high. Indications of root growth into the manifold. Added 4 bottles of Root Stop to hopefully kill the roots. Blower #2 running light (green) replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/08/2023 | 06:43 AM
06/01/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/16/2023 | Alternative | RoutineScheduled Component Maintenance | 196-06-361 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | As noted previously, the control panel is not registering ETMs or cycle counts but seems to be working otherwise. Panel replacement is recommended. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
12/08/2023 | Alternative | Reportable Incident | 093-17-0011 | Isle Of Wight | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the red light being on. Serviced system. Checked the pump, panel, and floats (ok). Changed the filter in the aerator and changed the mesh screen in the spinfilter. The aerator needs to be raised. The UV is not working - probably the UV ballast and bulb - needs to be fixed. Need to pump and clean out the Clearstream tank and pump tank. The timer is set to 4 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/08/2023 | Dec 30 1899 4:30PM
04/05/2023 |  | Routine/Scheduled | 18-120-0278A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Norweco Singulair ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/05/2023 | Jan 1 1900 5:01PM
03/10/2023 |  | RoutineScheduled | 13-100-0048 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Puraflo | Gravity | Pressure | Pad | Not Applicable | 300.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 02:35 PM
04/24/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [7 empty] | 04/24/2023 | Sample Chamber | 11.000000 | [5 empty] | Attached to this report |  | Septic Tank-4"sludge 3"scum/ Microfast ATU-2"sludge / Pump Tank-0"sludge/ No pump out needed at this time/ Blower air filter cleaned and blower working correctly/ Faulty off float replaced during inspection/ Controls, pumps, floats and alarms now functioning properly/ Counts: Pump1-157 ETM-10h 41m/ Pump2-171 ETM-9h 58m/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
12/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 12/06/2023 |  | 55.000000 | [5 empty] | Will be sent separately | Inspected | Replaced all media in treatment tanks | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
01/24/2023 |  | RoutineScheduled | 177-06-0501-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
10/13/2023 | Alternative | Follow-Up Component Maintenance | 047-16-019 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | UV |  |  |  | NA | [9 empty] | 2.000000 |  | 1.000000 | 1.000000 |  |  | Will be sent separately | Inspected | *SAMPLING/TESTING RESULTS ONLY** Dissolved Oxygen 8.48 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
05/02/2023 | Alternative | Routine/Scheduled | S 800-17-0046 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/02/2023 | Dec 30 1899 9:10AM
01/27/2023 | Alternative | Routine/Scheduled | 166-08-080 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Gravity | Pad |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 35.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/27/2023 | 05:35 PM
09/01/2023 | Alternative | RoutineScheduled | 087-STS-6179 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | EZ Treat |  | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/19/2023 | 12:00 AM
03/21/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/12/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air filter replaced as a matter of preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
04/04/2023 | Alternative | RoutineScheduled | 17-100-0154 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AQUASAFE |  | Pump | Pressure | Mound | UV | 600.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | REPLACED BLOWER ALARM EVERYTHING WORKING AS IT SHOULD | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/07/2023 | 10:30 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
04/11/2023 |  | Routine/Scheduled |  | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Advanced Septic |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service - Aquasafe ATU Trash Tank - normal level Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 07:15 AM
03/29/2023 |  | RoutineScheduled | 2018-143-0236 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Fuji |  | Pump | Gravity | Trenches |  |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Distribution Pump Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:00 AM
04/12/2023 | Alternative | RoutineScheduled | SD-10-208 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic, LLC | 1942001236 | Stuart | Lynn |  | 8000 | Whitewater ATU | Whitewater ATU | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | 4-12-2023 8,000 gallons sludge removed from bottom of ECOPOD 1 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | 12:05 PM
04/03/2023 | Alternative | RoutineScheduled | 06-100-0071 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1250 | ECOFLO |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | [] | [] | YES | [16 empty] | Pumped Out | REPLACED PEAT, REPLACED PUMP, REPLACED FORCEMAIN, EVERYTHING WORKING AS IT SHOULD. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 09:40 AM
04/01/2023 | Alternative | Routine/Scheduled | 03-160-0132 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 122.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/01/2023 | 01:00 PM
01/13/2023 | Alternative | Initial Visit | 159-09-0053 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 3.000000 | 5000 | Clearstream | Clearstream | Pump | Pressure | Trenches | Not Applicable | 2000.000000 | ["Control Operation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit for Full Service. Grease Trap - requires pumpout. Primary septic tank - riser fractured - recommend replacing. Secondary septic tank - riser leaking / cracked - recommend replacing. Effluent screen - held together by zip ties - recommend replacing. Aeration Tank #1 - mixing present - compressor serviced. Aeration Tank #2 - mixing present - compressor serviced. Pump Tank - pumps pulling high amperage - sparking / arcing noted in control panel - recommend replacing pumps and controls. AOSS is functioning, but requires some TLC, and Lab sampling as per Operations Permit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/16/2023 | 11:45 AM
09/15/2023 | Alternative | RoutineScheduled | 165-STS-336290 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
07/29/2023 | Alternative |  |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/07/2023 | Alternative | RoutineScheduled | 033-19-0057-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced filter, system check - okay | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | 175-00-0086 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/15/2023 | 01:44 PM
06/14/2023 |  |  |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | EcoPod | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
12/14/2023 | Alternative | RoutineScheduled | 181-05-0378 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | 12:00 AM
03/29/2023 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV ballast & bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/15/2023 | Jan 1 1900 7:20PM
10/05/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 10/16/2023 | Dec 30 1899 12:58PM
03/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/08/2023 |  | Routine/Scheduled | 09-120-0085A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Bionest |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/08/2023 | Jan 1 1900 9:50AM
10/16/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-01-501 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Roots in pod, cut roots and added root destroyer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
03/08/2023 |  | Initial Visit | 147-19-0046 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 500 | Aqua Klear |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | AOSS - Initial Visit. Trash Tank - normal level - effluent screen serviced. Aeration Tank - normal level - mixing present - compressor serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/09/2023 | Jan 1 1900 7:30AM
01/10/2023 |  | Pump-Out Only | 234-03-11112 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | Pumpout / Inspection Pumped processing tank empty - refilled with fresh water for restart. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2023 | Jan 1 1900 12:00PM
03/15/2023 |  | RoutineScheduled | 177-STS-91730 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | Musty | Cloudy | [5 empty] | 03/15/2023 |  | 56.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Sample taken. Treatment is cloudy. Gave customer copy of Do's and don'ts. Customer flushing a lot of toilet paper if paper level gets higher by the 1 year inspection tank will need pump out. Splitter box and both D-boxes needed dial flow adjusted. HL 4, LL12, OVERRIDE 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
08/21/2023 | Alternative | Follow-Up | 033-17-0095-SR | Caroline | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 2.000000 | 1000 | Purasys |  | Pump | Gravity | Mound | Not Applicable | 100.000000 | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | N/A | [17 empty] | Replaced control panel, aerator and discharge pump. pluged unused cord grips. System should work as designed. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/22/2023 | 07:53 AM
03/27/2023 |  | RoutineScheduled | SP-05-541 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Drip system appears to be functioning exactly as designed. Field shows perfect emitter spacing. If viewed from Spinks Ferry, it might appear that there is a nitrified streak coming from the pump chamber riser down, but during inspection, there were no signs of any malfunction, sewage on the ground, or any other explanation for the discoloration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/24/2023 | Alternative |  | SP-05-708 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/16/2023 | 12:00 AM
05/04/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 06:27 AM
10/30/2023 | Alternative | RoutineScheduled | 182-10-0130 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Auxiliary Filter","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Auxiliary Filter","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 12:00 AM
04/27/2023 |  |  | 2019-143-0007 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Aquaklear | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/10/2023 | 12:00 AM
09/05/2023 | Alternative | RoutineScheduled | 06-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | [12 empty] | None | Clear | 7.400000 | 8.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
02/24/2023 |  | Routine/Scheduled | 199-06-0021 | York | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/24/2023 | Jan 1 1900 1:07PM
04/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
10/03/2023 | Alternative | RoutineScheduled Component Maintenance | 061-15-443 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | None | Clear | [5 empty] | 10/03/2023 | Pump Chamber | 3.000000 | [5 empty] | Will be sent separately | Inspected | On site for annual inspection and to investigate high level alarm. The "ON" float was stuck off, and the "OFF" float was intermittently sticking on - replaced both of those floats with Orenco brand floats. Also collected the 5-year BOD sample. This system gets very little use so the blower timer had been set to run 30 min "ON" and 30 min "OFF". Treatment looked excellent and was confirmed by lab results of 3 mg/L. Riser joints for all 3 tank openings showed evidence of infiltration, need to be resealed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 06:08 AM
07/07/2023 | Alternative | RoutineScheduled Component Maintenance | 153-STS-20511 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | 02:41 PM
05/04/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/02/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
06/08/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
01/26/2023 |  | RoutineScheduled | 033-STS-86695 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
01/11/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Disinfection" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | Jan 1 1900 11:08AM
10/20/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation","Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/02/2023 |  | RoutineScheduled | 175-04-0420 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Whitewater ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
02/20/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Homeowner had tree company plant shallow saplings on the property. Tree company had planted some saplings on the end of the lines. They do not appear to be causing an issue at this time. The homeowner is contacting the tree company to move them off the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
06/23/2023 | Alternative | Follow-Up Component Maintenance | SP-03-320 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank pumped out by others 2 days prior to peat replacement. Degraded peat was removed by hand and new peat was installed. Peat was purchased from Wrights Ready Mix. Degraded peat was disposed at Spotsylvania Refuse. Added root destoyer to pods. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
12/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Do not park vehicles near tanks | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/15/2024 | 10:39 AM
08/11/2023 | Alternative | RoutineScheduled | 10-192-161 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | AQUAKLEAR |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/11/2023 | 12:00 AM
07/28/2023 | Alternative | RoutineScheduled | 19-160-0036 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | [9 empty] | [] | [] | [17 empty] | Inspected | - replaced blower and repaired broken air line - completed inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/07/2023 | 12:00 AM
02/16/2023 |  | RoutineScheduled | 177-06-0361-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | We recommend mowing the dispersal area and maintaining it in a mowed condition to prevent roots from interfering with the drip tubing. The water meter is not working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 12:05 PM
05/30/2023 |  | Routine/Scheduled | 041-STS-258117 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | Jan 1 1900 1:54PM
02/03/2023 | Alternative | Initial Visit | 133-STS-93163 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 500 | Norweco Singulair ATU | Advanced Septic | Pump | Gravity | Trenches | Not Applicable | 300.000000 |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Initial Visit - AOSS - Trash Tank - normal level Aeration Tank - normal level - mixing present - aspirator serviced. Clarifier - effluent screen serviced. Pump Tank - float sensors, pump and controls operating. DBox - Intact | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/06/2023 | 11:15 AM
02/17/2023 | Alternative | Routine/Scheduled | 159-96-367 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Puraflo |  | Gravity | Gravity | Pad | Not Applicable | 300.000000 | ["Attached Growth Medium","Effluent Screens","Septic Tank Baffles"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit Primary septic tank - no riser access - effluent screen broken / serviced - requires installation of access riser to grade and replacement of cannister effluent screen. Pump Tank - float sensors, pump and controls operating. Biofilter - 3 Modules - Peatmoss is spent - requires replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 02/20/2023 | 11:00 AM
05/03/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The end of the lowest mound (closest to Hillsboro Rd) is soft and spongey. Homeowner is contacting someone to look at. Recommend addressing issue before if becomes a bigger problem. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
08/30/2023 | Alternative | RoutineScheduled | 195-STS-27630 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Rodney | Neece | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Septic | Clear | 6.000000 | 4.000000 | [13 empty] | The unit needs caps on it and not sure it is working correctly. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
03/27/2023 |  | Reportable Incident | 107-14-0261 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [15 empty] | Blower alarm. replaced blower. repaired dripfield leak | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/08/2023 | 12:00 AM
10/25/2023 | Alternative | RoutineScheduled Component Maintenance | 179-10-0047-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | Sulphitic | Discolored | [13 empty] | Will be sent separately | Inspected | Upon arrival breaker for discharge pump was tripped inside the house. Alarm did not sound due to corroded wiring. Cleaned and reconnected alarm float wire. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
06/23/2023 | Alternative |  | 139-07-0185 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Michael | Sikorski | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
07/19/2023 | Alternative | Reportable Incident Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired force main in pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
03/14/2023 | Alternative | Routine/Scheduled | 093-09-0175 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  | Pad | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/14/2023 | Dec 30 1899 9:00AM
03/30/2023 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | replaced contactor | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/28/2023 | 02:17 PM
08/15/2023 | Alternative | RoutineScheduled | 07-160-0109 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 3.000000 | 2500 | Ecoflo (peat moss) |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Septic | [6 empty] | 08/15/2023 | Pump Chamber | [6 empty] | Attached to this report | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/05/2023 | 12:00 AM
06/12/2023 |  | RoutineScheduled | 124-STS-2379 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Virginia Beach | Great Falls Septic Service, Inc. | 1942001763 | Jessica | Young | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/31/2023 | Alternative | Reportable Incident | 14-172-0441A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Upon arrival, I found the control panel NOT in alarm condition. System was in normal level. Checked and confirmed discharge pump, floats, and control panel were functioning properly. Checked clea out and found no signs of infiltration from residence. System appears to be functioning properly at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/03/2024 | Dec 30 1899 10:04AM
09/07/2023 | Alternative | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | LP | [6 empty] | ["None"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/07/2023 | 12:00 AM
04/10/2023 |  | RoutineScheduled | 001-STS-91758 | Accomack | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1000 | AquaSafe |  | Pump | Pressure | Mound | UV | 600.000000 | [] | [] | [18 empty] | Everything working properly. Put a new mushroom vent on AquaSafe lid. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/11/2023 | 12:00 AM
07/19/2023 | Alternative | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | [] | [] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 12:00 AM
07/14/2023 | Alternative | Routine/Scheduled | 12-142-0048 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 07/14/2023 | Dec 30 1899 2:30PM
05/05/2023 |  | Reportable Incident | 07-142-0370 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | AOSS - Initial Visit - Alarm Event - previous service provider = Mathews Soils. - Owner contacted Millers due to service provider not responding to phone calls and alarm event. Processing Tank - high level - dismounted RSV - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/08/2023 | Jan 1 1900 9:00AM
05/03/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | fuji tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
01/10/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/15/2023 | 06:51 AM
10/18/2023 | Alternative | Routine/Scheduled | 166-09-055 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal Level Less than 1" of sludge and solids No visible signs of infiltration Inlet tee intact Outlet filter was pulled and cleaned -Peat Moss: Minor crack in Peat chamber that has been repaired before has a minor Crack in it Peat moss chamber has signs of chamber filling with water at some point. Peat moss was sitting on top of trays Tipping bucket and dispersal trays are intact Inspection support is holding 13" of water | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/30/2023 | 11:15 AM
05/15/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Drip |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | [16 empty] | Inspected | Septic system, 1-2" Scum and 16-20" sludge in old Septic tank, Recirc znoe 7-8" sludge trace and discharge zone 7-10" sludge trace. Alarm Test Good - Floats test Good- low float on recirc maybe need to keep an eye, dimly lit when lifted may send a false signal. Maybe water in jbox. New wirenut did not fix the issue. - Recirc Pump time & count 591.4 Hours 43820 Cycles - Discharge pump time 104.6 hours 636 cycles. trended 368 days in history- 1 Alarms in history for1-5-2023 on advantex- same for alerts, Confirmed factory reccomended setting. Cleaned effluent filter in septic asystem is connected to montiroing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
02/19/2023 |  | Routine/Scheduled | 041-STS-259249 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [16 empty] | Recommend pump out! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/19/2023 | Jan 1 1900 10:00AM
03/11/2023 |  | RoutineScheduled | 133 13 0172 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 2" of accumulated solids in septic tank. O" of solids in discharge pump tank. Flushed treatment unit spray manifold. Cleaned recirculation pump basket filter. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/12/2023 | 07:03 PM
06/15/2023 | Alternative | RoutineScheduled Component Maintenance | 061-16-250 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. Drip tank was barely in low level alarm. PLC did show all floats as down. No reason found for alarm condition. High level count at 52, low level count at 470. In the past 16 days, system pumped an average of 897.4 gals/day at 281.5 gals/cycle (avg.) for a total of 14,359 gallons. The daily flow is probably the lowest it's been since tracking began. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
11/07/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-92122 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | ["Effluent Screens" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Replaced air blower filter. Added root destroyer around inside of riser to keep roots out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/04/2023 | 06:14 AM
04/28/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/18/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
07/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Filter was clogged but cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
08/14/2023 | Alternative | RoutineScheduled | 027-STS-17798 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/14/2023 | 12:00 AM
05/12/2023 | Alternative | RoutineScheduled | 023-STS-42681 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Sand Filter |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge levels-- 2-3" Scum layer-16" sludge in Septic tank. No Pumping Needed. Pump tank under 1" scum and 5" sludge on bottom. Alarm float and pump run float tested operational. Alarm sounded good. Drainfield - Owner is very careful about maintaining and cutting the drainfield.. Try to minimize FOG fats oil and grease in septic tank as well as chemicals and sanitizing and antibiotic cleaners and soaps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | Jan 1 1900 9:30AM
12/11/2023 | Alternative | RoutineScheduled | 165-STS-335993 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Advantex AX20 RT |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Septic Tank Baffles","Dispersal System Operation"] | ["Auxiliary Filter","Dispersal System Operation","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | 12:00 AM
11/13/2023 | Alternative | Reportable Incident | S 800-18-0154 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to the aerator not running. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter (it was blown out). Installed an aerator rebuild kit. The aerator should be raised. The septic tank needs to be pumped out (fill of grease - inlet tee was stopped up). When pumping the septic tank pump the sludge from the bottom of the Clearstream tank and clean the pump tank also. The timer is set to 6 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/13/2023 | Dec 30 1899 9:15AM
11/16/2023 | Alternative | Routine/Scheduled | 07-120-0586A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Orenco Advantex |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 11/16/2023 | Dec 30 1899 2:30PM
05/05/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Need to take sample peat is very broken down and sandy | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 05/15/2023 | 06:27 AM
09/28/2023 | Alternative | RoutineScheduled Component Maintenance | 179-08-0226-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
08/21/2023 | Alternative | Routine/Scheduled |  | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Drip | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service - component upgrades Processing tank - RSV, recirc pump replaced - effluent screen serviced. TReatment Module - media drapes & spray grid serviced. PUmp Tank - float sensors, discharge pump and controls upgraded / replaced. Drip field - headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/22/2023 | Dec 30 1899 6:30AM
06/02/2023 |  | RoutineScheduled | 175-13-0165 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank to Advantex Recirculation Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NO | [17 empty] | Septic Tank-6"sludge 0"scum/ Recirc Tank-4"sludge/ Pump Tank-3"sludge/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Recirc. pump intake cleaned/ Counts: Advantex pump-58034/ Pump run time-1352h/ Discharge pump counts-4756 ETM-30429/ AX-20 media in good condition and dosing properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
01/13/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Annual inspection. Air filter replaced as a matter of preventative maintenance. Minor buildup on the blower and slight bearing noise observed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/10/2023 | 06:25 PM
01/27/2023 | Alternative |  | 132-07-0200 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge |  |  | Royal | Duffy | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
09/25/2023 | Alternative | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/25/2023 | Dec 30 1899 10:40AM
12/15/2023 | Alternative | Routine/Scheduled | SP-04-205 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Type of System Alternative Type of AOSS System Advantex ax20 Septic Tank Condition of above Component Notes for above Component At normal level Has 3" of solids with 6" of sludge Pulled and cleaned rsv Recirculation Tank Condition of above Component Notes for above Component At normal level Has 8" of sludge Pulled and cleaned pump, floats and filter Pump and floats are aged Sb4 is not attached Discharge/Pump Tank Condition of above Component Notes for above Component Below normal level due to floats not working properly Customer approved to replace floats on sight Pump was replaced last year and is working properly Has concrete crock but is in good shape Media Sheets Condition of above Component Notes for above Component Sprayed off sheets and brushed laterals Locking strut no longer attached Sheets are ponding water and bridging Control Panel Condition of above Component Notes for above Component Panel is aged but working properly Recirc pulling 11.63amps Discharge pulling 8.40 Drain Field Condition of above Component Notes for above Component Showing no signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/18/2023 | 10:24 AM
12/18/2023 | Alternative | Reportable Incident Component Maintenance | 175-14-0128 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Discolored | [13 empty] | Will be sent separately | Inspected | High level alarm started at 2 a.m. this morning following a very heavy rain. Owner checked all toilets, said none out of adjustment or running in any way. Effluent in pump tank is discolored, possibly from infiltration. No infiltration seen in pump tank (above water line only, tank in high level). No water seen coming through sewer line inlet tee until after the ground was soaked with a garden hose around the closest clean-out. Ground is slightly depressed there. Suspect infiltration my be occurring at the return-to-septic line connection. Needs further investigation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/20/2023 | 11:50 AM
02/02/2023 |  | RoutineScheduled | 175-16-0436 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | Recommend Septic Tank pump out Summer of 2023 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/01/2023 | 02:21 PM
12/15/2023 | Alternative |  | {FIPSCode}-STS-79644 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
12/27/2023 | Alternative |  | 101-14-0291 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/15/2024 | 12:00 AM
08/01/2023 | Alternative | RoutineScheduled Component Maintenance | 179-12-0161-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation"] | ["Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 07:38 AM
03/21/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [7 empty] | 03/21/2023 |  | 386.000000 | [5 empty] | Will be sent separately | Inspected | brackets and shocks broke All tanks pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
08/05/2023 | Alternative | RoutineScheduled | 107-15-0175 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Distribution Pump Operation","Effluent Screens","Control Operation"] | ["Distribution Pump Operation","Effluent Screens","Control Operation"] | YES | Musty | Clear | [15 empty] | pump fuse was blown. replaced fuse. panel returned to function | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | 182-05-0238 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 06/19/2023 |  | 25.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
12/12/2023 | Alternative | Routine/Scheduled | 151-18-0155 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs to be pumped out. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 05:00 PM
03/15/2023 |  | RoutineScheduled | SWP-05-59 | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
03/06/2023 | Alternative | Routine/Scheduled | 159-03-090 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. Pump Basin - three cracks/fractures present - float sensors, pump and controls operating - recommend basin be replaced with pump tank. BioFilter - peat moss in fair to poor condition - module has a few visible fractures present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/07/2023 | 09:30 AM
02/20/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The Ecoflo peat fiber was replaced and is in working condition at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/21/2023 | 12:59 PM
04/19/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent pump appears to be near the end of its life but is functioning at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
06/19/2023 | Alternative | RoutineScheduled Component Maintenance | 015-STS-337154 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 06/19/2023 |  | 95.000000 | [5 empty] | Will be sent separately | Inspected | Filter Clogged able to clean | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/23/2023 | 06:57 AM
02/20/2023 | Alternative | Routine/Scheduled | 136-06-0693 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | COSS - Maintenance - VDH HDID 136-22-0017 Pumped concrete septic tank empty - crushed and removed. Installed new Infiltrator plastic ST (IM1060) in same location. Installed new 4" PVC sewer line Installed new 4" PVC conveyance line. Installed new 8 port concrete DBox Spliced to existing header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/21/2023 | 09:30 AM
06/23/2023 | Alternative | Routine/Scheduled | 085-STS-33055 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | Orenco Advantex |  | Pump | Gravity | Trenches | UV | 600.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary septic tank - normal level - recommend pumpout next service event - effluent screen serviced. Processing Tank - recirc - media drapes, recirc pump, spray grid serviced. U.V - bulb and housing serviced. Processing Tank - discharge - float sensors, pump and controls operating. DBox - concrete - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/26/2023 | Dec 30 1899 12:45PM
03/10/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.900000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 08:40 AM
03/08/2023 |  | Routine/Scheduled | 06-120-0420A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 2.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/08/2023 | Jan 1 1900 1:16PM
03/16/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-6"sludge 10"scum/ Microfast-18"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ The media is clogged in the Microfast unit and requires chemical cleaning and pump out of the tank/ Blower air filter cleaned and blower is working properly/ Controls, pump, floats and alarms are functioning properly/ Counts: Pump-3685 ETM-752h 37m/ High-11/ Peak-7 On-13m 16s Off-3h/ Watermeter- 0320481.4/ No breakout or spongy areas on the drip field and dosing properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/19/2023 | Alternative | RoutineScheduled | 2011-08-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Pura Flo |  | Pump | Gravity | Discharge | UV | 500.000000 | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 7.300000 | [15 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/21/2023 | 12:00 AM
03/29/2023 |  | Routine/Scheduled | {FIPSCode}-STS-3884 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | Jan 1 1900 9:05AM
10/04/2023 | Alternative | RoutineScheduled | 10-163-0056 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Septic Service | 1942001039 | Corey | Braxton |  |  | Ecopod |  | Gravity | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/04/2023 | 12:00 AM
06/25/2023 | Alternative | RoutineScheduled | SD-99-436 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 2.000000 | 1500 | septic | Multiflo | Gravity | Pressure | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | 7.010000 | 7.300000 |  | 1.020000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 06/29/2023 | 08:40 AM
03/30/2023 | Alternative | RoutineScheduled | 182-03-0289 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [17 empty] | Pumped Out | Blower replaced, FAST repaired, Septic pumped | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/30/2023 | 12:00 AM
08/09/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/15/2023 | Dec 30 1899 2:41PM
10/17/2023 | Alternative | RoutineScheduled | 08-100-0804 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 1500 | BIOCOIR |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | SLUDGE JUDGE SEPTIC TANK 6-7" FROM BOTTOM EVERYTHING WORKING AS IT SHOULD MEDIA IN GOOD CONDITION REHUNG FLOW PIPE IN BIOCOIR | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 01:05 PM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/23/2023 |  |  |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EZ Treat | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/05/2023 | 12:00 AM
06/13/2023 | Alternative | RoutineScheduled Component Maintenance | 154-04-0966 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 175-13-0246R | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Gravity | Gravity |  | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | 11/15/2023 | 02:02 PM
01/09/2023 | Alternative | Follow-Up | 166-14-158 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Adjusted time dose control. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
05/11/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/15/2023 | Dec 30 1899 12:05PM
03/18/2023 |  | RoutineScheduled | 2070-01-153 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | Dabney & Crooks, Inc. | 1965004241 | Doug | Crooks |  |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination | 500.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | Musty | Clear | 6.800000 |  |  | 1.700000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/23/2023 | 12:00 AM
09/15/2023 | Alternative | RoutineScheduled | {FIPSCode}-STS-23599 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | [12 empty] | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/03/2023 | 12:00 AM
03/30/2023 |  | RoutineScheduled | SWP-01-271 | Stafford | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for routine inspection. Peat moss 21 years old and needs to be change as soon as possible. Pounding in pods 2 and 3. Pods 1 and 4 the peat has no fiber to it and is not treating the waste water at all. Infiltration on both tanks. Proposal to be sent to make all corrections to the system. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/04/2023 | 04:51 AM
01/11/2023 |  | Follow-Up | SWP-04-21 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank pumped out by others prior to peat replacement. Degraded peat was removed by hand with pitch forks and new peat was installed. Peat was purchased from Driller Services. Degraded peat was disposed at Spotsylvania Refuse. Replaced 3 support bars on first Puraflo pod. Replaced top riser and lid on sample box. Deleted splitter box and made sample box splitter. Added riser over first distribution box for easy access. Cut down large Maple tree near headers, left debris in woods & grinded stump. Jet cleaned all lines. Re-timed distribution box and cleaned out sludge. Repaired header lines 5 & 10. Added root kill to all lines. Sealed mid-joint on septic tank outlet riser and pump tank riser. Cleared small saplings around pods. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
01/23/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/27/2023 | 07:00 PM
03/21/2023 |  | Reportable Incident | SP-04-384 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | High level alarm. Timer enabler float was floating but only carrying 80.5 volts (not enough to activate the timer). Replaced it and the high level alarm float (due to age and condition). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/04/2023 | 04:51 AM
08/10/2023 | Alternative | Reportable Incident Component Maintenance | SWP-05-130 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001681 | Scott | Perkins Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Onsite for tree hitting puraflo lid. Replaced the lid with a used lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 09/01/2023 | 05:07 AM
03/06/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/31/2023 | 12:26 PM
02/14/2023 |  | RoutineScheduled | 08-113-322 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","Auxiliary Filter","Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 15 Dechlorine | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 02/14/2023 | 12:00 AM
05/11/2023 | Alternative | Reportable Incident | 133-STS-92532 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
06/20/2023 | Alternative | RoutineScheduled | 181-05-0019 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | MicroFast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The blower and spin clean filters were both pulled and cleaned. The controls were operating as designed. There was return effluent returning to the pump tank, so the drip field was operating as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | 02:25 PM
02/03/2023 |  | RoutineScheduled |  | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend timer upgrade Wastewater lab denied | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
05/11/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/23/2023 | 09:32 AM
03/09/2023 |  | RoutineScheduled |  | Rockingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 03/09/2023 |  | 11.000000 | [5 empty] | Will be sent separately | Inspected | Pumping of primary tank is needed and pump tank is recommended Replaced blower panel and pressure gauge | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/28/2023 | 02:17 PM
04/10/2023 |  | Follow-Up | 179-14-0124-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [7 empty] | 04/10/2023 |  | 26.000000 | [5 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
06/07/2023 | Alternative | Reportable Incident | 550-STS-5875 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. | 06/07/2023 | Dec 30 1899 7:30AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Hydraulic unit is covered in overgrowth and is unserviceable. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/29/2023 | 12:05 PM
03/29/2023 | Alternative | Reportable Incident | 103-STS-101795 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1250 | None | None | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | [18 empty] | COSS - Maintenance - VDH Permit 151-22-0194 Installed gravity sewer line from Garage to pump basin. Installed Topps Fiberglass pump basin. Installed conveyance line from pump basin to existing septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/30/2023 | 07:00 AM
02/01/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/14/2023 | Dec 30 1899 8:41AM
07/24/2023 | Alternative | RoutineScheduled Component Maintenance | 179-13-0210-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Effluent Screens" ,"Control Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump"] | YES | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 07:01 AM
05/17/2023 | Alternative | RoutineScheduled | 03-160-0236 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Timothy | Conner | 2.000000 | 2000 | Whitewater |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | Septic | Dark Brown | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/18/2023 | 12:00 AM
11/28/2023 | Alternative | Routine/Scheduled | 136-17-0122 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Normal Level 6" of sludge 1" of solids Inlet and outlet tees intact No signs of infiltration -Discharge/Pump Tank: Normal Level Pulled and cleaned pump and floats All floats and pump are functioning properly No signs of infiltration -Aeration: Normal Level Less than 1" of suspended solids Pulled and cleaned diffuser is 50% clogged Pulled and cleaned weir Alarm float is functioning properly -Control Panel: 120v All audible and visual alarms are functioning properly Discharge pump pulled 8.75amps Air pump pulled 1.01amps -Distribution Box: Plastic distribution box at grade in good condition 4 lines balanced and taking water -Drain Field: No signs of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/12/2023 | 01:58 PM
03/28/2023 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | [28 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/29/2023 | 12:55 PM
09/16/2023 | Alternative | RoutineScheduled |  | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Orenco Advantex AX20RT |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. Cleaned septic tank solids filter. 13" of solids in recirculation portion of treatment unit. 12" of solids in discharge portion of treatment unit. Flushed treatment unit spray manifold. Cleaned recirculation pump intake screen, Tested floats, pump and alarm. Excellent treatment quality. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/24/2023 | 07:03 PM
03/17/2023 | Alternative | Routine/Scheduled | 800-08-0150 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | BlowerCompressorAerator Operation | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | N/A | [17 empty] | Routine Service. Primary septic tank - normal level. Aeration Tank - NO MIXING PRESENT - Compressor wiring causing electrical shorts and breaker to trip. Wiring disconnected from control panel. Pump Tank - high level due to tripped breaker - reset and pumped out of high level condition - float sensors, pump and controls operating. DBox - intact Requires electrical consult - new wiring to compressor and replace compressor. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 03/20/2023 | Dec 30 1899 9:45AM
05/31/2023 | Alternative | Reportable Incident | 166-17-142 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to an alarm. Serviced system. Checked the panel, and floats (ok). Cleaned the filter and cleaned the diffuser in the Clearstream. Changed the filter in the aerator. Installed an aerator rebuild kit. Replaced the relay and wired the pump through the pump float. Replaced the UV bulb, replaced the UV cord, and replaced the UV circuit board. The timer is set to 4 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 05/31/2023 | 09:30 AM
07/03/2023 | Alternative |  | 07-113-124 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/03/2023 |  | 2.280000 |  |  | 21.200000 |  |  | Will be sent separately |  | BOD: 2.28 TSS: 21.2 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/03/2023 | 12:00 AM
07/25/2023 | Alternative | RoutineScheduled Component Maintenance | 182-18-0049 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 07/25/2023 |  | 5.000000 | [5 empty] | Will be sent separately | Inspected | Repaired air supply and pumped primary tank | This AOSS should now return to normal function after having provided the above state routine maintenance | 09/20/2023 | 01:07 PM
05/18/2023 |  | RoutineScheduled |  | Page | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 05/18/2023 |  | 33.000000 | [5 empty] | Will be sent separately | Inspected | All peat needs replaced Discharge control and pump needs repairs Pressure gauge bad Alarms and floats not operating properly Filter needs to be extended | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 06/21/2023 | 03:35 PM
02/28/2023 |  | Routine/Scheduled | 550-STS-6377 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/28/2023 | Jan 1 1900 1:25PM
07/28/2023 | Alternative | Reportable Incident | 128-08-0185 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | replaced failed compressor | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12:00 AM
07/27/2023 | Alternative | Routine/Scheduled | 166-06-059 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Upgrade Riser access and discharge pump. Installed EcoFlo riser extension Intalled new discharge pump, float sensors, and controls. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/31/2023 | 07:30 AM
10/11/2023 | Alternative | RoutineScheduled Component Maintenance | 175-19-0166 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/15/2023 | 02:02 PM
12/05/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 12/05/2023 | Sample Chamber | 13.000000 | [5 empty] | Attached to this report |  | Septic Tank- 6"sludge 4"scum/ Microfast ATU-10"sludge 0"scum/ No pump out needed at this time/ Blower air filter cleaned, sealed openings in the blower housing/ Blower, controls and alarm are functioning properly / No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
05/09/2023 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced D80 compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
04/14/2023 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/15/2023 | 12:48 PM
12/12/2023 | Alternative | RoutineScheduled | 023-STS-42917 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NA | None | Clear | [5 empty] | 12/12/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/11/2024 | Dec 30 1899 1:50AM
02/24/2023 |  | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | Powell's Plumbing, LLC | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | N/A | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 02/27/2023 | 12:46 PM
01/25/2023 |  | Routine/Scheduled | 228-17-0216 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/25/2023 | Jan 1 1900 1:05PM
03/28/2023 | Alternative | Initial Visit | 073-STS-92818 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due to a red light. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed an aerator rebuild kit. Fixed the grade on the pipe in the Clearstream. Replaced the UV light and replaced the UV ballast. The timer is set to 8 minutes every 1 hour. Did not take initial samples. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 03/28/2023 | 02:30 PM
10/10/2023 | Alternative | RoutineScheduled Component Maintenance | 177-06-0357-SWT | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
06/29/2023 | Alternative | RoutineScheduled | 150-18-0035 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 1.000000 | 1500 gallons | Clearstream ATU |  | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Distribution Pump Operation","Control Operation","BlowerCompressorAerator Operation"] | NA | Musty | Clear |  |  | 10.000000 | [12 empty] | Clearstream ATU trash compartment 0" fog, 10" sludge. Clearstream ATU 10% SS. Serviced aerator pump. Pump, alarm, floats, controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/23/2023 | 06:45 PM
05/15/2023 |  | Routine/Scheduled | {FIPSCode}-STS-2398 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 05/15/2023 | Jan 1 1900 10:35AM
01/29/2023 |  | Routine/Scheduled | 145-STS-259902 | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Drainfields LLC | 1942001219 | Gene | Shanks | 1.000000 | 450 |  |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] |  | Musty | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/29/2023 | Jan 1 1900 10:30AM
01/04/2023 | Alternative | Routine/Scheduled | 234-18-173 | Chesapeake | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [13 empty] | UV is not working | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 01/04/2023 | Dec 30 1899 10:15AM
08/08/2023 | Alternative | Routine/Scheduled | {FIPSCode}-STS-3709 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 2:17PM
04/11/2023 |  | Reportable Incident |  | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 | Distribution Pump Operation | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [16 empty] | Pumped Out | AOSS - Alarm - dosing pump failure - high level alarm float failure. Pumped septic tank and pump tank - replaced dosing pump, and float sensors. Serviced effluent screen - peatmoss in good condition - raked / turned. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 04/17/2023 | 07:30 AM
03/15/2023 | Alternative | RoutineScheduled | 159-17-0102 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Aquasafe |  | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/11/2024 | 01:04 PM
10/17/2023 | Alternative | RoutineScheduled |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 1.000000 | 1500 | Microfast |  | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear |  | 7.600000 |  | 1.000000 |  | 10/17/2023 | Sample Tap | 3.000000 | 0.000000 |  | 6.330000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/11/2023 | 07:50 AM
03/15/2023 | Alternative | RoutineScheduled | 159-11-156 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic | 1942001302 | Charles | Langford | 1.000000 | 1200 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | [] | YES | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/16/2023 | 12:00 AM
07/20/2023 | Alternative | Routine/Scheduled | 151-14-0112 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | Gravity | Pad | Not Applicable | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service. Primary septic tank - normal level - effluent screen serviced. PUmp Basin - float sensors, pump and controls operating. Biofilter - peatmoss in poor condition - compacted - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/24/2023 | 07:15 AM
05/23/2023 | Alternative | RoutineScheduled | 171-11-0312 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aquaklear |  | Gravity | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [16 empty] | Inspected | Sludge level-2-3" scum layer on top-14" sludge on bottom in Septic tank - Treatment Unit has 3 inch scum layer and clear effluent, owner may recirculte the scum back to septic tank. Good aeration. Owner had recently replaced the UV light & bulb is running, the disharge to a moist grassy ditch was not remarkable. No samples was there to collect. No flow. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 05/30/2023 | 09:30 AM
03/28/2023 |  | RoutineScheduled | 182-17-0180 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | FAST |  |  | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | Septic/FAST needs pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 03/28/2023 | 12:00 AM
10/02/2023 | Alternative | Routine/Scheduled | 15-160-0167 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | None | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [7 empty] | 08/18/2023 | Pump Chamber | 2.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/02/2023 | 02:30 PM
06/14/2023 |  |  |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Drainfield Solutions, LLC | 2705163102 | Michele | Ware |  |  | Norweco | [27 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/23/2023 | 12:00 AM
05/16/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Parking on distribution box is falling off. There is root infiltration and the level is low. Recommend adding a 90 or a Tee to the inlet pipe. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/05/2023 | 03:56 AM
07/03/2023 | Alternative | Routine/Scheduled | 228-16-0357 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/03/2023 | Dec 30 1899 11:35AM
07/31/2023 | Alternative | RoutineScheduled Component Maintenance | SD-06-246 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001403 | Isail | Marquez |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | ["Control Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Sheets, biotube filter and pump intake were really dirty also the ax20 unit had alot slime due to customer using scented beads and liquid softeners. Gave customer copy of Do's and don'ts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/01/2023 | 12:19 PM
04/24/2023 | Alternative | Follow-Up | SD-15-43 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation"] | NA | None | [14 empty] | Will be sent separately | Inspected | Owner cut disposal area back to about 6", no balancing (globe) valves found. Repaired 4 broken 90* elbows, then jetted all 10 laterals. Fair amount of mud in the lateral turn-ups that were broken. Performed a drawdown and got 78.3 gpm. No records exist of the flow-rate achieved at startup. So today's rate could be pretty close to normal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/01/2023 | 06:44 AM
01/31/2023 | Alternative | RoutineScheduled | 154-04-0693 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 3.000000 | 3000 | Puraflow |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","Dispersal System Operation","Distribution Pump Operation","Effluent Screens"] | YES | Musty | Clear | [14 empty] | Inspected | One Way/ Shutoff Valve Replaced on Distribution Pump Leaking Quick Connect in Head Works Replaced Peat Moss Raked, Good Shape Septic, 1st Pump Station, and 2nd Pump Station Sludge Scum Levels all less than 6" | This AOSS should now return to normal function after having provided the above state routine maintenance. | 01/31/2023 | 10:00 AM
11/13/2023 | Alternative | RoutineScheduled | VAG401359 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | NA | None | Clear | [15 empty] | no discharge during visit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/09/2024 | 12:00 AM
06/10/2023 | Alternative | RoutineScheduled | 18-100-0066 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 | 500 | AQUASAFE |  | Pump | Pressure | Mound | Not Applicable | 300.000000 | [] | [] | [17 empty] | Pumped Out | EVERYTHING WORKING AS IT SHOULD. PUMPED SLUDGE IN AQUASAFE TANK. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/27/2023 | 12:00 AM
02/17/2023 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [17 empty] | Septic Tank-4"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Controls, pumps, floats and alarms functioning properly/ Puraflo Peat turned in all 6 Modules and the peat is in good condition at this time/ Counts: Pump1-31860 ETM-34405/ Pump2-31282 ETM-35316/ No breakout or spongy at the pad area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
03/27/2023 |  | Initial Visit | 182-97-0515 (LEGACY ALT. SYSTEM-spray) | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | SEAL'S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | Sand |  |  |  | Discharge | Chlorination |  | [] | [] |  |  |  | 6.300000 |  |  | 1.400000 |  | 03/27/2023 |  | 8.000000 |  |  | 22.200000 |  |  |  |  | recommend risers placed. 2 sprinklers required maintenance | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/27/2023 | 12:00 AM
08/14/2023 | Alternative | RoutineScheduled | 05-100-0122 | Accomack | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Eastern Shore | Boggs Water & Sewage, Inc | 1942001189 | Phillip | Dunn | 1.000000 |  | PURAFLO |  | Pump | Gravity | Pad |  | 450.000000 | [] | [] | YES | [17 empty] | SLUDGE JUDGE 5" FROM BOTTOM PEAT JUST PUT IN LAST YEAR EVERYTHING WORKING AS IT SHOULD | This AOSS should now return to normal function after having provided the above state routine maintenance. | 08/15/2023 | 10:00 AM
01/13/2023 |  | Routine/Scheduled | 234-12-141 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Mound | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/13/2023 | Jan 1 1900 9:10AM
12/01/2023 | Alternative | Reportable Incident | 157-02-132 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due it leaking by septic top. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank - was stopped up with wipes. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank should be pumped out due to the wipes - will stop up the filter again. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/01/2023 | 10:45 AM
11/30/2023 | Alternative | RoutineScheduled | 2003-143-0338 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001196 | Keith | McQuiddy | 1.000000 | 1250 | Advantex |  | Gravity | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/06/2023 | 12:00 AM
06/14/2023 | Alternative | Routine/Scheduled | 234-08 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/14/2023 | Dec 30 1899 8:45AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | ATU needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
10/11/2023 | Alternative | RoutineScheduled | 07-197-A9 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 7.000000 | 6.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12:00 AM
07/05/2023 | Alternative | RoutineScheduled | 109-07-0953 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. Tank inspected and determined no pump-out necessary | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium","Control Operation"] | ["Effluent Screens","Attached Growth Medium","Control Operation"] | NA | [16 empty] | Inspected | Septic zone 2-4"Scum layer & 18" Sludge in septic zone- time to pump this tank, recirculation zone 10-12 in. sludge, pumping maybe needed this year. Clear Effluent on top, system is operational, discharge basin 12" in trace of fine sludge, hosed off media, Cleaned Bio-filter, RSV, Brushed and Flushed Manifold, Ran system in test mode, 5 of 6 floats test operational. Both pumps operational. Pulled both pumps. Recirc run time 777 hours and 45,869 cycles.. Discharge pump run time 413.2 hours and 34,039 cycles. 1 alarm in history for low use. added 1 ROOTX treatment. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 07/30/2023 | 09:30 AM
03/14/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
02/15/2023 |  | Routine/Scheduled |  | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Richmond | Miller’s Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 1000 | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable | 750.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NO | [17 empty] | Routine Service Primary Trash Tanks - normal level Aeration Tanks - mixing present - compressors serviced. Pump Tank - float sensors, pump and controls operating. Community Absorption Field - not contracted for service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/16/2023 | Jan 1 1900 8:00AM
09/05/2023 | Alternative | Follow-Up |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [28 empty] | Raised the aerator and installed a new Norweco UV unit. Need to take 5 year labs. | This AOSS should now return to normal function after having provided the above state routine maintenance. | 09/05/2023 | Dec 30 1899 12:00PM
03/06/2023 |  | Follow-Up |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Loudoun | Mckim Septic and Pumping | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Drain field was mowed. Zone one has broken line that will need repaired. Also k-rain is cracked and spraying out when pump is on. The other issues still need addressed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 04/21/2023 | 12:59 PM
03/13/2023 |  | RoutineScheduled | SWP-04-967 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | We will contact you prior to next year's inspection regarding pumping the Advantex tank & pump tank during your 2024 inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
11/10/2023 | Alternative | RoutineScheduled Component Maintenance | SD-06-316 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Control Operation"] | ["Effluent Screens" ,"Control Operation"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | Owner called with alarm. Corroded wiring in the control panel was not allowing the pump to operate properly. We cleaned the wiring and the pump returned to normal operation. Because this is likely to reoccur, we recommend replacing the control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
07/26/2023 | Alternative |  | 195-Discharge-30134 Aistrop Road | Washington | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/26/2023 | [7 empty] | Will be sent separately |  | BOD: BDL TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 07/26/2023 | 12:00 AM
09/26/2023 | Alternative | RoutineScheduled Component Maintenance | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | System is under deck and footers are less than 5 feet from system. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 10/16/2023 | Dec 30 1899 12:58PM
04/20/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | NA | [16 empty] | Inspected | Septic Tank 1-2" scum, 12" sludge, Cleaned Effluent Filter it was dirty and backed up- level returned to normal. Pump Tank trace fine sludge, Tested pump- Good, Alarm operational, Float switches ok and Turned Peat in 3 pods, Peat in good like new shape- Pump count 36471 vs 33062 or 3,409 cycles this past year and pump run time 722.11hrs vs 667.85 hours last year 54.26 hours run since last year. 2 hours over last year. to keep them level we Zip tied sprayed manifolds in the treatment tank.(original metal bands removed when peat replaced) Owner May need some more zip ties or larger ones for strength. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/30/2023 | 09:30 AM
12/26/2023 | Alternative | RoutineScheduled | 107-11-0200 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 0.000000 | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/12/2024 | 04:55 PM
08/08/2023 | Alternative | Routine/Scheduled | 234-14-280 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/08/2023 | Dec 30 1899 12:10PM
08/03/2023 | Alternative | Follow-Up |  | Chesterfield | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Payment | EHD - Chesterfield | Miller's Septic Service | 1942001468 | Kevin | Blasing | 1.000000 | 1000 | Sandfilter, Non-recirculating |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 |  | None | N/A | Musty | Clear | [5 empty] | 08/03/2023 | Sample Chamber | [6 empty] | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/07/2023 | Dec 30 1899 9:15AM
12/20/2023 | Alternative | RoutineScheduled | 02-197-188 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Septic Tank Baffles","Control Operation","Dispersal System Operation"] | NA | Musty | Clear | [15 empty] | 4 - Blue crystal tablets installed 15 - Bio max tablets installed Discharge sign installed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 12/20/2023 | 12:00 AM
03/02/2023 |  | RoutineScheduled | SD-03-151 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Scum & sludge ae building up in all tanks, we plan to pump all tanks & power wash as necessary in the near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/03/2023 | 08:19 AM
02/02/2023 | Alternative | Routine/Scheduled | 166-04-224 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES |  |  |  |  | 50.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/02/2023 | 05:34 PM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-438 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001403 | Isail | Marquez | 2.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Routine inspection. Air filter dirty, cleaned. Outstanding proposal for installing riser on septic tank inlet side and to remove bush growing next to Dbox. Blower 1.02 amps. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:08 AM
04/13/2023 |  | RoutineScheduled | 196-08-004 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected | Cleaned clogged inlet tee. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 05/02/2023 | 07:49 AM
09/05/2023 | Alternative | RoutineScheduled | 107-18-0027 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 5000 | Septic Tank Only | EZ-Treat | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | The system did not need to pumped. The effluent filter and the spin filter were both pulled and cleaned. The 8 EZ-Treat pods were all opened and sprayed off. Several of the sprayers were pulled and cleaned. The recirculating pumps were pulled and sprayed off. The controls were operating as designed. There was effluent returning to the pump tank so the drip field was operating as designed. There was no visible leaks in the drip field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 09/26/2023 | 03:40 PM
03/20/2023 |  | Pump-Out Only |  | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Pending Review | EHD - Lord Fairfax | McKim Septic & Pumping | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Pumped Out | Fuji tank pumped out | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 03/28/2023 | 03:20 PM
10/12/2023 | Alternative | Routine/Scheduled | 041-STS-260035 | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 10/12/2023 | Dec 30 1899 3:55PM
06/06/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
08/23/2023 | Alternative | RoutineScheduled | 05-197-171 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | FAST |  | Pump | Pressure | Drip | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Control Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/23/2023 | 12:00 AM
08/18/2023 | Alternative | Routine/Scheduled | 550-STS-6361 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 4.000000 | [13 empty] | UV is not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/18/2023 | Dec 30 1899 10:05AM
05/01/2023 | Alternative | RoutineScheduled Component Maintenance | SWP-05-553 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | Musty | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/03/2023 | 05:43 AM
12/12/2023 | Alternative | RoutineScheduled | 085-STS-32514 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Carrington Pump & Irrigation | 1942001121 | John | Carrington | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
02/09/2023 | Alternative | Routine/Scheduled | 05-160-0195 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/09/2023 | 11:00 AM
05/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
07/14/2023 | Alternative | Follow-Up Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Review | EHD - Loudoun | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Jet UV bulb. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/17/2023 | 12:46 PM
02/04/2023 |  | RoutineScheduled |  | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | Orenco Advantex |  | Gravity | Gravity | Trenches |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Annual inspection. 14" of accumulated solids in septic tank. 6" of solids in recirculation tank. Cleaned recirculation pump basket filter. Flushed spray manifolds in both treatment units. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/17/2023 | 07:03 PM
08/07/2023 | Alternative | RoutineScheduled Inspection in Lieu of Pump-Out | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. Tank inspected and determined no pump-out necessary | Approved | EHD - Fairfax | Virginia Septic | 1942001004 | Markham | Smith | 2.000000 | 750 | Treatment level 1 |  | Gravity | Gravity | Discharge | Not Applicable |  | [] | [] | NA | Musty | Cloudy | [15 empty] | No effluent was seen at discharge point | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 08/08/2023 | Dec 30 1899 3:30PM
05/28/2023 |  | RoutineScheduled | 033-18-0079-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens"] | ["Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Effluent Screens"] | YES | Musty | Discolored | [13 empty] | Will be sent separately | Inspected | Alarm call by owner. Cleaned clogged biofilter & recirculation pump. The bluevalves are not seating properly. Replacement is recommended. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/01/2023 | 06:29 AM
03/23/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
03/27/2023 |  | RoutineScheduled | 153-STS-20354 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ Advantex Recirc. Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | YES | [17 empty] | Septic Tank-4"sludge 3"scum/ Recirculation Tank-4"sludge 0"scum/ Pump Tank-2"sludge 0"scum/ No pump out needed at this time/ Recirc. Pump intake cleaned/ Controls, pumps, floats and alarms functioning properly/ Counts: Discharge Pump Total cycles-1255 ETM-424 On-2.1m Off-6h/ Recirc Run Time-241.5 Total cycles-47151 / AX-20 Filter Media in good condition, spraying properly/ No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
08/29/2023 | Alternative | Routine/Scheduled | 196-94-145 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Sandfilter, Recirculating |  | Gravity | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [5 empty] | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/29/2023 | 04:32 PM
01/10/2023 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service | 2705051738 | Josh | Hott | 1.000000 | 1500 | Septic | Pureflow | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
04/05/2023 |  | Routine/Scheduled | 228-13-0311 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | N/A | None | Clear | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/05/2023 | Jan 1 1900 4:00PM
08/17/2023 | Alternative | RoutineScheduled Component Maintenance | 175-11-0194 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 08/29/2023 | 03:58 AM
04/20/2023 |  | RoutineScheduled | 07-113-071 | Buchanan | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Dispersal System Operation","SludgeScum Accumulation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | 04/20/2023 | 12:00 AM
04/20/2023 |  | RoutineScheduled | 101-06-0097 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  | Norweco |  | Gravity | Pressure | Mound | Not Applicable | 600.000000 | [] | ["Control Operation","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/23/2023 | 12:00 AM
09/15/2023 | Alternative | RoutineScheduled | 00-197-A10 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | WCHD |  | Tiffany | Large | 1.000000 |  |  |  | Gravity | Gravity | Discharge | Chlorination | [21 empty] | Aerator is not working, no tablets | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | 10/03/2023 | 12:00 AM
11/19/2023 | Alternative | Reportable Incident | 136-11-0260 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Customer stated alarm started going off this morning on clearstream system Upon arrival I opened tanks and found septic above normal Level due to clogged filter, I pulled and cleaned filter, I pulled and cleaned wier in aeration tank, all components in discharge tank were clean. Noticed air pump wasn't running. Opened air pump housing and cylinder block housings and found diaphragms broken which caused safety switch to engage on air pump shutting air pump off. Alarm was because Air pump diaphragms are broken Quoted to replace or rebuild customer chose to rebuild air pump. I rebuilt air pump and all components were functioning properly upon departure | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 11/28/2023 | 02:32 PM
08/11/2023 | Alternative | RoutineScheduled | 154-10-0226 | Louisa | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2000 | Norweco |  | Pump | Pressure | Mound | Not Applicable |  | ["Level Sensor Operation","Distribution Pump Operation","Other"] | ["Auxiliary Filter","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Cloudy | [14 empty] | Pumped Out | Sewer inlet settling at tank - piping running uphill into tank - no T/baffle on inlet pipe Risers (3) on Poly Norweco Tank deformed allowing water to enter system High Water Float has a short - giving sporadic high water alarms Pressure Gauge not functioning Risers on pump station leaking - allowing outside water into pump chamber | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 08/11/2023 | 01:00 PM
09/15/2023 | Alternative | RoutineScheduled | 087-STS-6479 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Distribution Pump Operation","Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation","Auxiliary Filter"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/13/2023 | 12:00 AM
02/21/2023 |  | Routine/Scheduled | {FIPSCode}-STS-4026 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Miller's Septic Service | 1942001468 | Kevin | Blasing | 2.000000 | 2000 | EZ Treat Sandfilter |  | Pump | Gravity | Trenches | Not Applicable | 900.000000 | ["Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | Routine Service Primary Septic Tank - normal level - recommend pumpout next service event. Secondary septic tank - normal level Processing Tank - recirc pump, RSV, effluent screen serviced. Treatment Module - spray grid serviced, media washed down. Pump Tank - float sensors, pump and controls operating. DBox - intact. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 02/22/2023 | Jan 1 1900 10:00AM
02/21/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 03/04/2023 | 06:02 AM
05/01/2023 | Alternative | RoutineScheduled | 163-STS-333823 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Septic Tank Only | AdvantexAX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The system did not need to be pumped. The effluent filter was cleaned. The textile sheets were sprayed off. The recirculating and discharge pumps were pulled and sprayed off. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 06/06/2023 | 10:25 PM
10/02/2023 | Alternative | Routine/Scheduled | 157-08-0247 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | James Lee Miller III | 1942001468 | Kevin | Blasing | [11 empty] | N/A | [17 empty] | Annual Maintenance: -Septic Tank: Found at normal level, 9in of sludge and less than 1in of solids. Pulled and cleaned filter -Discharge/Pump Tank: Found at normal level, 4in of sludge and less than 1in of solids. Tested floats and pump all working as they should. Pump pulling high amps. Floats are aged. -Peat Moss: Raked out peat in all four modules. Some roots but peat still looks good. Inspection port is not holding water -Control Panel: 120 volts. audio and visual alarms working as they should. Pump pulled 17 amps. -Drain Field: No signs of surfacing in drainfield area | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/12/2023 | 12:46 PM
12/19/2023 | Alternative | RoutineScheduled | 19-160-0005 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner |  |  | Ecoflo | [6 empty] | [] | ["SludgeScum Accumulation"] | YES | Septic | [16 empty] | - pipe inside of the Ecoflo pretreatment unit is broke off, recommend repair/replacement | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | 12/20/2023 | 12:00 AM
01/31/2023 |  | Routine/Scheduled | 550-STS-6617 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 01/31/2023 |  | 4.000000 |  | 1.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 9:00AM
12/12/2023 | Alternative | RoutineScheduled | 18-137-0136 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Carrington Pump & Irrigation | 1942001121 | John | Carrington |  |  | Norweco |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Auxiliary Filter"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/10/2024 | 12:00 AM
10/30/2023 | Alternative | RoutineScheduled Component Maintenance | 177-15-0297-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Attached Growth Medium"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 12/01/2023 | 08:44 AM
12/20/2023 | Alternative | Routine/Scheduled | 17-120-0082AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | EZ Treat Sandfilter |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. | 12/20/2023 | Dec 30 1899 4:20PM
10/18/2023 | Alternative | Routine/Scheduled | 121-STS-11578 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable | 148.000000 | None | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 10/18/2023 | 09:15 AM
05/17/2023 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 06/21/2023 | 03:35 PM
07/11/2023 | Alternative | RoutineScheduled | VAG408073 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | NA | Musty | Clear | [15 empty] | no discharge during visit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 12/19/2023 | 12:00 AM
05/24/2023 | Alternative | RoutineScheduled Component Maintenance |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend mowing the drainfield area to aid in evapotranspiration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/05/2023 | 03:56 AM
05/26/2023 | Alternative | RoutineScheduled Component Maintenance | SD-07-138 | Orange | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | NA | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | There is broken plumbing next to the Zone 1 air release valve that should be repaired. There appears to be a wet area near where the Zone 2 air release valve is located. We recommend excavating & repairing this area. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | 07/03/2023 | 05:43 AM
01/03/2023 |  | Follow-Up | 177-17-0127-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed pump tank wedge lid. No leak found on inlet tank wall or sewer pipe penetration. Groundwater was 3? from top of tank. This is enough hydraulic pressure to show any leaks in tank. Tank was inspected up close and no leaks found other than pump tank wedge lid. Assisted pumper with pump out of Recirc tank. Refilled tank with clean water to proper operating level. Replaced tri-check with quality brass check valve, gate valve and union. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 01/12/2023 | 09:31 AM
04/13/2023 |  | RoutineScheduled | 10-165-0041 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Puraflo | Gravity | Pressure | Pad | Not Applicable | 300.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/27/2023 | 01:05 PM
05/17/2023 |  | RoutineScheduled | 153-STS-19072 | Prince William | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | SES Mid Atlantic, LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | UV |  | ["Effluent Screens" ,"Disinfection"] | ["Effluent Screens" ,"Disinfection"] | YES | Musty | Clear | 6.900000 | 17.800000 |  |  |  | 05/18/2023 |  | 7.000000 |  | 1600.000000 | 3.000000 |  |  | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | 06/15/2023 | 12:05 PM
03/17/2023 |  |  | 124-STS-2379 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 04/14/2023 | 12:00 AM
10/02/2023 | Alternative | RoutineScheduled Component Maintenance | 179-STS-88650 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Effluent Screens"] | YES | Musty | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 11/01/2023 | 07:38 AM
02/09/2023 |  | RoutineScheduled |  | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 04/18/2023 | 04:10 AM
01/23/2023 |  | RoutineScheduled |  | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith |  |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | ditches so signs of settlement talk to home owner | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/27/2023 | 07:00 PM
09/25/2023 | Alternative | RoutineScheduled | 166-19-005 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | cleaned filters | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12:00 AM
02/02/2023 | Alternative | RoutineScheduled Component Maintenance |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Pending Payment | EHD - Prince William | Ace Contracting Services, Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 | 0 | Puraflo | none | Gravity | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Septic | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 07/26/2023 | 03:09 AM
12/29/2023 | Alternative | RoutineScheduled Component Maintenance | 033-09-0175-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 Tank inspected and determined no pump-out necessary | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | Sulphitic | Cloudy | [13 empty] | Will be sent separately | Inspected | The Pump tank is leaking around the inlet and outlet pipes and wedge lid door. Please contact our office when you would like an estimate to excavate and reseal both tanks. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | 02/01/2024 | 07:56 AM
08/10/2023 | Alternative | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering, Inc. | 1942001664 | Randy | Kepler | 2.000000 | 1500 gallon-Septic W/Fast and 1000 Pump | Septic | MicroFast | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation"] | NA | [17 empty] | 2" of Scum And 12' of sludge Average. Owner is going to schedule a pumping. Alarms, blower, pump, floats ,are all working. Cleaned spin filter and filter on blower, Walked the field its dry no leaks. running in auto when I opened tank. 10275 Events 1279.31 hr | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 08/10/2023 | 11:45 AM
01/31/2023 |  | Routine/Scheduled | 175-STS-14483 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [16 empty] | 01/31/2023 |  | 8.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | 01/31/2023 | Jan 1 1900 8:26AM
11/08/2023 | Alternative | RoutineScheduled Component Maintenance | 107-09-0406 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance Tank inspected and determined no pump-out necessary | Approved | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Air vent repaired Pump intake was clogged but repaired | This AOSS should now return to normal function after having provided the above state routine maintenance | 12/06/2023 | 03:05 PM